## Cover
CogenS validation evidence
Module | DHW Hydronic Indirect Water Heater (IHWH)
Published stage | Stage 1
Case code | STAGE1_IHWH_IHWH_300
Reference engine | EnergyPlus
EnergyPlus version | unknown
Reference object | WaterHeater:Mixed with Heater Maximum Capacity = 0, source-side coil on a hot-water PlantLoop fed by an ideal DistrictHeating:Water source
Weather file | C:\EnergyPlusV26-1-0\WeatherData\USA_IL_Chicago-OHare.Intl.AP.725300_TMY3.epw
Scoring band | ASHRAE Guideline 14-2023 strict
Gated metrics | Annual total (+-5%), monthly NMBE (+-5%), monthly CV(RMSE) (<=15%).
Reported, NOT gated | Peak hourly (+-10%) and hourly CV(RMSE) (<=30%). Both are computed and shown on the Gates sheet. A single-hour extremum and hourly dispersion are the statistics most sensitive to intra-hour cycling phase, and are out of scope for an annual/monthly energy claim — the same treatment the DHW heat-pump module publishes.
Comparison basis | EnergyPlus runs first and defines BOTH the thermal draw and the mains water temperature; the two engines are then compared on boiler source-side heat transfer. Letting each engine derive its own load would blend draw and mains modelling into the result and make a deviation unattributable.
Overall result | PASS — every gated metric inside band
Headline deviation | -0.22%
Reproducing this | The full EnergyPlus run directory for this case — .idf, .err and eplusout.csv — ships in the audit-trace pack alongside this workbook, so every number here can be re-derived independently.
Git SHA | redacted
Run timestamp (UTC) | 2026-07-29T17:49:50Z

## Inputs
Parameter | Value
description | 300 gal commercial
equipment_type | Hydronic indirect (IHWH)
tank_volume_gal | 300
jacket_UA_Btu_h_F | 5.68
setpoint_F | 140
ambient_F | 65
coil_rating_Btu_h | 400000
dash_model | stateless (shipped default)
scored_quantity | SOURCE-side heat transfer — the boiler demand, which is what calc_ihwh_profile returns as hourly_data.
system_efficiency | 1.0 in the harness so boiler demand equals coil duty; this isolates the tank from an exchanger-efficiency assumption EP's ideal source does not model.

## CogenS Output
hour | draw_kW | source_kW
0 | 0 | 0.12485
1 | 0 | 0.12485
2 | 0 | 0.12485
3 | 0 | 0.12485
4 | 0 | 0.12485
5 | 0 | 0.12485
6 | 12.5257 | 12.6506
7 | 1.2893 | 1.4142
8 | 1.6775 | 1.8023
9 | 0 | 0.12485
10 | 0 | 0.12485
11 | 0 | 0.12485
12 | 0.89846 | 1.0233
13 | 0 | 0.12485
14 | 0 | 0.12485
15 | 0 | 0.12485
16 | 0 | 0.12485
17 | 0 | 0.12485
18 | 6.4206 | 6.5454
19 | 12.9212 | 13.046
20 | 0 | 0.12485
21 | 1.3154 | 1.4402
22 | 0 | 0.12485
23 | 0 | 0.12485
24 | 0 | 0.12485
25 | 0 | 0.12485
26 | 0 | 0.12485
27 | 0 | 0.12485
28 | 0 | 0.12485
29 | 0 | 0.12485
30 | 12.5334 | 12.6582
31 | 1.2904 | 1.4152
32 | 1.6788 | 1.8037
33 | 0 | 0.12485
34 | 0 | 0.12485
35 | 0 | 0.12485
36 | 0.89932 | 1.0242
37 | 0 | 0.12485
38 | 0 | 0.12485
39 | 0 | 0.12485
40 | 0 | 0.12485
41 | 0 | 0.12485
42 | 6.4267 | 6.5516
43 | 12.9326 | 13.0575
44 | 0 | 0.12485
45 | 1.3166 | 1.4415
46 | 0 | 0.12485
47 | 0 | 0.12485
48 | 0 | 0.12485
49 | 0 | 0.12485
50 | 0 | 0.12485
51 | 0 | 0.12485
52 | 0 | 0.12485
53 | 0 | 0.12485
54 | 12.5448 | 12.6696
55 | 1.2914 | 1.4163
56 | 1.6802 | 1.805
57 | 0 | 0.12485
58 | 0 | 0.12485
59 | 0 | 0.12485
60 | 0.90017 | 1.025
61 | 0 | 0.12485
62 | 0 | 0.12485
63 | 0 | 0.12485
64 | 0 | 0.12485
65 | 0 | 0.12485
66 | 6.4329 | 6.5577
67 | 12.944 | 13.0689
68 | 0 | 0.12485
69 | 1.3179 | 1.4427
70 | 0 | 0.12485
71 | 0 | 0.12485
72 | 0 | 0.12485
73 | 0 | 0.12485
74 | 0 | 0.12485
75 | 0 | 0.12485
76 | 0 | 0.12485
77 | 0 | 0.12485
78 | 12.556 | 12.6808
79 | 1.2924 | 1.4173
80 | 1.6815 | 1.8064
81 | 0 | 0.12485
82 | 0 | 0.12485
83 | 0 | 0.12485
84 | 0.90101 | 1.0259
85 | 0 | 0.12485
86 | 0 | 0.12485
87 | 0 | 0.12485
88 | 0 | 0.12485
89 | 0 | 0.12485
90 | 6.4389 | 6.5637
91 | 12.9552 | 13.0801
92 | 0 | 0.12485
93 | 1.3191 | 1.444
94 | 0 | 0.12485
95 | 0 | 0.12485
96 | 0 | 0.12485
97 | 0 | 0.12485
98 | 0 | 0.12485
99 | 0 | 0.12485
100 | 0 | 0.12485
101 | 0 | 0.12485
102 | 12.567 | 12.6918
103 | 1.2935 | 1.4183
104 | 1.6829 | 1.8077
105 | 0 | 0.12485
106 | 0 | 0.12485
107 | 0 | 0.12485
108 | 0.90184 | 1.0267
109 | 0 | 0.12485
110 | 0 | 0.12485
111 | 0 | 0.12485
112 | 0 | 0.12485
113 | 0 | 0.12485
114 | 6.4448 | 6.5697
115 | 12.9662 | 13.0911
116 | 0 | 0.12485
117 | 1.3203 | 1.4452
118 | 0 | 0.12485
119 | 0 | 0.12485
120 | 0 | 0.12485
121 | 0 | 0.12485
122 | 0 | 0.12485
123 | 0 | 0.12485
124 | 0 | 0.12485
125 | 0 | 0.12485
126 | 12.5778 | 12.7026
127 | 1.2944 | 1.4193
128 | 1.6842 | 1.809
129 | 0 | 0.12485
130 | 0 | 0.12485
131 | 0 | 0.12485
132 | 0.90265 | 1.0275
133 | 0 | 0.12485
134 | 0 | 0.12485
135 | 0 | 0.12485
136 | 0 | 0.12485
137 | 0 | 0.12485
138 | 6.4506 | 6.5755
139 | 12.977 | 13.1018
140 | 0 | 0.12485
141 | 1.3215 | 1.4463
142 | 0 | 0.12485
143 | 0 | 0.12485
144 | 0 | 0.12485
145 | 0 | 0.12485
146 | 0 | 0.12485
147 | 0 | 0.12485
148 | 0 | 0.12485
149 | 0 | 0.12485
150 | 12.5883 | 12.7131
151 | 1.2954 | 1.4203
152 | 1.6854 | 1.8103
153 | 0 | 0.12485
154 | 0 | 0.12485
155 | 0 | 0.12485
156 | 0.90343 | 1.0283
157 | 0 | 0.12485
158 | 0 | 0.12485
159 | 0 | 0.12485
160 | 0 | 0.12485
161 | 0 | 0.12485
162 | 6.4563 | 6.5811
163 | 12.9875 | 13.1123
164 | 0 | 0.12485
165 | 1.3226 | 1.4475
166 | 0 | 0.12485
167 | 0 | 0.12485
168 | 0 | 0.12485
169 | 0 | 0.12485
170 | 0 | 0.12485
171 | 0 | 0.12485
172 | 0 | 0.12485
173 | 0 | 0.12485
174 | 12.5986 | 12.7234
175 | 1.2964 | 1.4212
176 | 1.6867 | 1.8115
177 | 0 | 0.12485
178 | 0 | 0.12485
179 | 0 | 0.12485
180 | 0.90421 | 1.0291
181 | 0 | 0.12485
182 | 0 | 0.12485
183 | 0 | 0.12485
184 | 0 | 0.12485
185 | 0 | 0.12485
186 | 6.4618 | 6.5867
187 | 12.9978 | 13.1226
188 | 0 | 0.12485
189 | 1.3238 | 1.4486
190 | 0 | 0.12485
191 | 0 | 0.12485
192 | 0 | 0.12485
193 | 0 | 0.12485
194 | 0 | 0.12485
195 | 0 | 0.12485
196 | 0 | 0.12485
197 | 0 | 0.12485
198 | 12.6086 | 12.7335
199 | 1.2973 | 1.4221
200 | 1.6879 | 1.8127
201 | 0 | 0.12485
202 | 0 | 0.12485
203 | 0 | 0.12485
204 | 0.90496 | 1.0298
205 | 0 | 0.12485
206 | 0 | 0.12485
207 | 0 | 0.12485
208 | 0 | 0.12485
209 | 0 | 0.12485
210 | 6.4672 | 6.5921
211 | 13.0078 | 13.1327
212 | 0 | 0.12485
213 | 1.3249 | 1.4497
214 | 0 | 0.12485
215 | 0 | 0.12485
216 | 0 | 0.12485
217 | 0 | 0.12485
218 | 0 | 0.12485
219 | 0 | 0.12485
220 | 0 | 0.12485
221 | 0 | 0.12485
222 | 12.6184 | 12.7433
223 | 1.4013 | 1.5262
224 | 1.823 | 1.9478
225 | 0 | 0.12485
226 | 0 | 0.12485
227 | 0 | 0.12485
228 | 0.88715 | 1.012
229 | 0 | 0.12485
230 | 0 | 0.12485
231 | 0 | 0.12485
232 | 0 | 0.12485
233 | 0 | 0.12485
234 | 6.3469 | 6.4718
235 | 12.8387 | 12.9635
236 | 0 | 0.12485
237 | 1.313 | 1.4378
238 | 0 | 0.12485
239 | 0 | 0.12485
240 | 0 | 0.12485
241 | 0 | 0.12485
242 | 0 | 0.12485
243 | 0 | 0.12485
244 | 0 | 0.12485
245 | 0 | 0.12485
246 | 12.5154 | 12.6403
247 | 1.3957 | 1.5205
248 | 1.8156 | 1.9405
249 | 0 | 0.12485
250 | 0 | 0.12485
251 | 0 | 0.12485
252 | 0.8836 | 1.0084
253 | 0 | 0.12485
254 | 0 | 0.12485
255 | 0 | 0.12485
256 | 0 | 0.12485
257 | 0 | 0.12485
258 | 6.533 | 6.6578
259 | 12.7375 | 12.8624
260 | 0 | 0.12485
261 | 1.3057 | 1.4305
262 | 0 | 0.12485
263 | 0 | 0.12485
264 | 0 | 0.12485
265 | 0 | 0.12485
266 | 0 | 0.12485
267 | 0 | 0.12485
268 | 0 | 0.12485
269 | 0 | 0.12485
270 | 12.4505 | 12.5753
271 | 1.3922 | 1.517
272 | 1.8111 | 1.936
273 | 0 | 0.12485
274 | 0 | 0.12485
275 | 0 | 0.12485
276 | 0.88143 | 1.0063
277 | 0 | 0.12485
278 | 0 | 0.12485
279 | 0 | 0.12485
280 | 0 | 0.12485
281 | 0 | 0.12485
282 | 6.5207 | 6.6455
283 | 12.7214 | 12.8462
284 | 0 | 0.12485
285 | 1.3042 | 1.4291
286 | 0 | 0.12485
287 | 0 | 0.12485
288 | 0 | 0.12485
289 | 0 | 0.12485
290 | 0 | 0.12485
291 | 0 | 0.12485
292 | 0 | 0.12485
293 | 0 | 0.12485
294 | 12.4376 | 12.5624
295 | 1.3919 | 1.5167
296 | 1.8107 | 1.9356
297 | 0 | 0.12485
298 | 0 | 0.12485
299 | 0 | 0.12485
300 | 0.88124 | 1.0061
301 | 0 | 0.12485
302 | 0 | 0.12485
303 | 0 | 0.12485
304 | 0 | 0.12485
305 | 0 | 0.12485
306 | 6.5197 | 6.6446
307 | 12.72 | 12.8448
308 | 0 | 0.12485
309 | 1.3041 | 1.4289
310 | 0 | 0.12485
311 | 0 | 0.12485
312 | 0 | 0.12485
313 | 0 | 0.12485
314 | 0 | 0.12485
315 | 0 | 0.12485
316 | 0 | 0.12485
317 | 0 | 0.12485
318 | 12.4364 | 12.5612
319 | 1.3923 | 1.5171
320 | 1.8112 | 1.9361
321 | 0 | 0.12485
322 | 0 | 0.12485
323 | 0 | 0.12485
324 | 0.8815 | 1.0063
325 | 0 | 0.12485
326 | 0 | 0.12485
327 | 0 | 0.12485
328 | 0 | 0.12485
329 | 0 | 0.12485
330 | 6.5217 | 6.6466
331 | 12.7237 | 12.8486
332 | 0 | 0.12485
333 | 1.3044 | 1.4293
334 | 0 | 0.12485
335 | 0 | 0.12485
336 | 0 | 0.12485
337 | 0 | 0.12485
338 | 0 | 0.12485
339 | 0 | 0.12485
340 | 0 | 0.12485
341 | 0 | 0.12485
342 | 12.4393 | 12.5642
343 | 1.3929 | 1.5178
344 | 1.8121 | 1.9369
345 | 0 | 0.12485
346 | 0 | 0.12485
347 | 0 | 0.12485
348 | 0.88191 | 1.0068
349 | 0 | 0.12485
350 | 0 | 0.12485
351 | 0 | 0.12485
352 | 0 | 0.12485
353 | 0 | 0.12485
354 | 6.5248 | 6.6496
355 | 12.7292 | 12.854
356 | 0 | 0.12485
357 | 1.3049 | 1.4298
358 | 0 | 0.12485
359 | 0 | 0.12485
360 | 0 | 0.12485
361 | 0 | 0.12485
362 | 0 | 0.12485
363 | 0 | 0.12485
364 | 0 | 0.12485
365 | 0 | 0.12485
366 | 12.4437 | 12.5685
367 | 1.3936 | 1.5185
368 | 1.813 | 1.9378
369 | 0 | 0.12485
370 | 0 | 0.12485
371 | 0 | 0.12485
372 | 0.88236 | 1.0072
373 | 0 | 0.12485
374 | 0 | 0.12485
375 | 0 | 0.12485
376 | 0 | 0.12485
377 | 0 | 0.12485
378 | 6.5281 | 6.653
379 | 12.7352 | 12.86
380 | 0 | 0.12485
381 | 1.3055 | 1.4303
382 | 0 | 0.12485
383 | 0 | 0.12485
384 | 0 | 0.12485
385 | 0 | 0.12485
386 | 0 | 0.12485
387 | 0 | 0.12485
388 | 0 | 0.12485
389 | 0 | 0.12485
390 | 12.4484 | 12.5732
391 | 1.3943 | 1.5192
392 | 1.8139 | 1.9388
393 | 0 | 0.12485
394 | 0 | 0.12485
395 | 0 | 0.12485
396 | 0.88282 | 1.0077
397 | 0 | 0.12485
398 | 0 | 0.12485
399 | 0 | 0.12485
400 | 0 | 0.12485
401 | 0 | 0.12485
402 | 6.5315 | 6.6563
403 | 12.7412 | 12.866
404 | 0 | 0.12485
405 | 1.306 | 1.4309
406 | 0 | 0.12485
407 | 0 | 0.12485
408 | 0 | 0.12485
409 | 0 | 0.12485
410 | 0 | 0.12485
411 | 0 | 0.12485
412 | 0 | 0.12485
413 | 0 | 0.12485
414 | 12.4531 | 12.578
415 | 1.395 | 1.5199
416 | 1.8148 | 1.9397
417 | 0 | 0.12485
418 | 0 | 0.12485
419 | 0 | 0.12485
420 | 0.88327 | 1.0081
421 | 0 | 0.12485
422 | 0 | 0.12485
423 | 0 | 0.12485
424 | 0 | 0.12485
425 | 0 | 0.12485
426 | 6.5348 | 6.6597
427 | 12.7471 | 12.872
428 | 0 | 0.12485
429 | 1.4095 | 1.5344
430 | 0 | 0.12485
431 | 0 | 0.12485
432 | 0 | 0.12485
433 | 0 | 0.12485
434 | 0 | 0.12485
435 | 0 | 0.12485
436 | 0 | 0.12485
437 | 0 | 0.12485
438 | 12.72 | 12.8448
439 | 1.3763 | 1.5011
440 | 1.7904 | 1.9153
441 | 0 | 0.12485
442 | 0 | 0.12485
443 | 0 | 0.12485
444 | 0.87146 | 0.99631
445 | 0 | 0.12485
446 | 0 | 0.12485
447 | 0 | 0.12485
448 | 0 | 0.12485
449 | 0 | 0.12485
450 | 6.454 | 6.5788
451 | 12.6093 | 12.7341
452 | 0 | 0.12485
453 | 1.4016 | 1.5264
454 | 0 | 0.12485
455 | 0 | 0.12485
456 | 0 | 0.12485
457 | 0 | 0.12485
458 | 0 | 0.12485
459 | 0 | 0.12485
460 | 0 | 0.12485
461 | 0 | 0.12485
462 | 12.6504 | 12.7752
463 | 1.3702 | 1.495
464 | 1.7825 | 1.9074
465 | 0 | 0.12485
466 | 0 | 0.12485
467 | 0 | 0.12485
468 | 0.86764 | 0.99249
469 | 0 | 0.12485
470 | 0 | 0.12485
471 | 0 | 0.12485
472 | 0 | 0.12485
473 | 0 | 0.12485
474 | 6.4274 | 6.5523
475 | 12.5634 | 12.6883
476 | 0 | 0.12485
477 | 1.3992 | 1.524
478 | 0 | 0.12485
479 | 0 | 0.12485
480 | 0 | 0.12485
481 | 0 | 0.12485
482 | 0 | 0.12485
483 | 0 | 0.12485
484 | 0 | 0.12485
485 | 0 | 0.12485
486 | 12.6294 | 12.7543
487 | 1.3683 | 1.4932
488 | 1.7802 | 1.905
489 | 0 | 0.12485
490 | 0 | 0.12485
491 | 0 | 0.12485
492 | 0.86651 | 0.99136
493 | 0 | 0.12485
494 | 0 | 0.12485
495 | 0 | 0.12485
496 | 0 | 0.12485
497 | 0 | 0.12485
498 | 6.4196 | 6.5444
499 | 12.5499 | 12.6747
500 | 0 | 0.12485
501 | 1.3987 | 1.5235
502 | 0 | 0.12485
503 | 0 | 0.12485
504 | 0 | 0.12485
505 | 0 | 0.12485
506 | 0 | 0.12485
507 | 0 | 0.12485
508 | 0 | 0.12485
509 | 0 | 0.12485
510 | 13.0353 | 13.1601
511 | 1.3607 | 1.4856
512 | 1.7703 | 1.8951
513 | 0 | 0.12485
514 | 0 | 0.12485
515 | 0 | 0.12485
516 | 0.86173 | 0.98658
517 | 0 | 0.12485
518 | 0 | 0.12485
519 | 0 | 0.12485
520 | 0 | 0.12485
521 | 0 | 0.12485
522 | 6.6348 | 6.7597
523 | 12.8666 | 12.9915
524 | 0 | 0.12485
525 | 1.3819 | 1.5067
526 | 0 | 0.12485
527 | 0 | 0.12485
528 | 0 | 0.12485
529 | 0 | 0.12485
530 | 0 | 0.12485
531 | 0 | 0.12485
532 | 0 | 0.12485
533 | 0 | 0.12485
534 | 13.1004 | 13.2252
535 | 1.3393 | 1.4642
536 | 1.7425 | 1.8673
537 | 0 | 0.12485
538 | 0 | 0.12485
539 | 0 | 0.12485
540 | 0.84828 | 0.97313
541 | 0 | 0.12485
542 | 0 | 0.12485
543 | 0 | 0.12485
544 | 0 | 0.12485
545 | 0 | 0.12485
546 | 6.5634 | 6.6883
547 | 12.7768 | 12.9017
548 | 0 | 0.12485
549 | 1.3763 | 1.5011
550 | 0 | 0.12485
551 | 0 | 0.12485
552 | 0 | 0.12485
553 | 0 | 0.12485
554 | 0 | 0.12485
555 | 0 | 0.12485
556 | 0 | 0.12485
557 | 0 | 0.12485
558 | 13.0548 | 13.1797
559 | 1.3363 | 1.4612
560 | 1.7386 | 1.8635
561 | 0 | 0.12485
562 | 0 | 0.12485
563 | 0 | 0.12485
564 | 0.92833 | 1.0532
565 | 0 | 0.12485
566 | 0 | 0.12485
567 | 0 | 0.12485
568 | 0 | 0.12485
569 | 0 | 0.12485
570 | 6.5169 | 6.6417
571 | 12.7087 | 12.8336
572 | 0 | 0.12485
573 | 1.3701 | 1.495
574 | 0 | 0.12485
575 | 0 | 0.12485
576 | 0 | 0.12485
577 | 0 | 0.12485
578 | 0 | 0.12485
579 | 0 | 0.12485
580 | 0 | 0.12485
581 | 0 | 0.12485
582 | 13.0002 | 13.1251
583 | 1.3314 | 1.4562
584 | 1.7322 | 1.8571
585 | 0 | 0.12485
586 | 0 | 0.12485
587 | 0 | 0.12485
588 | 0.92456 | 1.0494
589 | 0 | 0.12485
590 | 0 | 0.12485
591 | 0 | 0.12485
592 | 0 | 0.12485
593 | 0 | 0.12485
594 | 6.6053 | 6.7302
595 | 13.2446 | 13.3695
596 | 0 | 0.12485
597 | 1.3457 | 1.4706
598 | 0 | 0.12485
599 | 0 | 0.12485
600 | 0 | 0.12485
601 | 0 | 0.12485
602 | 0 | 0.12485
603 | 0 | 0.12485
604 | 0 | 0.12485
605 | 0 | 0.12485
606 | 12.8006 | 12.9254
607 | 1.4188 | 1.5436
608 | 1.8457 | 1.9706
609 | 0 | 0.12485
610 | 0 | 0.12485
611 | 0 | 0.12485
612 | 0.89833 | 1.0232
613 | 0 | 0.12485
614 | 0 | 0.12485
615 | 0 | 0.12485
616 | 0 | 0.12485
617 | 0 | 0.12485
618 | 6.4268 | 6.5516
619 | 12.9798 | 13.1046
620 | 0 | 0.12485
621 | 1.3258 | 1.4507
622 | 0 | 0.12485
623 | 0 | 0.12485
624 | 0 | 0.12485
625 | 0 | 0.12485
626 | 0 | 0.12485
627 | 0 | 0.12485
628 | 0 | 0.12485
629 | 0 | 0.12485
630 | 12.6268 | 12.7517
631 | 1.4086 | 1.5335
632 | 1.8325 | 1.9574
633 | 0 | 0.12485
634 | 0 | 0.12485
635 | 0 | 0.12485
636 | 0.89193 | 1.0168
637 | 0 | 0.12485
638 | 0 | 0.12485
639 | 0 | 0.12485
640 | 0 | 0.12485
641 | 0 | 0.12485
642 | 6.5959 | 6.7207
643 | 12.8532 | 12.9781
644 | 0 | 0.12485
645 | 1.3162 | 1.4411
646 | 0 | 0.12485
647 | 0 | 0.12485
648 | 0 | 0.12485
649 | 0 | 0.12485
650 | 0 | 0.12485
651 | 0 | 0.12485
652 | 0 | 0.12485
653 | 0 | 0.12485
654 | 12.5416 | 12.6664
655 | 1.4037 | 1.5285
656 | 1.8261 | 1.951
657 | 0 | 0.12485
658 | 0 | 0.12485
659 | 0 | 0.12485
660 | 0.88883 | 1.0137
661 | 0 | 0.12485
662 | 0 | 0.12485
663 | 0 | 0.12485
664 | 0 | 0.12485
665 | 0 | 0.12485
666 | 6.5747 | 6.6996
667 | 12.8173 | 12.9422
668 | 0 | 0.12485
669 | 1.4171 | 1.542
670 | 0 | 0.12485
671 | 0 | 0.12485
672 | 0 | 0.12485
673 | 0 | 0.12485
674 | 0 | 0.12485
675 | 0 | 0.12485
676 | 0 | 0.12485
677 | 0 | 0.12485
678 | 12.785 | 12.9098
679 | 1.3823 | 1.5071
680 | 1.7983 | 1.9231
681 | 0 | 0.12485
682 | 0 | 0.12485
683 | 0 | 0.12485
684 | 0.87534 | 1.0002
685 | 0 | 0.12485
686 | 0 | 0.12485
687 | 0 | 0.12485
688 | 0 | 0.12485
689 | 0 | 0.12485
690 | 6.4821 | 6.607
691 | 12.6591 | 12.7839
692 | 0 | 0.12485
693 | 1.4077 | 1.5326
694 | 0 | 0.12485
695 | 0 | 0.12485
696 | 0 | 0.12485
697 | 0 | 0.12485
698 | 0 | 0.12485
699 | 0 | 0.12485
700 | 0 | 0.12485
701 | 0 | 0.12485
702 | 12.7032 | 12.828
703 | 1.3751 | 1.4999
704 | 1.789 | 1.9138
705 | 0 | 0.12485
706 | 0 | 0.12485
707 | 0 | 0.12485
708 | 0.87082 | 0.99567
709 | 0 | 0.12485
710 | 0 | 0.12485
711 | 0 | 0.12485
712 | 0 | 0.12485
713 | 0 | 0.12485
714 | 6.6463 | 6.7711
715 | 13.2842 | 13.4091
716 | 0 | 0.12485
717 | 1.3883 | 1.5132
718 | 0 | 0.12485
719 | 0 | 0.12485
720 | 0 | 0.12485
721 | 0 | 0.12485
722 | 0 | 0.12485
723 | 0 | 0.12485
724 | 0 | 0.12485
725 | 0 | 0.12485
726 | 13.1564 | 13.2813
727 | 1.3447 | 1.4696
728 | 1.7496 | 1.8744
729 | 0 | 0.12485
730 | 0 | 0.12485
731 | 0 | 0.12485
732 | 0.85175 | 0.9766
733 | 0 | 0.12485
734 | 0 | 0.12485
735 | 0 | 0.12485
736 | 0 | 0.12485
737 | 0 | 0.12485
738 | 6.5906 | 6.7155
739 | 12.8248 | 12.9496
740 | 0 | 0.12485
741 | 1.3807 | 1.5055
742 | 0 | 0.12485
743 | 0 | 0.12485
744 | 0 | 0.12485
745 | 0 | 0.12485
746 | 0 | 0.12485
747 | 0 | 0.12485
748 | 0 | 0.12485
749 | 0 | 0.12485
750 | 13.0917 | 13.2165
751 | 1.3397 | 1.4645
752 | 1.743 | 1.8679
753 | 0 | 0.12485
754 | 0 | 0.12485
755 | 0 | 0.12485
756 | 0.93014 | 1.055
757 | 0 | 0.12485
758 | 0 | 0.12485
759 | 0 | 0.12485
760 | 0 | 0.12485
761 | 0 | 0.12485
762 | 6.6445 | 6.7693
763 | 13.3105 | 13.4354
764 | 0 | 0.12485
765 | 1.3514 | 1.4763
766 | 0 | 0.12485
767 | 0 | 0.12485
768 | 0 | 0.12485
769 | 0 | 0.12485
770 | 0 | 0.12485
771 | 0 | 0.12485
772 | 0 | 0.12485
773 | 0 | 0.12485
774 | 12.8491 | 12.974
775 | 1.4234 | 1.5482
776 | 1.8517 | 1.9766
777 | 0 | 0.12485
778 | 0 | 0.12485
779 | 0 | 0.12485
780 | 0.90126 | 1.0261
781 | 0 | 0.12485
782 | 0 | 0.12485
783 | 0 | 0.12485
784 | 0 | 0.12485
785 | 0 | 0.12485
786 | 6.6561 | 6.7809
787 | 12.9483 | 13.0732
788 | 0 | 0.12485
789 | 1.3248 | 1.4497
790 | 0 | 0.12485
791 | 0 | 0.12485
792 | 0 | 0.12485
793 | 0 | 0.12485
794 | 0 | 0.12485
795 | 0 | 0.12485
796 | 0 | 0.12485
797 | 0 | 0.12485
798 | 12.6162 | 12.7411
799 | 1.4095 | 1.5344
800 | 1.8337 | 1.9585
801 | 0 | 0.12485
802 | 0 | 0.12485
803 | 0 | 0.12485
804 | 0.89252 | 1.0174
805 | 0 | 0.12485
806 | 0 | 0.12485
807 | 0 | 0.12485
808 | 0 | 0.12485
809 | 0 | 0.12485
810 | 6.6007 | 6.7256
811 | 12.8625 | 12.9874
812 | 0 | 0.12485
813 | 1.4211 | 1.546
814 | 0 | 0.12485
815 | 0 | 0.12485
816 | 0 | 0.12485
817 | 0 | 0.12485
818 | 0 | 0.12485
819 | 0 | 0.12485
820 | 0 | 0.12485
821 | 0 | 0.12485
822 | 12.8186 | 12.9434
823 | 1.3853 | 1.5102
824 | 1.8023 | 1.9271
825 | 0 | 0.12485
826 | 0 | 0.12485
827 | 0 | 0.12485
828 | 0.87731 | 1.0022
829 | 0 | 0.12485
830 | 0 | 0.12485
831 | 0 | 0.12485
832 | 0 | 0.12485
833 | 0 | 0.12485
834 | 6.4962 | 6.621
835 | 12.6838 | 12.8086
836 | 0 | 0.12485
837 | 1.4104 | 1.5353
838 | 0 | 0.12485
839 | 0 | 0.12485
840 | 0 | 0.12485
841 | 0 | 0.12485
842 | 0 | 0.12485
843 | 0 | 0.12485
844 | 0 | 0.12485
845 | 0 | 0.12485
846 | 13.3374 | 13.4622
847 | 1.3568 | 1.4817
848 | 1.7653 | 1.8901
849 | 0 | 0.12485
850 | 0 | 0.12485
851 | 0 | 0.12485
852 | 0.85938 | 0.98423
853 | 0 | 0.12485
854 | 0 | 0.12485
855 | 0 | 0.12485
856 | 0 | 0.12485
857 | 0 | 0.12485
858 | 6.6289 | 6.7538
859 | 12.8896 | 13.0145
860 | 0 | 0.12485
861 | 1.3866 | 1.5115
862 | 0 | 0.12485
863 | 0 | 0.12485
864 | 0 | 0.12485
865 | 0 | 0.12485
866 | 0 | 0.12485
867 | 0 | 0.12485
868 | 0 | 0.12485
869 | 0 | 0.12485
870 | 13.1421 | 13.2669
871 | 1.3442 | 1.4691
872 | 1.7489 | 1.8738
873 | 0 | 0.12485
874 | 0 | 0.12485
875 | 0 | 0.12485
876 | 0.93324 | 1.0581
877 | 0 | 0.12485
878 | 0 | 0.12485
879 | 0 | 0.12485
880 | 0 | 0.12485
881 | 0 | 0.12485
882 | 6.5518 | 6.6766
883 | 12.771 | 12.8958
884 | 0 | 0.12485
885 | 1.3758 | 1.5006
886 | 0 | 0.12485
887 | 0 | 0.12485
888 | 0 | 0.12485
889 | 0 | 0.12485
890 | 0 | 0.12485
891 | 0 | 0.12485
892 | 0 | 0.12485
893 | 0 | 0.12485
894 | 13.0469 | 13.1717
895 | 1.3356 | 1.4605
896 | 1.7378 | 1.8626
897 | 0 | 0.12485
898 | 0 | 0.12485
899 | 0 | 0.12485
900 | 0.92753 | 1.0524
901 | 0 | 0.12485
902 | 0 | 0.12485
903 | 0 | 0.12485
904 | 0 | 0.12485
905 | 0 | 0.12485
906 | 6.6269 | 6.7518
907 | 13.2869 | 13.4118
908 | 0 | 0.12485
909 | 1.3507 | 1.4755
910 | 0 | 0.12485
911 | 0 | 0.12485
912 | 0 | 0.12485
913 | 0 | 0.12485
914 | 0 | 0.12485
915 | 0 | 0.12485
916 | 0 | 0.12485
917 | 0 | 0.12485
918 | 12.8414 | 12.9663
919 | 1.4238 | 1.5486
920 | 1.8522 | 1.9771
921 | 0 | 0.12485
922 | 0 | 0.12485
923 | 0 | 0.12485
924 | 0.90152 | 1.0264
925 | 0 | 0.12485
926 | 0 | 0.12485
927 | 0 | 0.12485
928 | 0 | 0.12485
929 | 0 | 0.12485
930 | 6.6599 | 6.7848
931 | 12.9586 | 13.0835
932 | 0 | 0.12485
933 | 1.3258 | 1.4506
934 | 0 | 0.12485
935 | 0 | 0.12485
936 | 0 | 0.12485
937 | 0 | 0.12485
938 | 0 | 0.12485
939 | 0 | 0.12485
940 | 0 | 0.12485
941 | 0 | 0.12485
942 | 12.6226 | 12.7474
943 | 1.4106 | 1.5355
944 | 1.8351 | 1.96
945 | 0 | 0.12485
946 | 0 | 0.12485
947 | 0 | 0.12485
948 | 0.89323 | 1.0181
949 | 0 | 0.12485
950 | 0 | 0.12485
951 | 0 | 0.12485
952 | 0 | 0.12485
953 | 0 | 0.12485
954 | 6.606 | 6.7308
955 | 12.8719 | 12.9968
956 | 0 | 0.12485
957 | 1.4224 | 1.5473
958 | 0 | 0.12485
959 | 0 | 0.12485
960 | 0 | 0.12485
961 | 0 | 0.12485
962 | 0 | 0.12485
963 | 0 | 0.12485
964 | 0 | 0.12485
965 | 0 | 0.12485
966 | 12.8278 | 12.9527
967 | 1.3862 | 1.511
968 | 1.8034 | 1.9283
969 | 0 | 0.12485
970 | 0 | 0.12485
971 | 0 | 0.12485
972 | 0.87787 | 1.0027
973 | 0 | 0.12485
974 | 0 | 0.12485
975 | 0 | 0.12485
976 | 0 | 0.12485
977 | 0 | 0.12485
978 | 6.5003 | 6.6251
979 | 12.691 | 12.8159
980 | 0 | 0.12485
981 | 1.4115 | 1.5363
982 | 0 | 0.12485
983 | 0 | 0.12485
984 | 0 | 0.12485
985 | 0 | 0.12485
986 | 0 | 0.12485
987 | 0 | 0.12485
988 | 0 | 0.12485
989 | 0 | 0.12485
990 | 13.3452 | 13.4701
991 | 1.3578 | 1.4826
992 | 1.7665 | 1.8914
993 | 0 | 0.12485
994 | 0 | 0.12485
995 | 0 | 0.12485
996 | 0.86 | 0.98485
997 | 0 | 0.12485
998 | 0 | 0.12485
999 | 0 | 0.12485
1000 | 0 | 0.12485
1001 | 0 | 0.12485
1002 | 6.6345 | 6.7594
1003 | 12.8996 | 13.0244
1004 | 0 | 0.12485
1005 | 1.3875 | 1.5124
1006 | 0 | 0.12485
1007 | 0 | 0.12485
1008 | 0 | 0.12485
1009 | 0 | 0.12485
1010 | 0 | 0.12485
1011 | 0 | 0.12485
1012 | 0 | 0.12485
1013 | 0 | 0.12485
1014 | 13.148 | 13.2729
1015 | 1.3448 | 1.4696
1016 | 1.7497 | 1.8745
1017 | 0 | 0.12485
1018 | 0 | 0.12485
1019 | 0 | 0.12485
1020 | 0.93364 | 1.0585
1021 | 0 | 0.12485
1022 | 0 | 0.12485
1023 | 0 | 0.12485
1024 | 0 | 0.12485
1025 | 0 | 0.12485
1026 | 6.6688 | 6.7937
1027 | 12.742 | 12.8668
1028 | 0 | 0.12485
1029 | 1.3746 | 1.4995
1030 | 0 | 0.12485
1031 | 0 | 0.12485
1032 | 0 | 0.12485
1033 | 0 | 0.12485
1034 | 0 | 0.12485
1035 | 0 | 0.12485
1036 | 0 | 0.12485
1037 | 0 | 0.12485
1038 | 13.0344 | 13.1593
1039 | 1.3345 | 1.4593
1040 | 1.7363 | 1.8612
1041 | 0 | 0.12485
1042 | 0 | 0.12485
1043 | 0 | 0.12485
1044 | 0.92728 | 1.0521
1045 | 0 | 0.12485
1046 | 0 | 0.12485
1047 | 0 | 0.12485
1048 | 0 | 0.12485
1049 | 0 | 0.12485
1050 | 6.6253 | 6.7502
1051 | 13.2853 | 13.4101
1052 | 0 | 0.12485
1053 | 1.3509 | 1.4757
1054 | 0 | 0.12485
1055 | 0 | 0.12485
1056 | 0 | 0.12485
1057 | 0 | 0.12485
1058 | 0 | 0.12485
1059 | 0 | 0.12485
1060 | 0 | 0.12485
1061 | 0 | 0.12485
1062 | 12.8409 | 12.9657
1063 | 1.424 | 1.5488
1064 | 1.8525 | 1.9773
1065 | 0 | 0.12485
1066 | 0 | 0.12485
1067 | 0 | 0.12485
1068 | 0.90166 | 1.0265
1069 | 0 | 0.12485
1070 | 0 | 0.12485
1071 | 0 | 0.12485
1072 | 0 | 0.12485
1073 | 0 | 0.12485
1074 | 6.6615 | 6.7863
1075 | 12.9622 | 13.0871
1076 | 0 | 0.12485
1077 | 1.3261 | 1.451
1078 | 0 | 0.12485
1079 | 0 | 0.12485
1080 | 0 | 0.12485
1081 | 0 | 0.12485
1082 | 0 | 0.12485
1083 | 0 | 0.12485
1084 | 0 | 0.12485
1085 | 0 | 0.12485
1086 | 12.6231 | 12.7479
1087 | 1.4108 | 1.5356
1088 | 1.8354 | 1.9602
1089 | 0 | 0.12485
1090 | 0 | 0.12485
1091 | 0 | 0.12485
1092 | 0.89335 | 1.0182
1093 | 0 | 0.12485
1094 | 0 | 0.12485
1095 | 0 | 0.12485
1096 | 0 | 0.12485
1097 | 0 | 0.12485
1098 | 6.6069 | 6.7317
1099 | 12.8735 | 12.9983
1100 | 0 | 0.12485
1101 | 1.4227 | 1.5475
1102 | 0 | 0.12485
1103 | 0 | 0.12485
1104 | 0 | 0.12485
1105 | 0 | 0.12485
1106 | 0 | 0.12485
1107 | 0 | 0.12485
1108 | 0 | 0.12485
1109 | 0 | 0.12485
1110 | 12.8275 | 12.9524
1111 | 1.3862 | 1.511
1112 | 1.8034 | 1.9282
1113 | 0 | 0.12485
1114 | 0 | 0.12485
1115 | 0 | 0.12485
1116 | 0.87786 | 1.0027
1117 | 0 | 0.12485
1118 | 0 | 0.12485
1119 | 0 | 0.12485
1120 | 0 | 0.12485
1121 | 0 | 0.12485
1122 | 6.5002 | 6.6251
1123 | 12.6909 | 12.8157
1124 | 0 | 0.12485
1125 | 1.4115 | 1.5364
1126 | 0 | 0.12485
1127 | 0 | 0.12485
1128 | 0 | 0.12485
1129 | 0 | 0.12485
1130 | 0 | 0.12485
1131 | 0 | 0.12485
1132 | 0 | 0.12485
1133 | 0 | 0.12485
1134 | 13.3431 | 13.4679
1135 | 1.3576 | 1.4825
1136 | 1.7663 | 1.8911
1137 | 0 | 0.12485
1138 | 0 | 0.12485
1139 | 0 | 0.12485
1140 | 0.8599 | 0.98474
1141 | 0 | 0.12485
1142 | 0 | 0.12485
1143 | 0 | 0.12485
1144 | 0 | 0.12485
1145 | 0 | 0.12485
1146 | 6.6338 | 6.7587
1147 | 12.8984 | 13.0232
1148 | 0 | 0.12485
1149 | 1.3874 | 1.5123
1150 | 0 | 0.12485
1151 | 0 | 0.12485
1152 | 0 | 0.12485
1153 | 0 | 0.12485
1154 | 0 | 0.12485
1155 | 0 | 0.12485
1156 | 0 | 0.12485
1157 | 0 | 0.12485
1158 | 13.1444 | 13.2693
1159 | 1.3445 | 1.4693
1160 | 1.7492 | 1.8741
1161 | 0 | 0.12485
1162 | 0 | 0.12485
1163 | 0 | 0.12485
1164 | 0.93341 | 1.0583
1165 | 0 | 0.12485
1166 | 0 | 0.12485
1167 | 0 | 0.12485
1168 | 0 | 0.12485
1169 | 0 | 0.12485
1170 | 6.6671 | 6.792
1171 | 12.7388 | 12.8636
1172 | 0 | 0.12485
1173 | 1.3744 | 1.4992
1174 | 0 | 0.12485
1175 | 0 | 0.12485
1176 | 0 | 0.12485
1177 | 0 | 0.12485
1178 | 0 | 0.12485
1179 | 0 | 0.12485
1180 | 0 | 0.12485
1181 | 0 | 0.12485
1182 | 13.0292 | 13.154
1183 | 1.334 | 1.4589
1184 | 1.7357 | 1.8605
1185 | 0 | 0.12485
1186 | 0 | 0.12485
1187 | 0 | 0.12485
1188 | 0.92692 | 1.0518
1189 | 0 | 0.12485
1190 | 0 | 0.12485
1191 | 0 | 0.12485
1192 | 0 | 0.12485
1193 | 0 | 0.12485
1194 | 6.6227 | 6.7476
1195 | 13.2806 | 13.4054
1196 | 0 | 0.12485
1197 | 1.3504 | 1.4752
1198 | 0 | 0.12485
1199 | 0 | 0.12485
1200 | 0 | 0.12485
1201 | 0 | 0.12485
1202 | 0 | 0.12485
1203 | 0 | 0.12485
1204 | 0 | 0.12485
1205 | 0 | 0.12485
1206 | 12.8337 | 12.9585
1207 | 1.4232 | 1.548
1208 | 1.8515 | 1.9763
1209 | 0 | 0.12485
1210 | 0 | 0.12485
1211 | 0 | 0.12485
1212 | 0.90117 | 1.026
1213 | 0 | 0.12485
1214 | 0 | 0.12485
1215 | 0 | 0.12485
1216 | 0 | 0.12485
1217 | 0 | 0.12485
1218 | 6.6577 | 6.7826
1219 | 12.9552 | 13.08
1220 | 0 | 0.12485
1221 | 1.3255 | 1.4503
1222 | 0 | 0.12485
1223 | 0 | 0.12485
1224 | 0 | 0.12485
1225 | 0 | 0.12485
1226 | 0 | 0.12485
1227 | 0 | 0.12485
1228 | 0 | 0.12485
1229 | 0 | 0.12485
1230 | 12.6146 | 12.7394
1231 | 1.4098 | 1.5347
1232 | 1.8341 | 1.959
1233 | 0 | 0.12485
1234 | 0 | 0.12485
1235 | 0 | 0.12485
1236 | 0.89275 | 1.0176
1237 | 0 | 0.12485
1238 | 0 | 0.12485
1239 | 0 | 0.12485
1240 | 0 | 0.12485
1241 | 0 | 0.12485
1242 | 6.6025 | 6.7274
1243 | 12.8658 | 12.9907
1244 | 0 | 0.12485
1245 | 1.4218 | 1.5466
1246 | 0 | 0.12485
1247 | 0 | 0.12485
1248 | 0 | 0.12485
1249 | 0 | 0.12485
1250 | 0 | 0.12485
1251 | 0 | 0.12485
1252 | 0 | 0.12485
1253 | 0 | 0.12485
1254 | 12.8168 | 12.9417
1255 | 1.3852 | 1.51
1256 | 1.8021 | 1.927
1257 | 0 | 0.12485
1258 | 0 | 0.12485
1259 | 0 | 0.12485
1260 | 0.87722 | 1.0021
1261 | 0 | 0.12485
1262 | 0 | 0.12485
1263 | 0 | 0.12485
1264 | 0 | 0.12485
1265 | 0 | 0.12485
1266 | 6.4956 | 6.6205
1267 | 12.6828 | 12.8077
1268 | 0 | 0.12485
1269 | 1.4105 | 1.5354
1270 | 0 | 0.12485
1271 | 0 | 0.12485
1272 | 0 | 0.12485
1273 | 0 | 0.12485
1274 | 0 | 0.12485
1275 | 0 | 0.12485
1276 | 0 | 0.12485
1277 | 0 | 0.12485
1278 | 13.3308 | 13.4557
1279 | 1.3563 | 1.4812
1280 | 1.7646 | 1.8894
1281 | 0 | 0.12485
1282 | 0 | 0.12485
1283 | 0 | 0.12485
1284 | 0.85905 | 0.9839
1285 | 0 | 0.12485
1286 | 0 | 0.12485
1287 | 0 | 0.12485
1288 | 0 | 0.12485
1289 | 0 | 0.12485
1290 | 6.6268 | 6.7516
1291 | 12.8859 | 13.0107
1292 | 0 | 0.12485
1293 | 1.3863 | 1.5111
1294 | 0 | 0.12485
1295 | 0 | 0.12485
1296 | 0 | 0.12485
1297 | 0 | 0.12485
1298 | 0 | 0.12485
1299 | 0 | 0.12485
1300 | 0 | 0.12485
1301 | 0 | 0.12485
1302 | 13.1312 | 13.2561
1303 | 1.3432 | 1.4681
1304 | 1.7476 | 1.8725
1305 | 0 | 0.12485
1306 | 0 | 0.12485
1307 | 0 | 0.12485
1308 | 0.93267 | 1.0575
1309 | 0 | 0.12485
1310 | 0 | 0.12485
1311 | 0 | 0.12485
1312 | 0 | 0.12485
1313 | 0 | 0.12485
1314 | 6.5477 | 6.6726
1315 | 12.7635 | 12.8883
1316 | 0 | 0.12485
1317 | 1.3751 | 1.5
1318 | 0 | 0.12485
1319 | 0 | 0.12485
1320 | 0 | 0.12485
1321 | 0 | 0.12485
1322 | 0 | 0.12485
1323 | 0 | 0.12485
1324 | 0 | 0.12485
1325 | 0 | 0.12485
1326 | 13.0328 | 13.1577
1327 | 1.3343 | 1.4592
1328 | 1.7361 | 1.861
1329 | 0 | 0.12485
1330 | 0 | 0.12485
1331 | 0 | 0.12485
1332 | 0.92652 | 1.0514
1333 | 0 | 0.12485
1334 | 0 | 0.12485
1335 | 0 | 0.12485
1336 | 0 | 0.12485
1337 | 0 | 0.12485
1338 | 6.6197 | 6.7445
1339 | 13.2735 | 13.3984
1340 | 0 | 0.12485
1341 | 1.3492 | 1.4741
1342 | 0 | 0.12485
1343 | 0 | 0.12485
1344 | 0 | 0.12485
1345 | 0 | 0.12485
1346 | 0 | 0.12485
1347 | 0 | 0.12485
1348 | 0 | 0.12485
1349 | 0 | 0.12485
1350 | 12.8203 | 12.9452
1351 | 1.4215 | 1.5463
1352 | 1.8493 | 1.9741
1353 | 0 | 0.12485
1354 | 0 | 0.12485
1355 | 0 | 0.12485
1356 | 0.90007 | 1.0249
1357 | 0 | 0.12485
1358 | 0 | 0.12485
1359 | 0 | 0.12485
1360 | 0 | 0.12485
1361 | 0 | 0.12485
1362 | 6.6488 | 6.7736
1363 | 12.9377 | 13.0626
1364 | 0 | 0.12485
1365 | 1.3239 | 1.4487
1366 | 0 | 0.12485
1367 | 0 | 0.12485
1368 | 0 | 0.12485
1369 | 0 | 0.12485
1370 | 0 | 0.12485
1371 | 0 | 0.12485
1372 | 0 | 0.12485
1373 | 0 | 0.12485
1374 | 12.5973 | 12.7222
1375 | 1.4078 | 1.5327
1376 | 1.8315 | 1.9563
1377 | 0 | 0.12485
1378 | 0 | 0.12485
1379 | 0 | 0.12485
1380 | 0.89145 | 1.0163
1381 | 0 | 0.12485
1382 | 0 | 0.12485
1383 | 0 | 0.12485
1384 | 0 | 0.12485
1385 | 0 | 0.12485
1386 | 6.5931 | 6.7179
1387 | 12.8491 | 12.9739
1388 | 0 | 0.12485
1389 | 1.4198 | 1.5446
1390 | 0 | 0.12485
1391 | 0 | 0.12485
1392 | 0 | 0.12485
1393 | 0 | 0.12485
1394 | 0 | 0.12485
1395 | 0 | 0.12485
1396 | 0 | 0.12485
1397 | 0 | 0.12485
1398 | 12.796 | 12.9208
1399 | 1.3833 | 1.5081
1400 | 1.7996 | 1.9244
1401 | 0 | 0.12485
1402 | 0 | 0.12485
1403 | 0 | 0.12485
1404 | 0.87597 | 1.0008
1405 | 0 | 0.12485
1406 | 0 | 0.12485
1407 | 0 | 0.12485
1408 | 0 | 0.12485
1409 | 0 | 0.12485
1410 | 6.4866 | 6.6115
1411 | 12.6669 | 12.7918
1412 | 0 | 0.12485
1413 | 1.4085 | 1.5333
1414 | 0 | 0.12485
1415 | 0 | 0.12485
1416 | 0 | 0.12485
1417 | 0 | 0.12485
1418 | 0 | 0.12485
1419 | 0 | 0.12485
1420 | 0 | 0.12485
1421 | 0 | 0.12485
1422 | 12.697 | 12.8219
1423 | 1.3745 | 1.4994
1424 | 1.7882 | 1.9131
1425 | 0 | 0.12485
1426 | 0 | 0.12485
1427 | 0 | 0.12485
1428 | 0.87047 | 0.99531
1429 | 0 | 0.12485
1430 | 0 | 0.12485
1431 | 0 | 0.12485
1432 | 0 | 0.12485
1433 | 0 | 0.12485
1434 | 6.6437 | 6.7686
1435 | 13.2795 | 13.4043
1436 | 0 | 0.12485
1437 | 1.3878 | 1.5127
1438 | 0 | 0.12485
1439 | 0 | 0.12485
1440 | 0 | 0.12485
1441 | 0 | 0.12485
1442 | 0 | 0.12485
1443 | 0 | 0.12485
1444 | 0 | 0.12485
1445 | 0 | 0.12485
1446 | 13.1386 | 13.2635
1447 | 1.343 | 1.4679
1448 | 1.7473 | 1.8722
1449 | 0 | 0.12485
1450 | 0 | 0.12485
1451 | 0 | 0.12485
1452 | 0.85066 | 0.9755
1453 | 0 | 0.12485
1454 | 0 | 0.12485
1455 | 0 | 0.12485
1456 | 0 | 0.12485
1457 | 0 | 0.12485
1458 | 6.5821 | 6.707
1459 | 12.8098 | 12.9346
1460 | 0 | 0.12485
1461 | 1.3793 | 1.5042
1462 | 0 | 0.12485
1463 | 0 | 0.12485
1464 | 0 | 0.12485
1465 | 0 | 0.12485
1466 | 0 | 0.12485
1467 | 0 | 0.12485
1468 | 0 | 0.12485
1469 | 0 | 0.12485
1470 | 13.0663 | 13.1911
1471 | 1.3374 | 1.4622
1472 | 1.74 | 1.8648
1473 | 0 | 0.12485
1474 | 0 | 0.12485
1475 | 0 | 0.12485
1476 | 0.92877 | 1.0536
1477 | 0 | 0.12485
1478 | 0 | 0.12485
1479 | 0 | 0.12485
1480 | 0 | 0.12485
1481 | 0 | 0.12485
1482 | 6.5201 | 6.645
1483 | 12.7162 | 12.8411
1484 | 0 | 0.12485
1485 | 1.3708 | 1.4956
1486 | 0 | 0.12485
1487 | 0 | 0.12485
1488 | 0 | 0.12485
1489 | 0 | 0.12485
1490 | 0 | 0.12485
1491 | 0 | 0.12485
1492 | 0 | 0.12485
1493 | 0 | 0.12485
1494 | 12.9908 | 13.1156
1495 | 1.3305 | 1.4554
1496 | 1.7311 | 1.856
1497 | 0 | 0.12485
1498 | 0 | 0.12485
1499 | 0 | 0.12485
1500 | 0.92392 | 1.0488
1501 | 0 | 0.12485
1502 | 0 | 0.12485
1503 | 0 | 0.12485
1504 | 0 | 0.12485
1505 | 0 | 0.12485
1506 | 6.6011 | 6.7259
1507 | 13.2394 | 13.3642
1508 | 0 | 0.12485
1509 | 1.3457 | 1.4705
1510 | 0 | 0.12485
1511 | 0 | 0.12485
1512 | 0 | 0.12485
1513 | 0 | 0.12485
1514 | 0 | 0.12485
1515 | 0 | 0.12485
1516 | 0 | 0.12485
1517 | 0 | 0.12485
1518 | 12.7844 | 12.9093
1519 | 1.4176 | 1.5424
1520 | 1.8441 | 1.969
1521 | 0 | 0.12485
1522 | 0 | 0.12485
1523 | 0 | 0.12485
1524 | 0.89755 | 1.0224
1525 | 0 | 0.12485
1526 | 0 | 0.12485
1527 | 0 | 0.12485
1528 | 0 | 0.12485
1529 | 0 | 0.12485
1530 | 6.4213 | 6.5461
1531 | 12.9702 | 13.0951
1532 | 0 | 0.12485
1533 | 1.325 | 1.4498
1534 | 0 | 0.12485
1535 | 0 | 0.12485
1536 | 0 | 0.12485
1537 | 0 | 0.12485
1538 | 0 | 0.12485
1539 | 0 | 0.12485
1540 | 0 | 0.12485
1541 | 0 | 0.12485
1542 | 12.6028 | 12.7277
1543 | 1.4063 | 1.5312
1544 | 1.8295 | 1.9544
1545 | 0 | 0.12485
1546 | 0 | 0.12485
1547 | 0 | 0.12485
1548 | 0.89046 | 1.0153
1549 | 0 | 0.12485
1550 | 0 | 0.12485
1551 | 0 | 0.12485
1552 | 0 | 0.12485
1553 | 0 | 0.12485
1554 | 6.5853 | 6.7101
1555 | 12.8346 | 12.9595
1556 | 0 | 0.12485
1557 | 1.3145 | 1.4394
1558 | 0 | 0.12485
1559 | 0 | 0.12485
1560 | 0 | 0.12485
1561 | 0 | 0.12485
1562 | 0 | 0.12485
1563 | 0 | 0.12485
1564 | 0 | 0.12485
1565 | 0 | 0.12485
1566 | 12.5099 | 12.6348
1567 | 1.4003 | 1.5252
1568 | 1.8218 | 1.9466
1569 | 0 | 0.12485
1570 | 0 | 0.12485
1571 | 0 | 0.12485
1572 | 0.88668 | 1.0115
1573 | 0 | 0.12485
1574 | 0 | 0.12485
1575 | 0 | 0.12485
1576 | 0 | 0.12485
1577 | 0 | 0.12485
1578 | 6.5592 | 6.6841
1579 | 12.7899 | 12.9148
1580 | 0 | 0.12485
1581 | 1.414 | 1.5389
1582 | 0 | 0.12485
1583 | 0 | 0.12485
1584 | 0 | 0.12485
1585 | 0 | 0.12485
1586 | 0 | 0.12485
1587 | 0 | 0.12485
1588 | 0 | 0.12485
1589 | 0 | 0.12485
1590 | 12.7406 | 12.8654
1591 | 1.3782 | 1.503
1592 | 1.7929 | 1.9178
1593 | 0 | 0.12485
1594 | 0 | 0.12485
1595 | 0 | 0.12485
1596 | 0.8727 | 0.99755
1597 | 0 | 0.12485
1598 | 0 | 0.12485
1599 | 0 | 0.12485
1600 | 0 | 0.12485
1601 | 0 | 0.12485
1602 | 6.4631 | 6.588
1603 | 12.6257 | 12.7505
1604 | 0 | 0.12485
1605 | 1.4037 | 1.5285
1606 | 0 | 0.12485
1607 | 0 | 0.12485
1608 | 0 | 0.12485
1609 | 0 | 0.12485
1610 | 0 | 0.12485
1611 | 0 | 0.12485
1612 | 0 | 0.12485
1613 | 0 | 0.12485
1614 | 12.6499 | 12.7748
1615 | 1.3701 | 1.495
1616 | 1.7825 | 1.9074
1617 | 0 | 0.12485
1618 | 0 | 0.12485
1619 | 0 | 0.12485
1620 | 0.86765 | 0.9925
1621 | 0 | 0.12485
1622 | 0 | 0.12485
1623 | 0 | 0.12485
1624 | 0 | 0.12485
1625 | 0 | 0.12485
1626 | 6.4276 | 6.5524
1627 | 12.5638 | 12.6887
1628 | 0 | 0.12485
1629 | 1.3996 | 1.5244
1630 | 0 | 0.12485
1631 | 0 | 0.12485
1632 | 0 | 0.12485
1633 | 0 | 0.12485
1634 | 0 | 0.12485
1635 | 0 | 0.12485
1636 | 0 | 0.12485
1637 | 0 | 0.12485
1638 | 12.6134 | 12.7383
1639 | 1.3669 | 1.4917
1640 | 1.7783 | 1.9031
1641 | 0 | 0.12485
1642 | 0 | 0.12485
1643 | 0 | 0.12485
1644 | 0.86559 | 0.99044
1645 | 0 | 0.12485
1646 | 0 | 0.12485
1647 | 0 | 0.12485
1648 | 0 | 0.12485
1649 | 0 | 0.12485
1650 | 6.4131 | 6.5379
1651 | 12.5385 | 12.6633
1652 | 0 | 0.12485
1653 | 1.3977 | 1.5225
1654 | 0 | 0.12485
1655 | 0 | 0.12485
1656 | 0 | 0.12485
1657 | 0 | 0.12485
1658 | 0 | 0.12485
1659 | 0 | 0.12485
1660 | 0 | 0.12485
1661 | 0 | 0.12485
1662 | 12.5961 | 12.7209
1663 | 1.3653 | 1.4902
1664 | 1.7763 | 1.9011
1665 | 0 | 0.12485
1666 | 0 | 0.12485
1667 | 0 | 0.12485
1668 | 0.8646 | 0.98945
1669 | 0 | 0.12485
1670 | 0 | 0.12485
1671 | 0 | 0.12485
1672 | 0 | 0.12485
1673 | 0 | 0.12485
1674 | 6.406 | 6.5309
1675 | 12.5261 | 12.651
1676 | 0 | 0.12485
1677 | 1.3966 | 1.5214
1678 | 0 | 0.12485
1679 | 0 | 0.12485
1680 | 0 | 0.12485
1681 | 0 | 0.12485
1682 | 0 | 0.12485
1683 | 0 | 0.12485
1684 | 0 | 0.12485
1685 | 0 | 0.12485
1686 | 12.5855 | 12.7104
1687 | 1.3644 | 1.4892
1688 | 1.775 | 1.8999
1689 | 0 | 0.12485
1690 | 0 | 0.12485
1691 | 0 | 0.12485
1692 | 0.86398 | 0.98883
1693 | 0 | 0.12485
1694 | 0 | 0.12485
1695 | 0 | 0.12485
1696 | 0 | 0.12485
1697 | 0 | 0.12485
1698 | 6.4016 | 6.5264
1699 | 12.5183 | 12.6432
1700 | 0 | 0.12485
1701 | 1.3957 | 1.5205
1702 | 0 | 0.12485
1703 | 0 | 0.12485
1704 | 0 | 0.12485
1705 | 0 | 0.12485
1706 | 0 | 0.12485
1707 | 0 | 0.12485
1708 | 0 | 0.12485
1709 | 0 | 0.12485
1710 | 12.5772 | 12.702
1711 | 1.3636 | 1.4885
1712 | 1.774 | 1.8988
1713 | 0 | 0.12485
1714 | 0 | 0.12485
1715 | 0 | 0.12485
1716 | 0.86348 | 0.98833
1717 | 0 | 0.12485
1718 | 0 | 0.12485
1719 | 0 | 0.12485
1720 | 0 | 0.12485
1721 | 0 | 0.12485
1722 | 6.398 | 6.5229
1723 | 12.512 | 12.6369
1724 | 0 | 0.12485
1725 | 1.3949 | 1.5197
1726 | 0 | 0.12485
1727 | 0 | 0.12485
1728 | 0 | 0.12485
1729 | 0 | 0.12485
1730 | 0 | 0.12485
1731 | 0 | 0.12485
1732 | 0 | 0.12485
1733 | 0 | 0.12485
1734 | 12.5695 | 12.6944
1735 | 1.3629 | 1.4877
1736 | 1.7731 | 1.8979
1737 | 0 | 0.12485
1738 | 0 | 0.12485
1739 | 0 | 0.12485
1740 | 0.86302 | 0.98787
1741 | 0 | 0.12485
1742 | 0 | 0.12485
1743 | 0 | 0.12485
1744 | 0 | 0.12485
1745 | 0 | 0.12485
1746 | 6.3947 | 6.5195
1747 | 12.5062 | 12.631
1748 | 0 | 0.12485
1749 | 1.3941 | 1.519
1750 | 0 | 0.12485
1751 | 0 | 0.12485
1752 | 0 | 0.12485
1753 | 0 | 0.12485
1754 | 0 | 0.12485
1755 | 0 | 0.12485
1756 | 0 | 0.12485
1757 | 0 | 0.12485
1758 | 12.562 | 12.6868
1759 | 1.3622 | 1.487
1760 | 1.7721 | 1.897
1761 | 0 | 0.12485
1762 | 0 | 0.12485
1763 | 0 | 0.12485
1764 | 0.86257 | 0.98741
1765 | 0 | 0.12485
1766 | 0 | 0.12485
1767 | 0 | 0.12485
1768 | 0 | 0.12485
1769 | 0 | 0.12485
1770 | 6.3914 | 6.5162
1771 | 12.5003 | 12.6252
1772 | 0 | 0.12485
1773 | 1.3933 | 1.5182
1774 | 0 | 0.12485
1775 | 0 | 0.12485
1776 | 0 | 0.12485
1777 | 0 | 0.12485
1778 | 0 | 0.12485
1779 | 0 | 0.12485
1780 | 0 | 0.12485
1781 | 0 | 0.12485
1782 | 12.5543 | 12.6791
1783 | 1.3615 | 1.4863
1784 | 1.7712 | 1.8961
1785 | 0 | 0.12485
1786 | 0 | 0.12485
1787 | 0 | 0.12485
1788 | 0.8621 | 0.98695
1789 | 0 | 0.12485
1790 | 0 | 0.12485
1791 | 0 | 0.12485
1792 | 0 | 0.12485
1793 | 0 | 0.12485
1794 | 6.388 | 6.5128
1795 | 12.4944 | 12.6192
1796 | 0 | 0.12485
1797 | 1.3925 | 1.5174
1798 | 0 | 0.12485
1799 | 0 | 0.12485
1800 | 0 | 0.12485
1801 | 0 | 0.12485
1802 | 0 | 0.12485
1803 | 0 | 0.12485
1804 | 0 | 0.12485
1805 | 0 | 0.12485
1806 | 12.5464 | 12.6713
1807 | 1.3607 | 1.4856
1808 | 1.7703 | 1.8951
1809 | 0 | 0.12485
1810 | 0 | 0.12485
1811 | 0 | 0.12485
1812 | 0.86162 | 0.98647
1813 | 0 | 0.12485
1814 | 0 | 0.12485
1815 | 0 | 0.12485
1816 | 0 | 0.12485
1817 | 0 | 0.12485
1818 | 6.3845 | 6.5094
1819 | 12.4883 | 12.6131
1820 | 0 | 0.12485
1821 | 1.3917 | 1.5165
1822 | 0 | 0.12485
1823 | 0 | 0.12485
1824 | 0 | 0.12485
1825 | 0 | 0.12485
1826 | 0 | 0.12485
1827 | 0 | 0.12485
1828 | 0 | 0.12485
1829 | 0 | 0.12485
1830 | 12.5383 | 12.6632
1831 | 1.36 | 1.4848
1832 | 1.7693 | 1.8941
1833 | 0 | 0.12485
1834 | 0 | 0.12485
1835 | 0 | 0.12485
1836 | 0.86114 | 0.98599
1837 | 0 | 0.12485
1838 | 0 | 0.12485
1839 | 0 | 0.12485
1840 | 0 | 0.12485
1841 | 0 | 0.12485
1842 | 6.381 | 6.5058
1843 | 12.482 | 12.6069
1844 | 0 | 0.12485
1845 | 1.3908 | 1.5157
1846 | 0 | 0.12485
1847 | 0 | 0.12485
1848 | 0 | 0.12485
1849 | 0 | 0.12485
1850 | 0 | 0.12485
1851 | 0 | 0.12485
1852 | 0 | 0.12485
1853 | 0 | 0.12485
1854 | 12.5301 | 12.6549
1855 | 1.3592 | 1.4841
1856 | 1.7683 | 1.8931
1857 | 0 | 0.12485
1858 | 0 | 0.12485
1859 | 0 | 0.12485
1860 | 0.86064 | 0.98548
1861 | 0 | 0.12485
1862 | 0 | 0.12485
1863 | 0 | 0.12485
1864 | 0 | 0.12485
1865 | 0 | 0.12485
1866 | 6.3774 | 6.5022
1867 | 12.4756 | 12.6005
1868 | 0 | 0.12485
1869 | 1.3899 | 1.5148
1870 | 0 | 0.12485
1871 | 0 | 0.12485
1872 | 0 | 0.12485
1873 | 0 | 0.12485
1874 | 0 | 0.12485
1875 | 0 | 0.12485
1876 | 0 | 0.12485
1877 | 0 | 0.12485
1878 | 12.5216 | 12.6464
1879 | 1.3584 | 1.4833
1880 | 1.7672 | 1.8921
1881 | 0 | 0.12485
1882 | 0 | 0.12485
1883 | 0 | 0.12485
1884 | 0.86012 | 0.98497
1885 | 0 | 0.12485
1886 | 0 | 0.12485
1887 | 0 | 0.12485
1888 | 0 | 0.12485
1889 | 0 | 0.12485
1890 | 6.3736 | 6.4985
1891 | 12.4691 | 12.5939
1892 | 0 | 0.12485
1893 | 1.389 | 1.5139
1894 | 0 | 0.12485
1895 | 0 | 0.12485
1896 | 0 | 0.12485
1897 | 0 | 0.12485
1898 | 0 | 0.12485
1899 | 0 | 0.12485
1900 | 0 | 0.12485
1901 | 0 | 0.12485
1902 | 12.5129 | 12.6377
1903 | 1.3576 | 1.4825
1904 | 1.7662 | 1.891
1905 | 0 | 0.12485
1906 | 0 | 0.12485
1907 | 0 | 0.12485
1908 | 0.85959 | 0.98444
1909 | 0 | 0.12485
1910 | 0 | 0.12485
1911 | 0 | 0.12485
1912 | 0 | 0.12485
1913 | 0 | 0.12485
1914 | 6.3698 | 6.4947
1915 | 12.4623 | 12.5872
1916 | 0 | 0.12485
1917 | 1.3881 | 1.513
1918 | 0 | 0.12485
1919 | 0 | 0.12485
1920 | 0 | 0.12485
1921 | 0 | 0.12485
1922 | 0 | 0.12485
1923 | 0 | 0.12485
1924 | 0 | 0.12485
1925 | 0 | 0.12485
1926 | 12.504 | 12.6288
1927 | 1.3568 | 1.4816
1928 | 1.7651 | 1.8899
1929 | 0 | 0.12485
1930 | 0 | 0.12485
1931 | 0 | 0.12485
1932 | 0.85906 | 0.9839
1933 | 0 | 0.12485
1934 | 0 | 0.12485
1935 | 0 | 0.12485
1936 | 0 | 0.12485
1937 | 0 | 0.12485
1938 | 6.3659 | 6.4908
1939 | 12.4554 | 12.5803
1940 | 0 | 0.12485
1941 | 1.3872 | 1.512
1942 | 0 | 0.12485
1943 | 0 | 0.12485
1944 | 0 | 0.12485
1945 | 0 | 0.12485
1946 | 0 | 0.12485
1947 | 0 | 0.12485
1948 | 0 | 0.12485
1949 | 0 | 0.12485
1950 | 12.4949 | 12.6197
1951 | 1.3559 | 1.4808
1952 | 1.764 | 1.8888
1953 | 0 | 0.12485
1954 | 0 | 0.12485
1955 | 0 | 0.12485
1956 | 0.8585 | 0.98335
1957 | 0 | 0.12485
1958 | 0 | 0.12485
1959 | 0 | 0.12485
1960 | 0 | 0.12485
1961 | 0 | 0.12485
1962 | 6.3619 | 6.4868
1963 | 12.4484 | 12.5732
1964 | 0 | 0.12485
1965 | 1.3862 | 1.511
1966 | 0 | 0.12485
1967 | 0 | 0.12485
1968 | 0 | 0.12485
1969 | 0 | 0.12485
1970 | 0 | 0.12485
1971 | 0 | 0.12485
1972 | 0 | 0.12485
1973 | 0 | 0.12485
1974 | 12.4856 | 12.6104
1975 | 1.355 | 1.4799
1976 | 1.7628 | 1.8877
1977 | 0 | 0.12485
1978 | 0 | 0.12485
1979 | 0 | 0.12485
1980 | 0.85794 | 0.98279
1981 | 0 | 0.12485
1982 | 0 | 0.12485
1983 | 0 | 0.12485
1984 | 0 | 0.12485
1985 | 0 | 0.12485
1986 | 6.3578 | 6.4827
1987 | 12.4412 | 12.566
1988 | 0 | 0.12485
1989 | 1.3852 | 1.51
1990 | 0 | 0.12485
1991 | 0 | 0.12485
1992 | 0 | 0.12485
1993 | 0 | 0.12485
1994 | 0 | 0.12485
1995 | 0 | 0.12485
1996 | 0 | 0.12485
1997 | 0 | 0.12485
1998 | 12.4761 | 12.6009
1999 | 1.3542 | 1.479
2000 | 1.7617 | 1.8865
2001 | 0 | 0.12485
2002 | 0 | 0.12485
2003 | 0 | 0.12485
2004 | 0.85736 | 0.98221
2005 | 0 | 0.12485
2006 | 0 | 0.12485
2007 | 0 | 0.12485
2008 | 0 | 0.12485
2009 | 0 | 0.12485
2010 | 6.3536 | 6.4785
2011 | 12.4338 | 12.5586
2012 | 0 | 0.12485
2013 | 1.3842 | 1.509
2014 | 0 | 0.12485
2015 | 0 | 0.12485
2016 | 0 | 0.12485
2017 | 0 | 0.12485
2018 | 0 | 0.12485
2019 | 0 | 0.12485
2020 | 0 | 0.12485
2021 | 0 | 0.12485
2022 | 12.4663 | 12.5912
2023 | 1.3533 | 1.4781
2024 | 1.7605 | 1.8853
2025 | 0 | 0.12485
2026 | 0 | 0.12485
2027 | 0 | 0.12485
2028 | 0.85677 | 0.98162
2029 | 0 | 0.12485
2030 | 0 | 0.12485
2031 | 0 | 0.12485
2032 | 0 | 0.12485
2033 | 0 | 0.12485
2034 | 6.3493 | 6.4742
2035 | 12.4261 | 12.551
2036 | 0 | 0.12485
2037 | 1.3831 | 1.508
2038 | 0 | 0.12485
2039 | 0 | 0.12485
2040 | 0 | 0.12485
2041 | 0 | 0.12485
2042 | 0 | 0.12485
2043 | 0 | 0.12485
2044 | 0 | 0.12485
2045 | 0 | 0.12485
2046 | 12.4564 | 12.5812
2047 | 1.3523 | 1.4772
2048 | 1.7593 | 1.8841
2049 | 0 | 0.12485
2050 | 0 | 0.12485
2051 | 0 | 0.12485
2052 | 0.85617 | 0.98102
2053 | 0 | 0.12485
2054 | 0 | 0.12485
2055 | 0 | 0.12485
2056 | 0 | 0.12485
2057 | 0 | 0.12485
2058 | 6.3449 | 6.4697
2059 | 12.4181 | 12.543
2060 | 0 | 0.12485
2061 | 1.382 | 1.5069
2062 | 0 | 0.12485
2063 | 0 | 0.12485
2064 | 0 | 0.12485
2065 | 0 | 0.12485
2066 | 0 | 0.12485
2067 | 0 | 0.12485
2068 | 0 | 0.12485
2069 | 0 | 0.12485
2070 | 12.4461 | 12.5709
2071 | 1.3513 | 1.4761
2072 | 1.7579 | 1.8827
2073 | 0 | 0.12485
2074 | 0 | 0.12485
2075 | 0 | 0.12485
2076 | 0.85549 | 0.98034
2077 | 0 | 0.12485
2078 | 0 | 0.12485
2079 | 0 | 0.12485
2080 | 0 | 0.12485
2081 | 0 | 0.12485
2082 | 6.3399 | 6.4647
2083 | 12.4092 | 12.534
2084 | 0 | 0.12485
2085 | 1.3809 | 1.5057
2086 | 0 | 0.12485
2087 | 0 | 0.12485
2088 | 0 | 0.12485
2089 | 0 | 0.12485
2090 | 0 | 0.12485
2091 | 0 | 0.12485
2092 | 0 | 0.12485
2093 | 0 | 0.12485
2094 | 12.4352 | 12.5601
2095 | 1.35 | 1.4748
2096 | 1.7562 | 1.881
2097 | 0 | 0.12485
2098 | 0 | 0.12485
2099 | 0 | 0.12485
2100 | 0.85466 | 0.97951
2101 | 0 | 0.12485
2102 | 0 | 0.12485
2103 | 0 | 0.12485
2104 | 0 | 0.12485
2105 | 0 | 0.12485
2106 | 6.3338 | 6.4587
2107 | 12.3985 | 12.5234
2108 | 0 | 0.12485
2109 | 1.3796 | 1.5045
2110 | 0 | 0.12485
2111 | 0 | 0.12485
2112 | 0 | 0.12485
2113 | 0 | 0.12485
2114 | 0 | 0.12485
2115 | 0 | 0.12485
2116 | 0 | 0.12485
2117 | 0 | 0.12485
2118 | 12.4233 | 12.5482
2119 | 1.3486 | 1.4735
2120 | 1.7544 | 1.8793
2121 | 0 | 0.12485
2122 | 0 | 0.12485
2123 | 0 | 0.12485
2124 | 0.85379 | 0.97863
2125 | 0 | 0.12485
2126 | 0 | 0.12485
2127 | 0 | 0.12485
2128 | 0 | 0.12485
2129 | 0 | 0.12485
2130 | 6.3275 | 6.4523
2131 | 12.3873 | 12.5121
2132 | 0 | 0.12485
2133 | 1.3783 | 1.5032
2134 | 0 | 0.12485
2135 | 0 | 0.12485
2136 | 0 | 0.12485
2137 | 0 | 0.12485
2138 | 0 | 0.12485
2139 | 0 | 0.12485
2140 | 0 | 0.12485
2141 | 0 | 0.12485
2142 | 12.411 | 12.5359
2143 | 1.3472 | 1.4721
2144 | 1.7526 | 1.8774
2145 | 0 | 0.12485
2146 | 0 | 0.12485
2147 | 0 | 0.12485
2148 | 0.85289 | 0.97773
2149 | 0 | 0.12485
2150 | 0 | 0.12485
2151 | 0 | 0.12485
2152 | 0 | 0.12485
2153 | 0 | 0.12485
2154 | 6.321 | 6.4458
2155 | 12.3758 | 12.5006
2156 | 0 | 0.12485
2157 | 1.377 | 1.5018
2158 | 0 | 0.12485
2159 | 0 | 0.12485
2160 | 0 | 0.12485
2161 | 0 | 0.12485
2162 | 0 | 0.12485
2163 | 0 | 0.12485
2164 | 0 | 0.12485
2165 | 0 | 0.12485
2166 | 12.3985 | 12.5233
2167 | 1.3458 | 1.4706
2168 | 1.7507 | 1.8756
2169 | 0 | 0.12485
2170 | 0 | 0.12485
2171 | 0 | 0.12485
2172 | 0.85197 | 0.97682
2173 | 0 | 0.12485
2174 | 0 | 0.12485
2175 | 0 | 0.12485
2176 | 0 | 0.12485
2177 | 0 | 0.12485
2178 | 6.3144 | 6.4392
2179 | 12.3641 | 12.4889
2180 | 0 | 0.12485
2181 | 1.3756 | 1.5005
2182 | 0 | 0.12485
2183 | 0 | 0.12485
2184 | 0 | 0.12485
2185 | 0 | 0.12485
2186 | 0 | 0.12485
2187 | 0 | 0.12485
2188 | 0 | 0.12485
2189 | 0 | 0.12485
2190 | 12.3857 | 12.5106
2191 | 1.3443 | 1.4692
2192 | 1.7489 | 1.8737
2193 | 0 | 0.12485
2194 | 0 | 0.12485
2195 | 0 | 0.12485
2196 | 0.85104 | 0.97589
2197 | 0 | 0.12485
2198 | 0 | 0.12485
2199 | 0 | 0.12485
2200 | 0 | 0.12485
2201 | 0 | 0.12485
2202 | 6.3076 | 6.4325
2203 | 12.3522 | 12.477
2204 | 0 | 0.12485
2205 | 1.3742 | 1.4991
2206 | 0 | 0.12485
2207 | 0 | 0.12485
2208 | 0 | 0.12485
2209 | 0 | 0.12485
2210 | 0 | 0.12485
2211 | 0 | 0.12485
2212 | 0 | 0.12485
2213 | 0 | 0.12485
2214 | 12.3728 | 12.4976
2215 | 1.3429 | 1.4677
2216 | 1.7469 | 1.8718
2217 | 0 | 0.12485
2218 | 0 | 0.12485
2219 | 0 | 0.12485
2220 | 0.85009 | 0.97494
2221 | 0 | 0.12485
2222 | 0 | 0.12485
2223 | 0 | 0.12485
2224 | 0 | 0.12485
2225 | 0 | 0.12485
2226 | 6.3008 | 6.4256
2227 | 12.3401 | 12.4649
2228 | 0 | 0.12485
2229 | 1.3728 | 1.4977
2230 | 0 | 0.12485
2231 | 0 | 0.12485
2232 | 0 | 0.12485
2233 | 0 | 0.12485
2234 | 0 | 0.12485
2235 | 0 | 0.12485
2236 | 0 | 0.12485
2237 | 0 | 0.12485
2238 | 12.3596 | 12.4844
2239 | 1.3414 | 1.4662
2240 | 1.745 | 1.8698
2241 | 0 | 0.12485
2242 | 0 | 0.12485
2243 | 0 | 0.12485
2244 | 0.84913 | 0.97398
2245 | 0 | 0.12485
2246 | 0 | 0.12485
2247 | 0 | 0.12485
2248 | 0 | 0.12485
2249 | 0 | 0.12485
2250 | 6.2938 | 6.4187
2251 | 12.3278 | 12.4526
2252 | 0 | 0.12485
2253 | 1.3714 | 1.4963
2254 | 0 | 0.12485
2255 | 0 | 0.12485
2256 | 0 | 0.12485
2257 | 0 | 0.12485
2258 | 0 | 0.12485
2259 | 0 | 0.12485
2260 | 0 | 0.12485
2261 | 0 | 0.12485
2262 | 12.3462 | 12.4711
2263 | 1.3399 | 1.4647
2264 | 1.743 | 1.8678
2265 | 0 | 0.12485
2266 | 0 | 0.12485
2267 | 0 | 0.12485
2268 | 0.84815 | 0.973
2269 | 0 | 0.12485
2270 | 0 | 0.12485
2271 | 0 | 0.12485
2272 | 0 | 0.12485
2273 | 0 | 0.12485
2274 | 6.2868 | 6.4116
2275 | 12.3153 | 12.4401
2276 | 0 | 0.12485
2277 | 1.2672 | 1.3921
2278 | 0 | 0.12485
2279 | 0 | 0.12485
2280 | 0 | 0.12485
2281 | 0 | 0.12485
2282 | 0 | 0.12485
2283 | 0 | 0.12485
2284 | 0 | 0.12485
2285 | 0 | 0.12485
2286 | 12.0709 | 12.1957
2287 | 1.3578 | 1.4826
2288 | 1.7663 | 1.8911
2289 | 0 | 0.12485
2290 | 0 | 0.12485
2291 | 0 | 0.12485
2292 | 0.85942 | 0.98427
2293 | 0 | 0.12485
2294 | 0 | 0.12485
2295 | 0 | 0.12485
2296 | 0 | 0.12485
2297 | 0 | 0.12485
2298 | 6.363 | 6.4878
2299 | 12.4436 | 12.5685
2300 | 0 | 0.12485
2301 | 1.2789 | 1.4038
2302 | 0 | 0.12485
2303 | 0 | 0.12485
2304 | 0 | 0.12485
2305 | 0 | 0.12485
2306 | 0 | 0.12485
2307 | 0 | 0.12485
2308 | 0 | 0.12485
2309 | 0 | 0.12485
2310 | 12.1736 | 12.2985
2311 | 1.3633 | 1.4882
2312 | 1.7735 | 1.8983
2313 | 0 | 0.12485
2314 | 0 | 0.12485
2315 | 0 | 0.12485
2316 | 0.8629 | 0.98775
2317 | 0 | 0.12485
2318 | 0 | 0.12485
2319 | 0 | 0.12485
2320 | 0 | 0.12485
2321 | 0 | 0.12485
2322 | 6.1749 | 6.2997
2323 | 12.5373 | 12.6621
2324 | 0 | 0.12485
2325 | 1.2856 | 1.4104
2326 | 0 | 0.12485
2327 | 0 | 0.12485
2328 | 0 | 0.12485
2329 | 0 | 0.12485
2330 | 0 | 0.12485
2331 | 0 | 0.12485
2332 | 0 | 0.12485
2333 | 0 | 0.12485
2334 | 12.2318 | 12.3567
2335 | 1.2631 | 1.388
2336 | 1.6434 | 1.7682
2337 | 0 | 0.12485
2338 | 0 | 0.12485
2339 | 0 | 0.12485
2340 | 0.88282 | 1.0077
2341 | 0 | 0.12485
2342 | 0 | 0.12485
2343 | 0 | 0.12485
2344 | 0 | 0.12485
2345 | 0 | 0.12485
2346 | 6.3098 | 6.4346
2347 | 12.5266 | 12.6515
2348 | 0 | 0.12485
2349 | 1.3109 | 1.4358
2350 | 0 | 0.12485
2351 | 0 | 0.12485
2352 | 0 | 0.12485
2353 | 0 | 0.12485
2354 | 0 | 0.12485
2355 | 0 | 0.12485
2356 | 0 | 0.12485
2357 | 0 | 0.12485
2358 | 12.4378 | 12.5626
2359 | 1.2803 | 1.4051
2360 | 1.6656 | 1.7904
2361 | 0 | 0.12485
2362 | 0 | 0.12485
2363 | 0 | 0.12485
2364 | 0.85524 | 0.98009
2365 | 0 | 0.12485
2366 | 0 | 0.12485
2367 | 0 | 0.12485
2368 | 0 | 0.12485
2369 | 0 | 0.12485
2370 | 6.2812 | 6.406
2371 | 12.2884 | 12.4133
2372 | 0 | 0.12485
2373 | 1.3291 | 1.454
2374 | 0 | 0.12485
2375 | 0 | 0.12485
2376 | 0 | 0.12485
2377 | 0 | 0.12485
2378 | 0 | 0.12485
2379 | 0 | 0.12485
2380 | 0 | 0.12485
2381 | 0 | 0.12485
2382 | 12.5887 | 12.7135
2383 | 1.2905 | 1.4153
2384 | 1.6788 | 1.8037
2385 | 0 | 0.12485
2386 | 0 | 0.12485
2387 | 0 | 0.12485
2388 | 0.81699 | 0.94184
2389 | 0 | 0.12485
2390 | 0 | 0.12485
2391 | 0 | 0.12485
2392 | 0 | 0.12485
2393 | 0 | 0.12485
2394 | 6.323 | 6.4478
2395 | 12.3388 | 12.4637
2396 | 0 | 0.12485
2397 | 1.3314 | 1.4562
2398 | 0 | 0.12485
2399 | 0 | 0.12485
2400 | 0 | 0.12485
2401 | 0 | 0.12485
2402 | 0 | 0.12485
2403 | 0 | 0.12485
2404 | 0 | 0.12485
2405 | 0 | 0.12485
2406 | 12.6046 | 12.7294
2407 | 1.2908 | 1.4157
2408 | 1.6792 | 1.8041
2409 | 0 | 0.12485
2410 | 0 | 0.12485
2411 | 0 | 0.12485
2412 | 0.81717 | 0.94202
2413 | 0 | 0.12485
2414 | 0 | 0.12485
2415 | 0 | 0.12485
2416 | 0 | 0.12485
2417 | 0 | 0.12485
2418 | 6.3197 | 6.4445
2419 | 12.3274 | 12.4523
2420 | 0 | 0.12485
2421 | 1.3299 | 1.4548
2422 | 0 | 0.12485
2423 | 0 | 0.12485
2424 | 0 | 0.12485
2425 | 0 | 0.12485
2426 | 0 | 0.12485
2427 | 0 | 0.12485
2428 | 0 | 0.12485
2429 | 0 | 0.12485
2430 | 12.5902 | 12.715
2431 | 1.2892 | 1.4141
2432 | 1.6772 | 1.802
2433 | 0 | 0.12485
2434 | 0 | 0.12485
2435 | 0 | 0.12485
2436 | 0.81615 | 0.941
2437 | 0 | 0.12485
2438 | 0 | 0.12485
2439 | 0 | 0.12485
2440 | 0 | 0.12485
2441 | 0 | 0.12485
2442 | 6.311 | 6.4359
2443 | 12.3102 | 12.4351
2444 | 0 | 0.12485
2445 | 1.3281 | 1.453
2446 | 0 | 0.12485
2447 | 0 | 0.12485
2448 | 0 | 0.12485
2449 | 0 | 0.12485
2450 | 0 | 0.12485
2451 | 0 | 0.12485
2452 | 0 | 0.12485
2453 | 0 | 0.12485
2454 | 12.5729 | 12.6978
2455 | 1.2875 | 1.4123
2456 | 1.6749 | 1.7997
2457 | 0 | 0.12485
2458 | 0 | 0.12485
2459 | 0 | 0.12485
2460 | 0.81501 | 0.93986
2461 | 0 | 0.12485
2462 | 0 | 0.12485
2463 | 0 | 0.12485
2464 | 0 | 0.12485
2465 | 0 | 0.12485
2466 | 6.3018 | 6.4267
2467 | 12.2923 | 12.4171
2468 | 0 | 0.12485
2469 | 1.3262 | 1.4511
2470 | 0 | 0.12485
2471 | 0 | 0.12485
2472 | 0 | 0.12485
2473 | 0 | 0.12485
2474 | 0 | 0.12485
2475 | 0 | 0.12485
2476 | 0 | 0.12485
2477 | 0 | 0.12485
2478 | 12.5552 | 12.6801
2479 | 1.2857 | 1.4105
2480 | 1.6725 | 1.7973
2481 | 0 | 0.12485
2482 | 0 | 0.12485
2483 | 0 | 0.12485
2484 | 0.81386 | 0.93871
2485 | 0 | 0.12485
2486 | 0 | 0.12485
2487 | 0 | 0.12485
2488 | 0 | 0.12485
2489 | 0 | 0.12485
2490 | 6.2934 | 6.4182
2491 | 12.2751 | 12.4
2492 | 0 | 0.12485
2493 | 1.3244 | 1.4493
2494 | 0 | 0.12485
2495 | 0 | 0.12485
2496 | 0 | 0.12485
2497 | 0 | 0.12485
2498 | 0 | 0.12485
2499 | 0 | 0.12485
2500 | 0 | 0.12485
2501 | 0 | 0.12485
2502 | 12.5378 | 12.6627
2503 | 1.2839 | 1.4087
2504 | 1.6702 | 1.795
2505 | 0 | 0.12485
2506 | 0 | 0.12485
2507 | 0 | 0.12485
2508 | 0.81271 | 0.93755
2509 | 0 | 0.12485
2510 | 0 | 0.12485
2511 | 0 | 0.12485
2512 | 0 | 0.12485
2513 | 0 | 0.12485
2514 | 6.2858 | 6.4107
2515 | 12.2588 | 12.3836
2516 | 0 | 0.12485
2517 | 1.3226 | 1.4475
2518 | 0 | 0.12485
2519 | 0 | 0.12485
2520 | 0 | 0.12485
2521 | 0 | 0.12485
2522 | 0 | 0.12485
2523 | 0 | 0.12485
2524 | 0 | 0.12485
2525 | 0 | 0.12485
2526 | 12.3202 | 12.4451
2527 | 1.2957 | 1.4206
2528 | 1.6855 | 1.8104
2529 | 0 | 0.12485
2530 | 0 | 0.12485
2531 | 0 | 0.12485
2532 | 0.82013 | 0.94498
2533 | 0 | 0.12485
2534 | 0 | 0.12485
2535 | 0 | 0.12485
2536 | 0 | 0.12485
2537 | 0 | 0.12485
2538 | 6.0888 | 6.2137
2539 | 11.9703 | 12.0952
2540 | 0 | 0.12485
2541 | 1.3408 | 1.4656
2542 | 0 | 0.12485
2543 | 0 | 0.12485
2544 | 0 | 0.12485
2545 | 0 | 0.12485
2546 | 0 | 0.12485
2547 | 0 | 0.12485
2548 | 0 | 0.12485
2549 | 0 | 0.12485
2550 | 12.068 | 12.1929
2551 | 1.314 | 1.4388
2552 | 1.7093 | 1.8341
2553 | 0 | 0.12485
2554 | 0 | 0.12485
2555 | 0 | 0.12485
2556 | 0.8316 | 0.95644
2557 | 0 | 0.12485
2558 | 0 | 0.12485
2559 | 0 | 0.12485
2560 | 0 | 0.12485
2561 | 0 | 0.12485
2562 | 6.1683 | 6.2932
2563 | 12.1075 | 12.2323
2564 | 0 | 0.12485
2565 | 1.2483 | 1.3731
2566 | 0 | 0.12485
2567 | 0 | 0.12485
2568 | 0 | 0.12485
2569 | 0 | 0.12485
2570 | 0 | 0.12485
2571 | 0 | 0.12485
2572 | 0 | 0.12485
2573 | 0 | 0.12485
2574 | 11.8947 | 12.0196
2575 | 1.3379 | 1.4628
2576 | 1.7404 | 1.8652
2577 | 0 | 0.12485
2578 | 0 | 0.12485
2579 | 0 | 0.12485
2580 | 0.84669 | 0.97154
2581 | 0 | 0.12485
2582 | 0 | 0.12485
2583 | 0 | 0.12485
2584 | 0 | 0.12485
2585 | 0 | 0.12485
2586 | 6.0594 | 6.1843
2587 | 12.3309 | 12.4558
2588 | 0 | 0.12485
2589 | 1.2654 | 1.3902
2590 | 0 | 0.12485
2591 | 0 | 0.12485
2592 | 0 | 0.12485
2593 | 0 | 0.12485
2594 | 0 | 0.12485
2595 | 0 | 0.12485
2596 | 0 | 0.12485
2597 | 0 | 0.12485
2598 | 12.0441 | 12.169
2599 | 1.246 | 1.3708
2600 | 1.621 | 1.7458
2601 | 0 | 0.12485
2602 | 0 | 0.12485
2603 | 0 | 0.12485
2604 | 0.86974 | 0.99458
2605 | 0 | 0.12485
2606 | 0 | 0.12485
2607 | 0 | 0.12485
2608 | 0 | 0.12485
2609 | 0 | 0.12485
2610 | 6.2155 | 6.3404
2611 | 11.9519 | 12.0767
2612 | 0 | 0.12485
2613 | 1.3019 | 1.4267
2614 | 0 | 0.12485
2615 | 0 | 0.12485
2616 | 0 | 0.12485
2617 | 0 | 0.12485
2618 | 0 | 0.12485
2619 | 0 | 0.12485
2620 | 0 | 0.12485
2621 | 0 | 0.12485
2622 | 12.3413 | 12.4661
2623 | 1.268 | 1.3928
2624 | 1.6495 | 1.7743
2625 | 0 | 0.12485
2626 | 0 | 0.12485
2627 | 0 | 0.12485
2628 | 0.80259 | 0.92744
2629 | 0 | 0.12485
2630 | 0 | 0.12485
2631 | 0 | 0.12485
2632 | 0 | 0.12485
2633 | 0 | 0.12485
2634 | 6.2165 | 6.3414
2635 | 12.1421 | 12.267
2636 | 0 | 0.12485
2637 | 1.3115 | 1.4364
2638 | 0 | 0.12485
2639 | 0 | 0.12485
2640 | 0 | 0.12485
2641 | 0 | 0.12485
2642 | 0 | 0.12485
2643 | 0 | 0.12485
2644 | 0 | 0.12485
2645 | 0 | 0.12485
2646 | 12.2183 | 12.3432
2647 | 1.2864 | 1.4113
2648 | 1.6734 | 1.7983
2649 | 0 | 0.12485
2650 | 0 | 0.12485
2651 | 0 | 0.12485
2652 | 0.81416 | 0.939
2653 | 0 | 0.12485
2654 | 0 | 0.12485
2655 | 0 | 0.12485
2656 | 0 | 0.12485
2657 | 0 | 0.12485
2658 | 6.046 | 6.1709
2659 | 11.8952 | 12.02
2660 | 0 | 0.12485
2661 | 1.3321 | 1.457
2662 | 0 | 0.12485
2663 | 0 | 0.12485
2664 | 0 | 0.12485
2665 | 0 | 0.12485
2666 | 0 | 0.12485
2667 | 0 | 0.12485
2668 | 0 | 0.12485
2669 | 0 | 0.12485
2670 | 11.988 | 12.1129
2671 | 1.3049 | 1.4298
2672 | 1.6975 | 1.8223
2673 | 0 | 0.12485
2674 | 0 | 0.12485
2675 | 0 | 0.12485
2676 | 0.82579 | 0.95064
2677 | 0 | 0.12485
2678 | 0 | 0.12485
2679 | 0 | 0.12485
2680 | 0 | 0.12485
2681 | 0 | 0.12485
2682 | 6.1263 | 6.2511
2683 | 12.0331 | 12.158
2684 | 0 | 0.12485
2685 | 1.2415 | 1.3664
2686 | 0 | 0.12485
2687 | 0 | 0.12485
2688 | 0 | 0.12485
2689 | 0 | 0.12485
2690 | 0 | 0.12485
2691 | 0 | 0.12485
2692 | 0 | 0.12485
2693 | 0 | 0.12485
2694 | 11.8313 | 11.9561
2695 | 1.3299 | 1.4548
2696 | 1.73 | 1.8548
2697 | 0 | 0.12485
2698 | 0 | 0.12485
2699 | 0 | 0.12485
2700 | 0.84154 | 0.96639
2701 | 0 | 0.12485
2702 | 0 | 0.12485
2703 | 0 | 0.12485
2704 | 0 | 0.12485
2705 | 0 | 0.12485
2706 | 6.0223 | 6.1471
2707 | 12.2606 | 12.3854
2708 | 0 | 0.12485
2709 | 1.2573 | 1.3822
2710 | 0 | 0.12485
2711 | 0 | 0.12485
2712 | 0 | 0.12485
2713 | 0 | 0.12485
2714 | 0 | 0.12485
2715 | 0 | 0.12485
2716 | 0 | 0.12485
2717 | 0 | 0.12485
2718 | 11.9684 | 12.0932
2719 | 1.239 | 1.3639
2720 | 1.6119 | 1.7367
2721 | 0 | 0.12485
2722 | 0 | 0.12485
2723 | 0 | 0.12485
2724 | 0.86571 | 0.99056
2725 | 0 | 0.12485
2726 | 0 | 0.12485
2727 | 0 | 0.12485
2728 | 0 | 0.12485
2729 | 0 | 0.12485
2730 | 6.0725 | 6.1973
2731 | 11.9322 | 12.057
2732 | 0 | 0.12485
2733 | 1.2955 | 1.4204
2734 | 0 | 0.12485
2735 | 0 | 0.12485
2736 | 0 | 0.12485
2737 | 0 | 0.12485
2738 | 0 | 0.12485
2739 | 0 | 0.12485
2740 | 0 | 0.12485
2741 | 0 | 0.12485
2742 | 12.2764 | 12.4013
2743 | 1.2602 | 1.385
2744 | 1.6392 | 1.7641
2745 | 0 | 0.12485
2746 | 0 | 0.12485
2747 | 0 | 0.12485
2748 | 0.79753 | 0.92238
2749 | 0 | 0.12485
2750 | 0 | 0.12485
2751 | 0 | 0.12485
2752 | 0 | 0.12485
2753 | 0 | 0.12485
2754 | 6.1785 | 6.3033
2755 | 12.0573 | 12.1822
2756 | 0 | 0.12485
2757 | 1.3021 | 1.4269
2758 | 0 | 0.12485
2759 | 0 | 0.12485
2760 | 0 | 0.12485
2761 | 0 | 0.12485
2762 | 0 | 0.12485
2763 | 0 | 0.12485
2764 | 0 | 0.12485
2765 | 0 | 0.12485
2766 | 11.7225 | 11.8474
2767 | 1.2856 | 1.4105
2768 | 1.6724 | 1.7972
2769 | 0 | 0.12485
2770 | 0 | 0.12485
2771 | 0 | 0.12485
2772 | 0.81355 | 0.9384
2773 | 0 | 0.12485
2774 | 0 | 0.12485
2775 | 0 | 0.12485
2776 | 0 | 0.12485
2777 | 0 | 0.12485
2778 | 6.0405 | 6.1653
2779 | 11.8845 | 12.0094
2780 | 0 | 0.12485
2781 | 1.228 | 1.3528
2782 | 0 | 0.12485
2783 | 0 | 0.12485
2784 | 0 | 0.12485
2785 | 0 | 0.12485
2786 | 0 | 0.12485
2787 | 0 | 0.12485
2788 | 0 | 0.12485
2789 | 0 | 0.12485
2790 | 11.7087 | 11.8335
2791 | 1.3191 | 1.4439
2792 | 1.7158 | 1.8406
2793 | 0 | 0.12485
2794 | 0 | 0.12485
2795 | 0 | 0.12485
2796 | 0.8346 | 0.95945
2797 | 0 | 0.12485
2798 | 0 | 0.12485
2799 | 0 | 0.12485
2800 | 0 | 0.12485
2801 | 0 | 0.12485
2802 | 5.9729 | 6.0978
2803 | 12.1726 | 12.2975
2804 | 0 | 0.12485
2805 | 1.2488 | 1.3736
2806 | 0 | 0.12485
2807 | 0 | 0.12485
2808 | 0 | 0.12485
2809 | 0 | 0.12485
2810 | 0 | 0.12485
2811 | 0 | 0.12485
2812 | 0 | 0.12485
2813 | 0 | 0.12485
2814 | 11.8896 | 12.0144
2815 | 1.2318 | 1.3567
2816 | 1.6024 | 1.7273
2817 | 0 | 0.12485
2818 | 0 | 0.12485
2819 | 0 | 0.12485
2820 | 0.82424 | 0.94909
2821 | 0 | 0.12485
2822 | 0 | 0.12485
2823 | 0 | 0.12485
2824 | 0 | 0.12485
2825 | 0 | 0.12485
2826 | 6.0604 | 6.1853
2827 | 11.9018 | 12.0266
2828 | 0 | 0.12485
2829 | 1.2902 | 1.4151
2830 | 0 | 0.12485
2831 | 0 | 0.12485
2832 | 0 | 0.12485
2833 | 0 | 0.12485
2834 | 0 | 0.12485
2835 | 0 | 0.12485
2836 | 0 | 0.12485
2837 | 0 | 0.12485
2838 | 12.025 | 12.1498
2839 | 1.2688 | 1.3937
2840 | 1.6504 | 1.7753
2841 | 0 | 0.12485
2842 | 0 | 0.12485
2843 | 0 | 0.12485
2844 | 0.80287 | 0.92772
2845 | 0 | 0.12485
2846 | 0 | 0.12485
2847 | 0 | 0.12485
2848 | 0 | 0.12485
2849 | 0 | 0.12485
2850 | 5.9653 | 6.0901
2851 | 11.7536 | 11.8784
2852 | 0 | 0.12485
2853 | 1.2161 | 1.3409
2854 | 0 | 0.12485
2855 | 0 | 0.12485
2856 | 0 | 0.12485
2857 | 0 | 0.12485
2858 | 0 | 0.12485
2859 | 0 | 0.12485
2860 | 0 | 0.12485
2861 | 0 | 0.12485
2862 | 11.6011 | 11.7259
2863 | 1.3099 | 1.4348
2864 | 1.7039 | 1.8287
2865 | 0 | 0.12485
2866 | 0 | 0.12485
2867 | 0 | 0.12485
2868 | 0.82875 | 0.9536
2869 | 0 | 0.12485
2870 | 0 | 0.12485
2871 | 0 | 0.12485
2872 | 0 | 0.12485
2873 | 0 | 0.12485
2874 | 5.9314 | 6.0563
2875 | 12.0994 | 12.2243
2876 | 0 | 0.12485
2877 | 1.2418 | 1.3667
2878 | 0 | 0.12485
2879 | 0 | 0.12485
2880 | 0 | 0.12485
2881 | 0 | 0.12485
2882 | 0 | 0.12485
2883 | 0 | 0.12485
2884 | 0 | 0.12485
2885 | 0 | 0.12485
2886 | 11.8261 | 11.9509
2887 | 1.226 | 1.3509
2888 | 1.5949 | 1.7197
2889 | 0 | 0.12485
2890 | 0 | 0.12485
2891 | 0 | 0.12485
2892 | 0.77591 | 0.90076
2893 | 0 | 0.12485
2894 | 0 | 0.12485
2895 | 0 | 0.12485
2896 | 0 | 0.12485
2897 | 0 | 0.12485
2898 | 6.0464 | 6.1713
2899 | 11.8608 | 11.9857
2900 | 0 | 0.12485
2901 | 1.285 | 1.4099
2902 | 0 | 0.12485
2903 | 0 | 0.12485
2904 | 0 | 0.12485
2905 | 0 | 0.12485
2906 | 0 | 0.12485
2907 | 0 | 0.12485
2908 | 0 | 0.12485
2909 | 0 | 0.12485
2910 | 11.5685 | 11.6934
2911 | 1.2712 | 1.396
2912 | 1.6535 | 1.7784
2913 | 0 | 0.12485
2914 | 0 | 0.12485
2915 | 0 | 0.12485
2916 | 0.80429 | 0.92914
2917 | 0 | 0.12485
2918 | 0 | 0.12485
2919 | 0 | 0.12485
2920 | 0 | 0.12485
2921 | 0 | 0.12485
2922 | 5.9742 | 6.099
2923 | 11.768 | 11.8929
2924 | 0 | 0.12485
2925 | 1.2174 | 1.3422
2926 | 0 | 0.12485
2927 | 0 | 0.12485
2928 | 0 | 0.12485
2929 | 0 | 0.12485
2930 | 0 | 0.12485
2931 | 0 | 0.12485
2932 | 0 | 0.12485
2933 | 0 | 0.12485
2934 | 11.6107 | 11.7355
2935 | 1.2066 | 1.3314
2936 | 1.5696 | 1.6945
2937 | 0 | 0.12485
2938 | 0 | 0.12485
2939 | 0 | 0.12485
2940 | 0.84487 | 0.96971
2941 | 0 | 0.12485
2942 | 0 | 0.12485
2943 | 0 | 0.12485
2944 | 0 | 0.12485
2945 | 0 | 0.12485
2946 | 5.9252 | 6.05
2947 | 11.6797 | 11.8046
2948 | 0 | 0.12485
2949 | 1.2724 | 1.3972
2950 | 0 | 0.12485
2951 | 0 | 0.12485
2952 | 0 | 0.12485
2953 | 0 | 0.12485
2954 | 0 | 0.12485
2955 | 0 | 0.12485
2956 | 0 | 0.12485
2957 | 0 | 0.12485
2958 | 11.8647 | 11.9895
2959 | 1.2543 | 1.3791
2960 | 1.6315 | 1.7564
2961 | 0 | 0.12485
2962 | 0 | 0.12485
2963 | 0 | 0.12485
2964 | 0.79359 | 0.91844
2965 | 0 | 0.12485
2966 | 0 | 0.12485
2967 | 0 | 0.12485
2968 | 0 | 0.12485
2969 | 0 | 0.12485
2970 | 5.8991 | 6.0239
2971 | 11.6376 | 11.7624
2972 | 0 | 0.12485
2973 | 1.2055 | 1.3303
2974 | 0 | 0.12485
2975 | 0 | 0.12485
2976 | 0 | 0.12485
2977 | 0 | 0.12485
2978 | 0 | 0.12485
2979 | 0 | 0.12485
2980 | 0 | 0.12485
2981 | 0 | 0.12485
2982 | 11.5042 | 11.6291
2983 | 1.1969 | 1.3217
2984 | 1.557 | 1.6819
2985 | 0 | 0.12485
2986 | 0 | 0.12485
2987 | 0 | 0.12485
2988 | 0.83954 | 0.96439
2989 | 0 | 0.12485
2990 | 0 | 0.12485
2991 | 0 | 0.12485
2992 | 0 | 0.12485
2993 | 0 | 0.12485
2994 | 6.0014 | 6.1263
2995 | 11.5794 | 11.7042
2996 | 0 | 0.12485
2997 | 1.2654 | 1.3902
2998 | 0 | 0.12485
2999 | 0 | 0.12485
3000 | 0 | 0.12485
3001 | 0 | 0.12485
3002 | 0 | 0.12485
3003 | 0 | 0.12485
3004 | 0 | 0.12485
3005 | 0 | 0.12485
3006 | 11.8023 | 11.9271
3007 | 1.2486 | 1.3735
3008 | 1.6241 | 1.749
3009 | 0 | 0.12485
3010 | 0 | 0.12485
3011 | 0 | 0.12485
3012 | 0.78998 | 0.91482
3013 | 0 | 0.12485
3014 | 0 | 0.12485
3015 | 0 | 0.12485
3016 | 0 | 0.12485
3017 | 0 | 0.12485
3018 | 5.8733 | 5.9981
3019 | 11.5924 | 11.7172
3020 | 0 | 0.12485
3021 | 1.2014 | 1.3262
3022 | 0 | 0.12485
3023 | 0 | 0.12485
3024 | 0 | 0.12485
3025 | 0 | 0.12485
3026 | 0 | 0.12485
3027 | 0 | 0.12485
3028 | 0 | 0.12485
3029 | 0 | 0.12485
3030 | 11.4665 | 11.5913
3031 | 1.1935 | 1.3183
3032 | 1.5525 | 1.6774
3033 | 0 | 0.12485
3034 | 0 | 0.12485
3035 | 0 | 0.12485
3036 | 0.83686 | 0.96171
3037 | 0 | 0.12485
3038 | 0 | 0.12485
3039 | 0 | 0.12485
3040 | 0 | 0.12485
3041 | 0 | 0.12485
3042 | 5.8684 | 5.9932
3043 | 11.5807 | 11.7056
3044 | 0 | 0.12485
3045 | 1.2627 | 1.3876
3046 | 0 | 0.12485
3047 | 0 | 0.12485
3048 | 0 | 0.12485
3049 | 0 | 0.12485
3050 | 0 | 0.12485
3051 | 0 | 0.12485
3052 | 0 | 0.12485
3053 | 0 | 0.12485
3054 | 11.777 | 11.9018
3055 | 1.2463 | 1.3711
3056 | 1.6211 | 1.7459
3057 | 0 | 0.12485
3058 | 0 | 0.12485
3059 | 0 | 0.12485
3060 | 0.78844 | 0.91329
3061 | 0 | 0.12485
3062 | 0 | 0.12485
3063 | 0 | 0.12485
3064 | 0 | 0.12485
3065 | 0 | 0.12485
3066 | 5.8622 | 5.987
3067 | 11.5728 | 11.6977
3068 | 0 | 0.12485
3069 | 1.1996 | 1.3244
3070 | 0 | 0.12485
3071 | 0 | 0.12485
3072 | 0 | 0.12485
3073 | 0 | 0.12485
3074 | 0 | 0.12485
3075 | 0 | 0.12485
3076 | 0 | 0.12485
3077 | 0 | 0.12485
3078 | 11.4494 | 11.5743
3079 | 1.1919 | 1.3168
3080 | 1.5505 | 1.6753
3081 | 0 | 0.12485
3082 | 0 | 0.12485
3083 | 0 | 0.12485
3084 | 0.83497 | 0.95981
3085 | 0 | 0.12485
3086 | 0 | 0.12485
3087 | 0 | 0.12485
3088 | 0 | 0.12485
3089 | 0 | 0.12485
3090 | 5.8547 | 5.9796
3091 | 11.5558 | 11.6806
3092 | 0 | 0.12485
3093 | 1.2594 | 1.3843
3094 | 0 | 0.12485
3095 | 0 | 0.12485
3096 | 0 | 0.12485
3097 | 0 | 0.12485
3098 | 0 | 0.12485
3099 | 0 | 0.12485
3100 | 0 | 0.12485
3101 | 0 | 0.12485
3102 | 11.7459 | 11.8707
3103 | 1.2433 | 1.3681
3104 | 1.6172 | 1.742
3105 | 0 | 0.12485
3106 | 0 | 0.12485
3107 | 0 | 0.12485
3108 | 0.78652 | 0.91137
3109 | 0 | 0.12485
3110 | 0 | 0.12485
3111 | 0 | 0.12485
3112 | 0 | 0.12485
3113 | 0 | 0.12485
3114 | 5.8482 | 5.973
3115 | 11.548 | 11.6729
3116 | 0 | 0.12485
3117 | 1.1973 | 1.3222
3118 | 0 | 0.12485
3119 | 0 | 0.12485
3120 | 0 | 0.12485
3121 | 0 | 0.12485
3122 | 0 | 0.12485
3123 | 0 | 0.12485
3124 | 0 | 0.12485
3125 | 0 | 0.12485
3126 | 11.4282 | 11.5531
3127 | 1.19 | 1.3148
3128 | 1.548 | 1.6728
3129 | 0 | 0.12485
3130 | 0 | 0.12485
3131 | 0 | 0.12485
3132 | 0.83404 | 0.95889
3133 | 0 | 0.12485
3134 | 0 | 0.12485
3135 | 0 | 0.12485
3136 | 0 | 0.12485
3137 | 0 | 0.12485
3138 | 5.8478 | 5.9727
3139 | 11.5403 | 11.6651
3140 | 0 | 0.12485
3141 | 1.2566 | 1.3815
3142 | 0 | 0.12485
3143 | 0 | 0.12485
3144 | 0 | 0.12485
3145 | 0 | 0.12485
3146 | 0 | 0.12485
3147 | 0 | 0.12485
3148 | 0 | 0.12485
3149 | 0 | 0.12485
3150 | 11.3121 | 11.4369
3151 | 1.2466 | 1.3714
3152 | 1.6214 | 1.7463
3153 | 0 | 0.12485
3154 | 0 | 0.12485
3155 | 0 | 0.12485
3156 | 0.78855 | 0.91339
3157 | 0 | 0.12485
3158 | 0 | 0.12485
3159 | 0 | 0.12485
3160 | 0 | 0.12485
3161 | 0 | 0.12485
3162 | 5.8613 | 5.9862
3163 | 11.5698 | 11.6946
3164 | 0 | 0.12485
3165 | 1.1993 | 1.3242
3166 | 0 | 0.12485
3167 | 0 | 0.12485
3168 | 0 | 0.12485
3169 | 0 | 0.12485
3170 | 0 | 0.12485
3171 | 0 | 0.12485
3172 | 0 | 0.12485
3173 | 0 | 0.12485
3174 | 11.4444 | 11.5692
3175 | 1.1915 | 1.3163
3176 | 1.5498 | 1.6747
3177 | 0 | 0.12485
3178 | 0 | 0.12485
3179 | 0 | 0.12485
3180 | 0.75383 | 0.87868
3181 | 0 | 0.12485
3182 | 0 | 0.12485
3183 | 0 | 0.12485
3184 | 0 | 0.12485
3185 | 0 | 0.12485
3186 | 5.8894 | 6.0143
3187 | 11.579 | 11.7039
3188 | 0 | 0.12485
3189 | 1.2571 | 1.3819
3190 | 0 | 0.12485
3191 | 0 | 0.12485
3192 | 0 | 0.12485
3193 | 0 | 0.12485
3194 | 0 | 0.12485
3195 | 0 | 0.12485
3196 | 0 | 0.12485
3197 | 0 | 0.12485
3198 | 11.314 | 11.4389
3199 | 1.2448 | 1.3696
3200 | 1.619 | 1.7439
3201 | 0 | 0.12485
3202 | 0 | 0.12485
3203 | 0 | 0.12485
3204 | 0.78734 | 0.91219
3205 | 0 | 0.12485
3206 | 0 | 0.12485
3207 | 0 | 0.12485
3208 | 0 | 0.12485
3209 | 0 | 0.12485
3210 | 5.8521 | 5.977
3211 | 11.552 | 11.6768
3212 | 0 | 0.12485
3213 | 1.1973 | 1.3221
3214 | 0 | 0.12485
3215 | 0 | 0.12485
3216 | 0 | 0.12485
3217 | 0 | 0.12485
3218 | 0 | 0.12485
3219 | 0 | 0.12485
3220 | 0 | 0.12485
3221 | 0 | 0.12485
3222 | 11.4246 | 11.5495
3223 | 1.1896 | 1.3145
3224 | 1.5474 | 1.6723
3225 | 0 | 0.12485
3226 | 0 | 0.12485
3227 | 0 | 0.12485
3228 | 0.75262 | 0.87747
3229 | 0 | 0.12485
3230 | 0 | 0.12485
3231 | 0 | 0.12485
3232 | 0 | 0.12485
3233 | 0 | 0.12485
3234 | 5.8748 | 5.9996
3235 | 11.5441 | 11.669
3236 | 0 | 0.12485
3237 | 1.2531 | 1.3779
3238 | 0 | 0.12485
3239 | 0 | 0.12485
3240 | 0 | 0.12485
3241 | 0 | 0.12485
3242 | 0 | 0.12485
3243 | 0 | 0.12485
3244 | 0 | 0.12485
3245 | 0 | 0.12485
3246 | 11.2776 | 11.4024
3247 | 1.2407 | 1.3655
3248 | 1.6137 | 1.7386
3249 | 0 | 0.12485
3250 | 0 | 0.12485
3251 | 0 | 0.12485
3252 | 0.78473 | 0.90958
3253 | 0 | 0.12485
3254 | 0 | 0.12485
3255 | 0 | 0.12485
3256 | 0 | 0.12485
3257 | 0 | 0.12485
3258 | 5.8332 | 5.958
3259 | 11.5171 | 11.642
3260 | 0 | 0.12485
3261 | 1.1935 | 1.3183
3262 | 0 | 0.12485
3263 | 0 | 0.12485
3264 | 0 | 0.12485
3265 | 0 | 0.12485
3266 | 0 | 0.12485
3267 | 0 | 0.12485
3268 | 0 | 0.12485
3269 | 0 | 0.12485
3270 | 11.3895 | 11.5143
3271 | 1.1864 | 1.3113
3272 | 1.5432 | 1.6681
3273 | 0 | 0.12485
3274 | 0 | 0.12485
3275 | 0 | 0.12485
3276 | 0.75054 | 0.87539
3277 | 0 | 0.12485
3278 | 0 | 0.12485
3279 | 0 | 0.12485
3280 | 0 | 0.12485
3281 | 0 | 0.12485
3282 | 5.856 | 5.9808
3283 | 11.5049 | 11.6297
3284 | 0 | 0.12485
3285 | 1.2488 | 1.3737
3286 | 0 | 0.12485
3287 | 0 | 0.12485
3288 | 0 | 0.12485
3289 | 0 | 0.12485
3290 | 0 | 0.12485
3291 | 0 | 0.12485
3292 | 0 | 0.12485
3293 | 0 | 0.12485
3294 | 11.239 | 11.3638
3295 | 1.2365 | 1.3613
3296 | 1.6082 | 1.7331
3297 | 0 | 0.12485
3298 | 0 | 0.12485
3299 | 0 | 0.12485
3300 | 0.78203 | 0.90688
3301 | 0 | 0.12485
3302 | 0 | 0.12485
3303 | 0 | 0.12485
3304 | 0 | 0.12485
3305 | 0 | 0.12485
3306 | 5.8137 | 5.9385
3307 | 11.4814 | 11.6063
3308 | 0 | 0.12485
3309 | 1.1896 | 1.3145
3310 | 0 | 0.12485
3311 | 0 | 0.12485
3312 | 0 | 0.12485
3313 | 0 | 0.12485
3314 | 0 | 0.12485
3315 | 0 | 0.12485
3316 | 0 | 0.12485
3317 | 0 | 0.12485
3318 | 11.3539 | 11.4788
3319 | 1.1831 | 1.308
3320 | 1.5389 | 1.6638
3321 | 0 | 0.12485
3322 | 0 | 0.12485
3323 | 0 | 0.12485
3324 | 0.74843 | 0.87328
3325 | 0 | 0.12485
3326 | 0 | 0.12485
3327 | 0 | 0.12485
3328 | 0 | 0.12485
3329 | 0 | 0.12485
3330 | 5.8371 | 5.9619
3331 | 11.4655 | 11.5903
3332 | 0 | 0.12485
3333 | 1.2446 | 1.3694
3334 | 0 | 0.12485
3335 | 0 | 0.12485
3336 | 0 | 0.12485
3337 | 0 | 0.12485
3338 | 0 | 0.12485
3339 | 0 | 0.12485
3340 | 0 | 0.12485
3341 | 0 | 0.12485
3342 | 11.2003 | 11.3252
3343 | 1.2323 | 1.3571
3344 | 1.6028 | 1.7276
3345 | 0 | 0.12485
3346 | 0 | 0.12485
3347 | 0 | 0.12485
3348 | 0.77934 | 0.90418
3349 | 0 | 0.12485
3350 | 0 | 0.12485
3351 | 0 | 0.12485
3352 | 0 | 0.12485
3353 | 0 | 0.12485
3354 | 5.7942 | 5.9191
3355 | 11.4457 | 11.5706
3356 | 0 | 0.12485
3357 | 1.1858 | 1.3106
3358 | 0 | 0.12485
3359 | 0 | 0.12485
3360 | 0 | 0.12485
3361 | 0 | 0.12485
3362 | 0 | 0.12485
3363 | 0 | 0.12485
3364 | 0 | 0.12485
3365 | 0 | 0.12485
3366 | 11.3184 | 11.4432
3367 | 1.1799 | 1.3047
3368 | 1.5347 | 1.6595
3369 | 0 | 0.12485
3370 | 0 | 0.12485
3371 | 0 | 0.12485
3372 | 0.74633 | 0.87117
3373 | 0 | 0.12485
3374 | 0 | 0.12485
3375 | 0 | 0.12485
3376 | 0 | 0.12485
3377 | 0 | 0.12485
3378 | 5.8181 | 5.943
3379 | 11.4261 | 11.5509
3380 | 0 | 0.12485
3381 | 1.2403 | 1.3652
3382 | 0 | 0.12485
3383 | 0 | 0.12485
3384 | 0 | 0.12485
3385 | 0 | 0.12485
3386 | 0 | 0.12485
3387 | 0 | 0.12485
3388 | 0 | 0.12485
3389 | 0 | 0.12485
3390 | 11.1617 | 11.2866
3391 | 1.2281 | 1.3529
3392 | 1.5973 | 1.7221
3393 | 0 | 0.12485
3394 | 0 | 0.12485
3395 | 0 | 0.12485
3396 | 0.77665 | 0.90149
3397 | 0 | 0.12485
3398 | 0 | 0.12485
3399 | 0 | 0.12485
3400 | 0 | 0.12485
3401 | 0 | 0.12485
3402 | 5.7747 | 5.8996
3403 | 11.4099 | 11.5348
3404 | 0 | 0.12485
3405 | 1.1819 | 1.3068
3406 | 0 | 0.12485
3407 | 0 | 0.12485
3408 | 0 | 0.12485
3409 | 0 | 0.12485
3410 | 0 | 0.12485
3411 | 0 | 0.12485
3412 | 0 | 0.12485
3413 | 0 | 0.12485
3414 | 11.282 | 11.4068
3415 | 1.1761 | 1.301
3416 | 1.5298 | 1.6546
3417 | 0 | 0.12485
3418 | 0 | 0.12485
3419 | 0 | 0.12485
3420 | 0.74391 | 0.86876
3421 | 0 | 0.12485
3422 | 0 | 0.12485
3423 | 0 | 0.12485
3424 | 0 | 0.12485
3425 | 0 | 0.12485
3426 | 5.7976 | 5.9224
3427 | 11.3849 | 11.5098
3428 | 0 | 0.12485
3429 | 1.236 | 1.3609
3430 | 0 | 0.12485
3431 | 0 | 0.12485
3432 | 0 | 0.12485
3433 | 0 | 0.12485
3434 | 0 | 0.12485
3435 | 0 | 0.12485
3436 | 0 | 0.12485
3437 | 0 | 0.12485
3438 | 11.1224 | 11.2472
3439 | 1.2239 | 1.3487
3440 | 1.5918 | 1.7166
3441 | 0 | 0.12485
3442 | 0 | 0.12485
3443 | 0 | 0.12485
3444 | 0.77393 | 0.89878
3445 | 0 | 0.12485
3446 | 0 | 0.12485
3447 | 0 | 0.12485
3448 | 0 | 0.12485
3449 | 0 | 0.12485
3450 | 5.7539 | 5.8787
3451 | 11.3697 | 11.4946
3452 | 0 | 0.12485
3453 | 1.1778 | 1.3026
3454 | 0 | 0.12485
3455 | 0 | 0.12485
3456 | 0 | 0.12485
3457 | 0 | 0.12485
3458 | 0 | 0.12485
3459 | 0 | 0.12485
3460 | 0 | 0.12485
3461 | 0 | 0.12485
3462 | 11.243 | 11.3678
3463 | 1.1721 | 1.2969
3464 | 1.5245 | 1.6493
3465 | 0 | 0.12485
3466 | 0 | 0.12485
3467 | 0 | 0.12485
3468 | 0.7413 | 0.86615
3469 | 0 | 0.12485
3470 | 0 | 0.12485
3471 | 0 | 0.12485
3472 | 0 | 0.12485
3473 | 0 | 0.12485
3474 | 5.778 | 5.9028
3475 | 11.345 | 11.4698
3476 | 0 | 0.12485
3477 | 1.2317 | 1.3566
3478 | 0 | 0.12485
3479 | 0 | 0.12485
3480 | 0 | 0.12485
3481 | 0 | 0.12485
3482 | 0 | 0.12485
3483 | 0 | 0.12485
3484 | 0 | 0.12485
3485 | 0 | 0.12485
3486 | 11.0837 | 11.2085
3487 | 1.2197 | 1.3445
3488 | 1.5863 | 1.7112
3489 | 0 | 0.12485
3490 | 0 | 0.12485
3491 | 0 | 0.12485
3492 | 0.77125 | 0.89609
3493 | 0 | 0.12485
3494 | 0 | 0.12485
3495 | 0 | 0.12485
3496 | 0 | 0.12485
3497 | 0 | 0.12485
3498 | 5.7332 | 5.858
3499 | 11.3299 | 11.4547
3500 | 0 | 0.12485
3501 | 1.1736 | 1.2985
3502 | 0 | 0.12485
3503 | 0 | 0.12485
3504 | 0 | 0.12485
3505 | 0 | 0.12485
3506 | 0 | 0.12485
3507 | 0 | 0.12485
3508 | 0 | 0.12485
3509 | 0 | 0.12485
3510 | 11.2042 | 11.3291
3511 | 1.168 | 1.2929
3512 | 1.5192 | 1.6441
3513 | 0 | 0.12485
3514 | 0 | 0.12485
3515 | 0 | 0.12485
3516 | 0.7387 | 0.86355
3517 | 0 | 0.12485
3518 | 0 | 0.12485
3519 | 0 | 0.12485
3520 | 0 | 0.12485
3521 | 0 | 0.12485
3522 | 5.7603 | 5.8851
3523 | 11.3072 | 11.432
3524 | 0 | 0.12485
3525 | 1.2276 | 1.3525
3526 | 0 | 0.12485
3527 | 0 | 0.12485
3528 | 0 | 0.12485
3529 | 0 | 0.12485
3530 | 0 | 0.12485
3531 | 0 | 0.12485
3532 | 0 | 0.12485
3533 | 0 | 0.12485
3534 | 11.0462 | 11.1711
3535 | 1.2156 | 1.3404
3536 | 1.581 | 1.7058
3537 | 0 | 0.12485
3538 | 0 | 0.12485
3539 | 0 | 0.12485
3540 | 0.76862 | 0.89346
3541 | 0 | 0.12485
3542 | 0 | 0.12485
3543 | 0 | 0.12485
3544 | 0 | 0.12485
3545 | 0 | 0.12485
3546 | 5.7128 | 5.8377
3547 | 11.2905 | 11.4153
3548 | 0 | 0.12485
3549 | 1.1696 | 1.2944
3550 | 0 | 0.12485
3551 | 0 | 0.12485
3552 | 0 | 0.12485
3553 | 0 | 0.12485
3554 | 0 | 0.12485
3555 | 0 | 0.12485
3556 | 0 | 0.12485
3557 | 0 | 0.12485
3558 | 11.1658 | 11.2907
3559 | 1.164 | 1.2889
3560 | 1.514 | 1.6388
3561 | 0 | 0.12485
3562 | 0 | 0.12485
3563 | 0 | 0.12485
3564 | 0.73613 | 0.86098
3565 | 0 | 0.12485
3566 | 0 | 0.12485
3567 | 0 | 0.12485
3568 | 0 | 0.12485
3569 | 0 | 0.12485
3570 | 5.7428 | 5.8676
3571 | 11.2697 | 11.3945
3572 | 0 | 0.12485
3573 | 1.2235 | 1.3484
3574 | 0 | 0.12485
3575 | 0 | 0.12485
3576 | 0 | 0.12485
3577 | 0 | 0.12485
3578 | 0 | 0.12485
3579 | 0 | 0.12485
3580 | 0 | 0.12485
3581 | 0 | 0.12485
3582 | 11.0091 | 11.1339
3583 | 1.2115 | 1.3364
3584 | 1.5757 | 1.7005
3585 | 0 | 0.12485
3586 | 0 | 0.12485
3587 | 0 | 0.12485
3588 | 0.76601 | 0.89085
3589 | 0 | 0.12485
3590 | 0 | 0.12485
3591 | 0 | 0.12485
3592 | 0 | 0.12485
3593 | 0 | 0.12485
3594 | 5.4867 | 5.6116
3595 | 11.3169 | 11.4417
3596 | 0 | 0.12485
3597 | 1.1685 | 1.2934
3598 | 0 | 0.12485
3599 | 0 | 0.12485
3600 | 0 | 0.12485
3601 | 0 | 0.12485
3602 | 0 | 0.12485
3603 | 0 | 0.12485
3604 | 0 | 0.12485
3605 | 0 | 0.12485
3606 | 11.1523 | 11.2771
3607 | 1.1616 | 1.2864
3608 | 1.5108 | 1.6356
3609 | 0 | 0.12485
3610 | 0 | 0.12485
3611 | 0 | 0.12485
3612 | 0.73454 | 0.85939
3613 | 0 | 0.12485
3614 | 0 | 0.12485
3615 | 0 | 0.12485
3616 | 0 | 0.12485
3617 | 0 | 0.12485
3618 | 5.7333 | 5.8582
3619 | 10.7874 | 10.9122
3620 | 0 | 0.12485
3621 | 1.1307 | 1.2555
3622 | 0 | 0.12485
3623 | 0 | 0.12485
3624 | 0 | 0.12485
3625 | 0 | 0.12485
3626 | 0 | 0.12485
3627 | 0 | 0.12485
3628 | 0 | 0.12485
3629 | 0 | 0.12485
3630 | 10.827 | 10.9518
3631 | 1.1352 | 1.2601
3632 | 1.4766 | 1.6014
3633 | 0 | 0.12485
3634 | 0 | 0.12485
3635 | 0 | 0.12485
3636 | 0.79943 | 0.92427
3637 | 0 | 0.12485
3638 | 0 | 0.12485
3639 | 0 | 0.12485
3640 | 0 | 0.12485
3641 | 0 | 0.12485
3642 | 5.6016 | 5.7265
3643 | 11.0902 | 11.2151
3644 | 0 | 0.12485
3645 | 1.2102 | 1.3351
3646 | 0 | 0.12485
3647 | 0 | 0.12485
3648 | 0 | 0.12485
3649 | 0 | 0.12485
3650 | 0 | 0.12485
3651 | 0 | 0.12485
3652 | 0 | 0.12485
3653 | 0 | 0.12485
3654 | 10.8911 | 11.016
3655 | 1.2018 | 1.3266
3656 | 1.563 | 1.6879
3657 | 0 | 0.12485
3658 | 0 | 0.12485
3659 | 0 | 0.12485
3660 | 0.75981 | 0.88466
3661 | 0 | 0.12485
3662 | 0 | 0.12485
3663 | 0 | 0.12485
3664 | 0 | 0.12485
3665 | 0 | 0.12485
3666 | 5.6495 | 5.7744
3667 | 11.177 | 11.3018
3668 | 0 | 0.12485
3669 | 1.1585 | 1.2833
3670 | 0 | 0.12485
3671 | 0 | 0.12485
3672 | 0 | 0.12485
3673 | 0 | 0.12485
3674 | 0 | 0.12485
3675 | 0 | 0.12485
3676 | 0 | 0.12485
3677 | 0 | 0.12485
3678 | 11.063 | 11.1879
3679 | 1.1536 | 1.2785
3680 | 1.5004 | 1.6253
3681 | 0 | 0.12485
3682 | 0 | 0.12485
3683 | 0 | 0.12485
3684 | 0.72946 | 0.85431
3685 | 0 | 0.12485
3686 | 0 | 0.12485
3687 | 0 | 0.12485
3688 | 0 | 0.12485
3689 | 0 | 0.12485
3690 | 5.6975 | 5.8223
3691 | 10.7246 | 10.8494
3692 | 0 | 0.12485
3693 | 1.1249 | 1.2498
3694 | 0 | 0.12485
3695 | 0 | 0.12485
3696 | 0 | 0.12485
3697 | 0 | 0.12485
3698 | 0 | 0.12485
3699 | 0 | 0.12485
3700 | 0 | 0.12485
3701 | 0 | 0.12485
3702 | 10.7748 | 10.8996
3703 | 1.1305 | 1.2553
3704 | 1.4704 | 1.5952
3705 | 0 | 0.12485
3706 | 0 | 0.12485
3707 | 0 | 0.12485
3708 | 0.71486 | 0.83971
3709 | 0 | 0.12485
3710 | 0 | 0.12485
3711 | 0 | 0.12485
3712 | 0 | 0.12485
3713 | 0 | 0.12485
3714 | 5.609 | 5.7338
3715 | 11.0708 | 11.1956
3716 | 0 | 0.12485
3717 | 1.2063 | 1.3311
3718 | 0 | 0.12485
3719 | 0 | 0.12485
3720 | 0 | 0.12485
3721 | 0 | 0.12485
3722 | 0 | 0.12485
3723 | 0 | 0.12485
3724 | 0 | 0.12485
3725 | 0 | 0.12485
3726 | 10.8549 | 10.9797
3727 | 1.1969 | 1.3218
3728 | 1.5566 | 1.6815
3729 | 0 | 0.12485
3730 | 0 | 0.12485
3731 | 0 | 0.12485
3732 | 0.75667 | 0.88151
3733 | 0 | 0.12485
3734 | 0 | 0.12485
3735 | 0 | 0.12485
3736 | 0 | 0.12485
3737 | 0 | 0.12485
3738 | 5.4201 | 5.5449
3739 | 11.0007 | 11.1255
3740 | 0 | 0.12485
3741 | 1.1715 | 1.2964
3742 | 0 | 0.12485
3743 | 0 | 0.12485
3744 | 0 | 0.12485
3745 | 0 | 0.12485
3746 | 0 | 0.12485
3747 | 0 | 0.12485
3748 | 0 | 0.12485
3749 | 0 | 0.12485
3750 | 10.9585 | 11.0834
3751 | 1.1716 | 1.2964
3752 | 1.5237 | 1.6485
3753 | 0 | 0.12485
3754 | 0 | 0.12485
3755 | 0 | 0.12485
3756 | 0.74066 | 0.86551
3757 | 0 | 0.12485
3758 | 0 | 0.12485
3759 | 0 | 0.12485
3760 | 0 | 0.12485
3761 | 0 | 0.12485
3762 | 5.5206 | 5.6454
3763 | 10.9686 | 11.0935
3764 | 0 | 0.12485
3765 | 1.1422 | 1.2671
3766 | 0 | 0.12485
3767 | 0 | 0.12485
3768 | 0 | 0.12485
3769 | 0 | 0.12485
3770 | 0 | 0.12485
3771 | 0 | 0.12485
3772 | 0 | 0.12485
3773 | 0 | 0.12485
3774 | 10.9207 | 11.0455
3775 | 1.1417 | 1.2665
3776 | 1.4848 | 1.6097
3777 | 0 | 0.12485
3778 | 0 | 0.12485
3779 | 0 | 0.12485
3780 | 0.72182 | 0.84667
3781 | 0 | 0.12485
3782 | 0 | 0.12485
3783 | 0 | 0.12485
3784 | 0 | 0.12485
3785 | 0 | 0.12485
3786 | 5.6423 | 5.7672
3787 | 10.6288 | 10.7537
3788 | 0 | 0.12485
3789 | 1.1162 | 1.2411
3790 | 0 | 0.12485
3791 | 0 | 0.12485
3792 | 0 | 0.12485
3793 | 0 | 0.12485
3794 | 0 | 0.12485
3795 | 0 | 0.12485
3796 | 0 | 0.12485
3797 | 0 | 0.12485
3798 | 10.6963 | 10.8211
3799 | 1.1233 | 1.2482
3800 | 1.461 | 1.5859
3801 | 0 | 0.12485
3802 | 0 | 0.12485
3803 | 0 | 0.12485
3804 | 0.71026 | 0.83511
3805 | 0 | 0.12485
3806 | 0 | 0.12485
3807 | 0 | 0.12485
3808 | 0 | 0.12485
3809 | 0 | 0.12485
3810 | 5.5705 | 5.6954
3811 | 10.9938 | 11.1186
3812 | 0 | 0.12485
3813 | 1.1982 | 1.323
3814 | 0 | 0.12485
3815 | 0 | 0.12485
3816 | 0 | 0.12485
3817 | 0 | 0.12485
3818 | 0 | 0.12485
3819 | 0 | 0.12485
3820 | 0 | 0.12485
3821 | 0 | 0.12485
3822 | 10.7815 | 10.9063
3823 | 1.189 | 1.3138
3824 | 1.5463 | 1.6712
3825 | 0 | 0.12485
3826 | 0 | 0.12485
3827 | 0 | 0.12485
3828 | 0.7516 | 0.87644
3829 | 0 | 0.12485
3830 | 0 | 0.12485
3831 | 0 | 0.12485
3832 | 0 | 0.12485
3833 | 0 | 0.12485
3834 | 5.3837 | 5.5086
3835 | 10.936 | 11.0609
3836 | 0 | 0.12485
3837 | 1.1642 | 1.2891
3838 | 0 | 0.12485
3839 | 0 | 0.12485
3840 | 0 | 0.12485
3841 | 0 | 0.12485
3842 | 0 | 0.12485
3843 | 0 | 0.12485
3844 | 0 | 0.12485
3845 | 0 | 0.12485
3846 | 10.8918 | 11.0167
3847 | 1.1641 | 1.289
3848 | 1.514 | 1.6388
3849 | 0 | 0.12485
3850 | 0 | 0.12485
3851 | 0 | 0.12485
3852 | 0.73588 | 0.86073
3853 | 0 | 0.12485
3854 | 0 | 0.12485
3855 | 0 | 0.12485
3856 | 0 | 0.12485
3857 | 0 | 0.12485
3858 | 5.486 | 5.6109
3859 | 10.9049 | 11.0298
3860 | 0 | 0.12485
3861 | 1.1353 | 1.2601
3862 | 0 | 0.12485
3863 | 0 | 0.12485
3864 | 0 | 0.12485
3865 | 0 | 0.12485
3866 | 0 | 0.12485
3867 | 0 | 0.12485
3868 | 0 | 0.12485
3869 | 0 | 0.12485
3870 | 10.8546 | 10.9794
3871 | 1.1345 | 1.2594
3872 | 1.4755 | 1.6004
3873 | 0 | 0.12485
3874 | 0 | 0.12485
3875 | 0 | 0.12485
3876 | 0.71723 | 0.84207
3877 | 0 | 0.12485
3878 | 0 | 0.12485
3879 | 0 | 0.12485
3880 | 0 | 0.12485
3881 | 0 | 0.12485
3882 | 5.612 | 5.7368
3883 | 10.5739 | 10.6988
3884 | 0 | 0.12485
3885 | 1.1111 | 1.2359
3886 | 0 | 0.12485
3887 | 0 | 0.12485
3888 | 0 | 0.12485
3889 | 0 | 0.12485
3890 | 0 | 0.12485
3891 | 0 | 0.12485
3892 | 0 | 0.12485
3893 | 0 | 0.12485
3894 | 10.6491 | 10.7739
3895 | 1.119 | 1.2439
3896 | 1.4554 | 1.5803
3897 | 0 | 0.12485
3898 | 0 | 0.12485
3899 | 0 | 0.12485
3900 | 0.70747 | 0.83231
3901 | 0 | 0.12485
3902 | 0 | 0.12485
3903 | 0 | 0.12485
3904 | 0 | 0.12485
3905 | 0 | 0.12485
3906 | 5.5411 | 5.6659
3907 | 10.9274 | 11.0523
3908 | 0 | 0.12485
3909 | 1.1907 | 1.3156
3910 | 0 | 0.12485
3911 | 0 | 0.12485
3912 | 0 | 0.12485
3913 | 0 | 0.12485
3914 | 0 | 0.12485
3915 | 0 | 0.12485
3916 | 0 | 0.12485
3917 | 0 | 0.12485
3918 | 10.7146 | 10.8395
3919 | 1.1816 | 1.3064
3920 | 1.5367 | 1.6615
3921 | 0 | 0.12485
3922 | 0 | 0.12485
3923 | 0 | 0.12485
3924 | 0.74684 | 0.87169
3925 | 0 | 0.12485
3926 | 0 | 0.12485
3927 | 0 | 0.12485
3928 | 0 | 0.12485
3929 | 0 | 0.12485
3930 | 5.3495 | 5.4744
3931 | 10.4759 | 10.6008
3932 | 0 | 0.12485
3933 | 1.1637 | 1.2886
3934 | 0 | 0.12485
3935 | 0 | 0.12485
3936 | 0 | 0.12485
3937 | 0 | 0.12485
3938 | 0 | 0.12485
3939 | 0 | 0.12485
3940 | 0 | 0.12485
3941 | 0 | 0.12485
3942 | 10.4785 | 10.6033
3943 | 1.1669 | 1.2918
3944 | 1.5176 | 1.6424
3945 | 0 | 0.12485
3946 | 0 | 0.12485
3947 | 0 | 0.12485
3948 | 0.73757 | 0.86241
3949 | 0 | 0.12485
3950 | 0 | 0.12485
3951 | 0 | 0.12485
3952 | 0 | 0.12485
3953 | 0 | 0.12485
3954 | 5.4928 | 5.6177
3955 | 10.9029 | 11.0277
3956 | 0 | 0.12485
3957 | 1.1323 | 1.2571
3958 | 0 | 0.12485
3959 | 0 | 0.12485
3960 | 0 | 0.12485
3961 | 0 | 0.12485
3962 | 0 | 0.12485
3963 | 0 | 0.12485
3964 | 0 | 0.12485
3965 | 0 | 0.12485
3966 | 10.8216 | 10.9464
3967 | 1.1295 | 1.2544
3968 | 1.469 | 1.5939
3969 | 0 | 0.12485
3970 | 0 | 0.12485
3971 | 0 | 0.12485
3972 | 0.714 | 0.83885
3973 | 0 | 0.12485
3974 | 0 | 0.12485
3975 | 0 | 0.12485
3976 | 0 | 0.12485
3977 | 0 | 0.12485
3978 | 5.3377 | 5.4626
3979 | 10.6637 | 10.7885
3980 | 0 | 0.12485
3981 | 1.1164 | 1.2412
3982 | 0 | 0.12485
3983 | 0 | 0.12485
3984 | 0 | 0.12485
3985 | 0 | 0.12485
3986 | 0 | 0.12485
3987 | 0 | 0.12485
3988 | 0 | 0.12485
3989 | 0 | 0.12485
3990 | 10.6894 | 10.8142
3991 | 1.1206 | 1.2454
3992 | 1.4574 | 1.5822
3993 | 0 | 0.12485
3994 | 0 | 0.12485
3995 | 0 | 0.12485
3996 | 0.70833 | 0.83318
3997 | 0 | 0.12485
3998 | 0 | 0.12485
3999 | 0 | 0.12485
4000 | 0 | 0.12485
4001 | 0 | 0.12485
4002 | 5.5481 | 5.6729
4003 | 10.463 | 10.5878
4004 | 0 | 0.12485
4005 | 1.101 | 1.2258
4006 | 0 | 0.12485
4007 | 0 | 0.12485
4008 | 0 | 0.12485
4009 | 0 | 0.12485
4010 | 0 | 0.12485
4011 | 0 | 0.12485
4012 | 0 | 0.12485
4013 | 0 | 0.12485
4014 | 10.5584 | 10.6832
4015 | 1.1108 | 1.2356
4016 | 1.4446 | 1.5695
4017 | 0 | 0.12485
4018 | 0 | 0.12485
4019 | 0 | 0.12485
4020 | 0.70215 | 0.827
4021 | 0 | 0.12485
4022 | 0 | 0.12485
4023 | 0 | 0.12485
4024 | 0 | 0.12485
4025 | 0 | 0.12485
4026 | 5.5001 | 5.6249
4027 | 10.3829 | 10.5077
4028 | 0 | 0.12485
4029 | 1.094 | 1.2189
4030 | 0 | 0.12485
4031 | 0 | 0.12485
4032 | 0 | 0.12485
4033 | 0 | 0.12485
4034 | 0 | 0.12485
4035 | 0 | 0.12485
4036 | 0 | 0.12485
4037 | 0 | 0.12485
4038 | 10.4963 | 10.6211
4039 | 1.1051 | 1.23
4040 | 1.4373 | 1.5621
4041 | 0 | 0.12485
4042 | 0 | 0.12485
4043 | 0 | 0.12485
4044 | 0.69856 | 0.82341
4045 | 0 | 0.12485
4046 | 0 | 0.12485
4047 | 0 | 0.12485
4048 | 0 | 0.12485
4049 | 0 | 0.12485
4050 | 5.4758 | 5.6007
4051 | 10.8076 | 10.9324
4052 | 0 | 0.12485
4053 | 1.1787 | 1.3035
4054 | 0 | 0.12485
4055 | 0 | 0.12485
4056 | 0 | 0.12485
4057 | 0 | 0.12485
4058 | 0 | 0.12485
4059 | 0 | 0.12485
4060 | 0 | 0.12485
4061 | 0 | 0.12485
4062 | 10.6064 | 10.7312
4063 | 1.1702 | 1.2951
4064 | 1.5219 | 1.6467
4065 | 0 | 0.12485
4066 | 0 | 0.12485
4067 | 0 | 0.12485
4068 | 0.73956 | 0.86441
4069 | 0 | 0.12485
4070 | 0 | 0.12485
4071 | 0 | 0.12485
4072 | 0 | 0.12485
4073 | 0 | 0.12485
4074 | 5.2974 | 5.4223
4075 | 10.3835 | 10.5084
4076 | 0 | 0.12485
4077 | 1.1534 | 1.2782
4078 | 0 | 0.12485
4079 | 0 | 0.12485
4080 | 0 | 0.12485
4081 | 0 | 0.12485
4082 | 0 | 0.12485
4083 | 0 | 0.12485
4084 | 0 | 0.12485
4085 | 0 | 0.12485
4086 | 10.3855 | 10.5103
4087 | 1.1565 | 1.2814
4088 | 1.504 | 1.6289
4089 | 0 | 0.12485
4090 | 0 | 0.12485
4091 | 0 | 0.12485
4092 | 0.73089 | 0.85574
4093 | 0 | 0.12485
4094 | 0 | 0.12485
4095 | 0 | 0.12485
4096 | 0 | 0.12485
4097 | 0 | 0.12485
4098 | 5.237 | 5.3618
4099 | 10.6797 | 10.8045
4100 | 0 | 0.12485
4101 | 1.1399 | 1.2648
4102 | 0 | 0.12485
4103 | 0 | 0.12485
4104 | 0 | 0.12485
4105 | 0 | 0.12485
4106 | 0 | 0.12485
4107 | 0 | 0.12485
4108 | 0 | 0.12485
4109 | 0 | 0.12485
4110 | 10.6739 | 10.7987
4111 | 1.1422 | 1.2671
4112 | 1.4854 | 1.6103
4113 | 0 | 0.12485
4114 | 0 | 0.12485
4115 | 0 | 0.12485
4116 | 0.72186 | 0.84671
4117 | 0 | 0.12485
4118 | 0 | 0.12485
4119 | 0 | 0.12485
4120 | 0 | 0.12485
4121 | 0 | 0.12485
4122 | 5.3852 | 5.51
4123 | 10.7219 | 10.8468
4124 | 0 | 0.12485
4125 | 1.1161 | 1.2409
4126 | 0 | 0.12485
4127 | 0 | 0.12485
4128 | 0 | 0.12485
4129 | 0 | 0.12485
4130 | 0 | 0.12485
4131 | 0 | 0.12485
4132 | 0 | 0.12485
4133 | 0 | 0.12485
4134 | 10.675 | 10.7999
4135 | 1.1156 | 1.2404
4136 | 1.4508 | 1.5757
4137 | 0 | 0.12485
4138 | 0 | 0.12485
4139 | 0 | 0.12485
4140 | 0.70505 | 0.8299
4141 | 0 | 0.12485
4142 | 0 | 0.12485
4143 | 0 | 0.12485
4144 | 0 | 0.12485
4145 | 0 | 0.12485
4146 | 5.2734 | 5.3983
4147 | 10.5473 | 10.6722
4148 | 0 | 0.12485
4149 | 1.1043 | 1.2292
4150 | 0 | 0.12485
4151 | 0 | 0.12485
4152 | 0 | 0.12485
4153 | 0 | 0.12485
4154 | 0 | 0.12485
4155 | 0 | 0.12485
4156 | 0 | 0.12485
4157 | 0 | 0.12485
4158 | 10.577 | 10.7019
4159 | 1.1088 | 1.2336
4160 | 1.442 | 1.5668
4161 | 0 | 0.12485
4162 | 0 | 0.12485
4163 | 0 | 0.12485
4164 | 0.70076 | 0.82561
4165 | 0 | 0.12485
4166 | 0 | 0.12485
4167 | 0 | 0.12485
4168 | 0 | 0.12485
4169 | 0 | 0.12485
4170 | 5.4968 | 5.6216
4171 | 10.3707 | 10.4956
4172 | 0 | 0.12485
4173 | 1.0923 | 1.2172
4174 | 0 | 0.12485
4175 | 0 | 0.12485
4176 | 0 | 0.12485
4177 | 0 | 0.12485
4178 | 0 | 0.12485
4179 | 0 | 0.12485
4180 | 0 | 0.12485
4181 | 0 | 0.12485
4182 | 10.4768 | 10.6016
4183 | 1.1018 | 1.2267
4184 | 1.4329 | 1.5578
4185 | 0 | 0.12485
4186 | 0 | 0.12485
4187 | 0 | 0.12485
4188 | 0.69636 | 0.82121
4189 | 0 | 0.12485
4190 | 0 | 0.12485
4191 | 0 | 0.12485
4192 | 0 | 0.12485
4193 | 0 | 0.12485
4194 | 5.4634 | 5.5883
4195 | 10.3149 | 10.4398
4196 | 0 | 0.12485
4197 | 1.0874 | 1.2123
4198 | 0 | 0.12485
4199 | 0 | 0.12485
4200 | 0 | 0.12485
4201 | 0 | 0.12485
4202 | 0 | 0.12485
4203 | 0 | 0.12485
4204 | 0 | 0.12485
4205 | 0 | 0.12485
4206 | 10.4345 | 10.5594
4207 | 1.0985 | 1.2234
4208 | 1.4286 | 1.5535
4209 | 0 | 0.12485
4210 | 0 | 0.12485
4211 | 0 | 0.12485
4212 | 0.69426 | 0.8191
4213 | 0 | 0.12485
4214 | 0 | 0.12485
4215 | 0 | 0.12485
4216 | 0 | 0.12485
4217 | 0 | 0.12485
4218 | 5.4476 | 5.5724
4219 | 10.2878 | 10.4126
4220 | 0 | 0.12485
4221 | 1.085 | 1.2099
4222 | 0 | 0.12485
4223 | 0 | 0.12485
4224 | 0 | 0.12485
4225 | 0 | 0.12485
4226 | 0 | 0.12485
4227 | 0 | 0.12485
4228 | 0 | 0.12485
4229 | 0 | 0.12485
4230 | 10.4129 | 10.5377
4231 | 1.0965 | 1.2214
4232 | 1.426 | 1.5509
4233 | 0 | 0.12485
4234 | 0 | 0.12485
4235 | 0 | 0.12485
4236 | 0.69298 | 0.81783
4237 | 0 | 0.12485
4238 | 0 | 0.12485
4239 | 0 | 0.12485
4240 | 0 | 0.12485
4241 | 0 | 0.12485
4242 | 5.4391 | 5.5639
4243 | 10.2727 | 10.3976
4244 | 0 | 0.12485
4245 | 1.0836 | 1.2085
4246 | 0 | 0.12485
4247 | 0 | 0.12485
4248 | 0 | 0.12485
4249 | 0 | 0.12485
4250 | 0 | 0.12485
4251 | 0 | 0.12485
4252 | 0 | 0.12485
4253 | 0 | 0.12485
4254 | 10.3998 | 10.5247
4255 | 1.0951 | 1.22
4256 | 1.4242 | 1.549
4257 | 0 | 0.12485
4258 | 0 | 0.12485
4259 | 0 | 0.12485
4260 | 0.69207 | 0.81692
4261 | 0 | 0.12485
4262 | 0 | 0.12485
4263 | 0 | 0.12485
4264 | 0 | 0.12485
4265 | 0 | 0.12485
4266 | 5.4331 | 5.5579
4267 | 10.2619 | 10.3867
4268 | 0 | 0.12485
4269 | 1.0826 | 1.2075
4270 | 0 | 0.12485
4271 | 0 | 0.12485
4272 | 0 | 0.12485
4273 | 0 | 0.12485
4274 | 0 | 0.12485
4275 | 0 | 0.12485
4276 | 0 | 0.12485
4277 | 0 | 0.12485
4278 | 10.3899 | 10.5147
4279 | 1.0939 | 1.2187
4280 | 1.4226 | 1.5474
4281 | 0 | 0.12485
4282 | 0 | 0.12485
4283 | 0 | 0.12485
4284 | 0.69128 | 0.81613
4285 | 0 | 0.12485
4286 | 0 | 0.12485
4287 | 0 | 0.12485
4288 | 0 | 0.12485
4289 | 0 | 0.12485
4290 | 5.4277 | 5.5526
4291 | 10.2521 | 10.3769
4292 | 0 | 0.12485
4293 | 1.0817 | 1.2065
4294 | 0 | 0.12485
4295 | 0 | 0.12485
4296 | 0 | 0.12485
4297 | 0 | 0.12485
4298 | 0 | 0.12485
4299 | 0 | 0.12485
4300 | 0 | 0.12485
4301 | 0 | 0.12485
4302 | 10.3808 | 10.5056
4303 | 1.0927 | 1.2176
4304 | 1.4211 | 1.5459
4305 | 0 | 0.12485
4306 | 0 | 0.12485
4307 | 0 | 0.12485
4308 | 0.69053 | 0.81538
4309 | 0 | 0.12485
4310 | 0 | 0.12485
4311 | 0 | 0.12485
4312 | 0 | 0.12485
4313 | 0 | 0.12485
4314 | 5.4226 | 5.5474
4315 | 10.2426 | 10.3675
4316 | 0 | 0.12485
4317 | 1.0808 | 1.2056
4318 | 0 | 0.12485
4319 | 0 | 0.12485
4320 | 0 | 0.12485
4321 | 0 | 0.12485
4322 | 0 | 0.12485
4323 | 0 | 0.12485
4324 | 0 | 0.12485
4325 | 0 | 0.12485
4326 | 10.3719 | 10.4968
4327 | 1.0916 | 1.2165
4328 | 1.4196 | 1.5444
4329 | 0 | 0.12485
4330 | 0 | 0.12485
4331 | 0 | 0.12485
4332 | 0.6898 | 0.81465
4333 | 0 | 0.12485
4334 | 0 | 0.12485
4335 | 0 | 0.12485
4336 | 0 | 0.12485
4337 | 0 | 0.12485
4338 | 5.4176 | 5.5424
4339 | 10.2335 | 10.3583
4340 | 0 | 0.12485
4341 | 1.0799 | 1.2047
4342 | 0 | 0.12485
4343 | 0 | 0.12485
4344 | 0 | 0.12485
4345 | 0 | 0.12485
4346 | 0 | 0.12485
4347 | 0 | 0.12485
4348 | 0 | 0.12485
4349 | 0 | 0.12485
4350 | 10.3633 | 10.4882
4351 | 1.0905 | 1.2153
4352 | 1.4181 | 1.543
4353 | 0 | 0.12485
4354 | 0 | 0.12485
4355 | 0 | 0.12485
4356 | 0.68908 | 0.81393
4357 | 0 | 0.12485
4358 | 0 | 0.12485
4359 | 0 | 0.12485
4360 | 0 | 0.12485
4361 | 0 | 0.12485
4362 | 5.4136 | 5.5385
4363 | 10.226 | 10.3508
4364 | 0 | 0.12485
4365 | 1.0792 | 1.204
4366 | 0 | 0.12485
4367 | 0 | 0.12485
4368 | 0 | 0.12485
4369 | 0 | 0.12485
4370 | 0 | 0.12485
4371 | 0 | 0.12485
4372 | 0 | 0.12485
4373 | 0 | 0.12485
4374 | 10.3559 | 10.4807
4375 | 1.0895 | 1.2143
4376 | 1.4168 | 1.5417
4377 | 0 | 0.12485
4378 | 0 | 0.12485
4379 | 0 | 0.12485
4380 | 0.68842 | 0.81327
4381 | 0 | 0.12485
4382 | 0 | 0.12485
4383 | 0 | 0.12485
4384 | 0 | 0.12485
4385 | 0 | 0.12485
4386 | 5.409 | 5.5339
4387 | 10.2175 | 10.3424
4388 | 0 | 0.12485
4389 | 1.0783 | 1.2032
4390 | 0 | 0.12485
4391 | 0 | 0.12485
4392 | 0 | 0.12485
4393 | 0 | 0.12485
4394 | 0 | 0.12485
4395 | 0 | 0.12485
4396 | 0 | 0.12485
4397 | 0 | 0.12485
4398 | 10.3479 | 10.4727
4399 | 1.0884 | 1.2133
4400 | 1.4154 | 1.5403
4401 | 0 | 0.12485
4402 | 0 | 0.12485
4403 | 0 | 0.12485
4404 | 0.68774 | 0.81259
4405 | 0 | 0.12485
4406 | 0 | 0.12485
4407 | 0 | 0.12485
4408 | 0 | 0.12485
4409 | 0 | 0.12485
4410 | 5.1506 | 5.2754
4411 | 10.3314 | 10.4563
4412 | 0 | 0.12485
4413 | 1.0841 | 1.2089
4414 | 0 | 0.12485
4415 | 0 | 0.12485
4416 | 0 | 0.12485
4417 | 0 | 0.12485
4418 | 0 | 0.12485
4419 | 0 | 0.12485
4420 | 0 | 0.12485
4421 | 0 | 0.12485
4422 | 10.3933 | 10.5181
4423 | 1.0907 | 1.2156
4424 | 1.4184 | 1.5433
4425 | 0 | 0.12485
4426 | 0 | 0.12485
4427 | 0 | 0.12485
4428 | 0.68917 | 0.81402
4429 | 0 | 0.12485
4430 | 0 | 0.12485
4431 | 0 | 0.12485
4432 | 0 | 0.12485
4433 | 0 | 0.12485
4434 | 5.1601 | 5.2849
4435 | 10.3454 | 10.4702
4436 | 0 | 0.12485
4437 | 1.0844 | 1.2093
4438 | 0 | 0.12485
4439 | 0 | 0.12485
4440 | 0 | 0.12485
4441 | 0 | 0.12485
4442 | 0 | 0.12485
4443 | 0 | 0.12485
4444 | 0 | 0.12485
4445 | 0 | 0.12485
4446 | 10.3948 | 10.5197
4447 | 1.0903 | 1.2151
4448 | 1.4178 | 1.5427
4449 | 0 | 0.12485
4450 | 0 | 0.12485
4451 | 0 | 0.12485
4452 | 0.68887 | 0.81372
4453 | 0 | 0.12485
4454 | 0 | 0.12485
4455 | 0 | 0.12485
4456 | 0 | 0.12485
4457 | 0 | 0.12485
4458 | 5.1577 | 5.2826
4459 | 10.3401 | 10.465
4460 | 0 | 0.12485
4461 | 1.0836 | 1.2084
4462 | 0 | 0.12485
4463 | 0 | 0.12485
4464 | 0 | 0.12485
4465 | 0 | 0.12485
4466 | 0 | 0.12485
4467 | 0 | 0.12485
4468 | 0 | 0.12485
4469 | 0 | 0.12485
4470 | 10.3864 | 10.5113
4471 | 1.0892 | 1.2141
4472 | 1.4165 | 1.5413
4473 | 0 | 0.12485
4474 | 0 | 0.12485
4475 | 0 | 0.12485
4476 | 0.68819 | 0.81304
4477 | 0 | 0.12485
4478 | 0 | 0.12485
4479 | 0 | 0.12485
4480 | 0 | 0.12485
4481 | 0 | 0.12485
4482 | 5.1527 | 5.2776
4483 | 10.3307 | 10.4556
4484 | 0 | 0.12485
4485 | 1.0825 | 1.2073
4486 | 0 | 0.12485
4487 | 0 | 0.12485
4488 | 0 | 0.12485
4489 | 0 | 0.12485
4490 | 0 | 0.12485
4491 | 0 | 0.12485
4492 | 0 | 0.12485
4493 | 0 | 0.12485
4494 | 10.376 | 10.5009
4495 | 1.0881 | 1.2129
4496 | 1.4149 | 1.5398
4497 | 0 | 0.12485
4498 | 0 | 0.12485
4499 | 0 | 0.12485
4500 | 0.68744 | 0.81229
4501 | 0 | 0.12485
4502 | 0 | 0.12485
4503 | 0 | 0.12485
4504 | 0 | 0.12485
4505 | 0 | 0.12485
4506 | 5.1473 | 5.2721
4507 | 10.3205 | 10.4454
4508 | 0 | 0.12485
4509 | 1.0813 | 1.2062
4510 | 0 | 0.12485
4511 | 0 | 0.12485
4512 | 0 | 0.12485
4513 | 0 | 0.12485
4514 | 0 | 0.12485
4515 | 0 | 0.12485
4516 | 0 | 0.12485
4517 | 0 | 0.12485
4518 | 10.3653 | 10.4901
4519 | 1.0869 | 1.2117
4520 | 1.4134 | 1.5382
4521 | 0 | 0.12485
4522 | 0 | 0.12485
4523 | 0 | 0.12485
4524 | 0.68668 | 0.81153
4525 | 0 | 0.12485
4526 | 0 | 0.12485
4527 | 0 | 0.12485
4528 | 0 | 0.12485
4529 | 0 | 0.12485
4530 | 5.1418 | 5.2666
4531 | 10.3103 | 10.4352
4532 | 0 | 0.12485
4533 | 1.0802 | 1.205
4534 | 0 | 0.12485
4535 | 0 | 0.12485
4536 | 0 | 0.12485
4537 | 0 | 0.12485
4538 | 0 | 0.12485
4539 | 0 | 0.12485
4540 | 0 | 0.12485
4541 | 0 | 0.12485
4542 | 10.3547 | 10.4796
4543 | 1.0857 | 1.2106
4544 | 1.4119 | 1.5367
4545 | 0 | 0.12485
4546 | 0 | 0.12485
4547 | 0 | 0.12485
4548 | 0.68594 | 0.81079
4549 | 0 | 0.12485
4550 | 0 | 0.12485
4551 | 0 | 0.12485
4552 | 0 | 0.12485
4553 | 0 | 0.12485
4554 | 5.1364 | 5.2612
4555 | 10.3003 | 10.4252
4556 | 0 | 0.12485
4557 | 1.0791 | 1.2039
4558 | 0 | 0.12485
4559 | 0 | 0.12485
4560 | 0 | 0.12485
4561 | 0 | 0.12485
4562 | 0 | 0.12485
4563 | 0 | 0.12485
4564 | 0 | 0.12485
4565 | 0 | 0.12485
4566 | 10.3443 | 10.4692
4567 | 1.0846 | 1.2094
4568 | 1.4104 | 1.5352
4569 | 0 | 0.12485
4570 | 0 | 0.12485
4571 | 0 | 0.12485
4572 | 0.68521 | 0.81006
4573 | 0 | 0.12485
4574 | 0 | 0.12485
4575 | 0 | 0.12485
4576 | 0 | 0.12485
4577 | 0 | 0.12485
4578 | 5.1311 | 5.2559
4579 | 10.2905 | 10.4154
4580 | 0 | 0.12485
4581 | 1.078 | 1.2028
4582 | 0 | 0.12485
4583 | 0 | 0.12485
4584 | 0 | 0.12485
4585 | 0 | 0.12485
4586 | 0 | 0.12485
4587 | 0 | 0.12485
4588 | 0 | 0.12485
4589 | 0 | 0.12485
4590 | 10.137 | 10.2619
4591 | 1.0979 | 1.2227
4592 | 1.4277 | 1.5525
4593 | 0 | 0.12485
4594 | 0 | 0.12485
4595 | 0 | 0.12485
4596 | 0.69357 | 0.81842
4597 | 0 | 0.12485
4598 | 0 | 0.12485
4599 | 0 | 0.12485
4600 | 0 | 0.12485
4601 | 0 | 0.12485
4602 | 5.1842 | 5.3091
4603 | 10.1724 | 10.2972
4604 | 0 | 0.12485
4605 | 1.0968 | 1.2217
4606 | 0 | 0.12485
4607 | 0 | 0.12485
4608 | 0 | 0.12485
4609 | 0 | 0.12485
4610 | 0 | 0.12485
4611 | 0 | 0.12485
4612 | 0 | 0.12485
4613 | 0 | 0.12485
4614 | 10.2915 | 10.4164
4615 | 1.1059 | 1.2307
4616 | 1.438 | 1.5629
4617 | 0 | 0.12485
4618 | 0 | 0.12485
4619 | 0 | 0.12485
4620 | 0.69859 | 0.82344
4621 | 0 | 0.12485
4622 | 0 | 0.12485
4623 | 0 | 0.12485
4624 | 0 | 0.12485
4625 | 0 | 0.12485
4626 | 5.2153 | 5.3401
4627 | 10.219 | 10.3439
4628 | 0 | 0.12485
4629 | 1.0991 | 1.224
4630 | 0 | 0.12485
4631 | 0 | 0.12485
4632 | 0 | 0.12485
4633 | 0 | 0.12485
4634 | 0 | 0.12485
4635 | 0 | 0.12485
4636 | 0 | 0.12485
4637 | 0 | 0.12485
4638 | 9.9058 | 10.0306
4639 | 1.113 | 1.2378
4640 | 1.4473 | 1.5721
4641 | 0 | 0.12485
4642 | 0 | 0.12485
4643 | 0 | 0.12485
4644 | 0.70306 | 0.82791
4645 | 0 | 0.12485
4646 | 0 | 0.12485
4647 | 0 | 0.12485
4648 | 0 | 0.12485
4649 | 0 | 0.12485
4650 | 5.0389 | 5.1637
4651 | 9.9333 | 10.0581
4652 | 0 | 0.12485
4653 | 1.1107 | 1.2356
4654 | 0 | 0.12485
4655 | 0 | 0.12485
4656 | 0 | 0.12485
4657 | 0 | 0.12485
4658 | 0 | 0.12485
4659 | 0 | 0.12485
4660 | 0 | 0.12485
4661 | 0 | 0.12485
4662 | 10.007 | 10.1318
4663 | 1.1184 | 1.2433
4664 | 1.4544 | 1.5792
4665 | 0 | 0.12485
4666 | 0 | 0.12485
4667 | 0 | 0.12485
4668 | 0.70648 | 0.83133
4669 | 0 | 0.12485
4670 | 0 | 0.12485
4671 | 0 | 0.12485
4672 | 0 | 0.12485
4673 | 0 | 0.12485
4674 | 5.0624 | 5.1873
4675 | 9.9724 | 10.0973
4676 | 0 | 0.12485
4677 | 1.1126 | 1.2375
4678 | 0 | 0.12485
4679 | 0 | 0.12485
4680 | 0 | 0.12485
4681 | 0 | 0.12485
4682 | 0 | 0.12485
4683 | 0 | 0.12485
4684 | 0 | 0.12485
4685 | 0 | 0.12485
4686 | 10.0235 | 10.1483
4687 | 1.1189 | 1.2437
4688 | 1.4549 | 1.5798
4689 | 0 | 0.12485
4690 | 0 | 0.12485
4691 | 0 | 0.12485
4692 | 0.70676 | 0.83161
4693 | 0 | 0.12485
4694 | 0 | 0.12485
4695 | 0 | 0.12485
4696 | 0 | 0.12485
4697 | 0 | 0.12485
4698 | 5.0642 | 5.189
4699 | 9.9749 | 10.0998
4700 | 0 | 0.12485
4701 | 1.1123 | 1.2371
4702 | 0 | 0.12485
4703 | 0 | 0.12485
4704 | 0 | 0.12485
4705 | 0 | 0.12485
4706 | 0 | 0.12485
4707 | 0 | 0.12485
4708 | 0 | 0.12485
4709 | 0 | 0.12485
4710 | 10.0206 | 10.1455
4711 | 1.1182 | 1.2431
4712 | 1.4541 | 1.5789
4713 | 0 | 0.12485
4714 | 0 | 0.12485
4715 | 0 | 0.12485
4716 | 0.70634 | 0.83119
4717 | 0 | 0.12485
4718 | 0 | 0.12485
4719 | 0 | 0.12485
4720 | 0 | 0.12485
4721 | 0 | 0.12485
4722 | 5.0611 | 5.1859
4723 | 9.9692 | 10.0941
4724 | 0 | 0.12485
4725 | 1.1115 | 1.2363
4726 | 0 | 0.12485
4727 | 0 | 0.12485
4728 | 0 | 0.12485
4729 | 0 | 0.12485
4730 | 0 | 0.12485
4731 | 0 | 0.12485
4732 | 0 | 0.12485
4733 | 0 | 0.12485
4734 | 10.0135 | 10.1384
4735 | 1.1173 | 1.2422
4736 | 1.4529 | 1.5778
4737 | 0 | 0.12485
4738 | 0 | 0.12485
4739 | 0 | 0.12485
4740 | 0.70577 | 0.83061
4741 | 0 | 0.12485
4742 | 0 | 0.12485
4743 | 0 | 0.12485
4744 | 0 | 0.12485
4745 | 0 | 0.12485
4746 | 5.057 | 5.1818
4747 | 9.9618 | 10.0867
4748 | 0 | 0.12485
4749 | 1.1106 | 1.2354
4750 | 0 | 0.12485
4751 | 0 | 0.12485
4752 | 0 | 0.12485
4753 | 0 | 0.12485
4754 | 0 | 0.12485
4755 | 0 | 0.12485
4756 | 0 | 0.12485
4757 | 0 | 0.12485
4758 | 10.0057 | 10.1306
4759 | 1.1164 | 1.2413
4760 | 1.4517 | 1.5766
4761 | 0 | 0.12485
4762 | 0 | 0.12485
4763 | 0 | 0.12485
4764 | 0.70518 | 0.83003
4765 | 0 | 0.12485
4766 | 0 | 0.12485
4767 | 0 | 0.12485
4768 | 0 | 0.12485
4769 | 0 | 0.12485
4770 | 5.0527 | 5.1776
4771 | 9.9543 | 10.0791
4772 | 0 | 0.12485
4773 | 1.1097 | 1.2345
4774 | 0 | 0.12485
4775 | 0 | 0.12485
4776 | 0 | 0.12485
4777 | 0 | 0.12485
4778 | 0 | 0.12485
4779 | 0 | 0.12485
4780 | 0 | 0.12485
4781 | 0 | 0.12485
4782 | 9.9979 | 10.1228
4783 | 1.1155 | 1.2404
4784 | 1.4506 | 1.5754
4785 | 0 | 0.12485
4786 | 0 | 0.12485
4787 | 0 | 0.12485
4788 | 0.7046 | 0.82945
4789 | 0 | 0.12485
4790 | 0 | 0.12485
4791 | 0 | 0.12485
4792 | 0 | 0.12485
4793 | 0 | 0.12485
4794 | 5.0486 | 5.1734
4795 | 9.9468 | 10.0717
4796 | 0 | 0.12485
4797 | 1.1088 | 1.2337
4798 | 0 | 0.12485
4799 | 0 | 0.12485
4800 | 0 | 0.12485
4801 | 0 | 0.12485
4802 | 0 | 0.12485
4803 | 0 | 0.12485
4804 | 0 | 0.12485
4805 | 0 | 0.12485
4806 | 9.9903 | 10.1152
4807 | 1.1147 | 1.2395
4808 | 1.4494 | 1.5743
4809 | 0 | 0.12485
4810 | 0 | 0.12485
4811 | 0 | 0.12485
4812 | 0.70404 | 0.82888
4813 | 0 | 0.12485
4814 | 0 | 0.12485
4815 | 0 | 0.12485
4816 | 0 | 0.12485
4817 | 0 | 0.12485
4818 | 5.0445 | 5.1694
4819 | 9.9397 | 10.0645
4820 | 0 | 0.12485
4821 | 1.108 | 1.2328
4822 | 0 | 0.12485
4823 | 0 | 0.12485
4824 | 0 | 0.12485
4825 | 0 | 0.12485
4826 | 0 | 0.12485
4827 | 0 | 0.12485
4828 | 0 | 0.12485
4829 | 0 | 0.12485
4830 | 9.983 | 10.1079
4831 | 1.1138 | 1.2387
4832 | 1.4483 | 1.5732
4833 | 0 | 0.12485
4834 | 0 | 0.12485
4835 | 0 | 0.12485
4836 | 0.70349 | 0.82834
4837 | 0 | 0.12485
4838 | 0 | 0.12485
4839 | 0 | 0.12485
4840 | 0 | 0.12485
4841 | 0 | 0.12485
4842 | 5.0406 | 5.1655
4843 | 9.9327 | 10.0576
4844 | 0 | 0.12485
4845 | 1.1072 | 1.232
4846 | 0 | 0.12485
4847 | 0 | 0.12485
4848 | 0 | 0.12485
4849 | 0 | 0.12485
4850 | 0 | 0.12485
4851 | 0 | 0.12485
4852 | 0 | 0.12485
4853 | 0 | 0.12485
4854 | 9.976 | 10.1008
4855 | 1.113 | 1.2378
4856 | 1.4473 | 1.5721
4857 | 0 | 0.12485
4858 | 0 | 0.12485
4859 | 0 | 0.12485
4860 | 0.70297 | 0.82782
4861 | 0 | 0.12485
4862 | 0 | 0.12485
4863 | 0 | 0.12485
4864 | 0 | 0.12485
4865 | 0 | 0.12485
4866 | 5.0369 | 5.1617
4867 | 9.926 | 10.0509
4868 | 0 | 0.12485
4869 | 1.1064 | 1.2312
4870 | 0 | 0.12485
4871 | 0 | 0.12485
4872 | 0 | 0.12485
4873 | 0 | 0.12485
4874 | 0 | 0.12485
4875 | 0 | 0.12485
4876 | 0 | 0.12485
4877 | 0 | 0.12485
4878 | 9.9692 | 10.0941
4879 | 1.1122 | 1.2371
4880 | 1.4462 | 1.5711
4881 | 0 | 0.12485
4882 | 0 | 0.12485
4883 | 0 | 0.12485
4884 | 0.70247 | 0.82732
4885 | 0 | 0.12485
4886 | 0 | 0.12485
4887 | 0 | 0.12485
4888 | 0 | 0.12485
4889 | 0 | 0.12485
4890 | 5.0333 | 5.1581
4891 | 9.9196 | 10.0445
4892 | 0 | 0.12485
4893 | 1.1056 | 1.2305
4894 | 0 | 0.12485
4895 | 0 | 0.12485
4896 | 0 | 0.12485
4897 | 0 | 0.12485
4898 | 0 | 0.12485
4899 | 0 | 0.12485
4900 | 0 | 0.12485
4901 | 0 | 0.12485
4902 | 9.9627 | 10.0876
4903 | 1.1115 | 1.2363
4904 | 1.4453 | 1.5701
4905 | 0 | 0.12485
4906 | 0 | 0.12485
4907 | 0 | 0.12485
4908 | 0.70199 | 0.82684
4909 | 0 | 0.12485
4910 | 0 | 0.12485
4911 | 0 | 0.12485
4912 | 0 | 0.12485
4913 | 0 | 0.12485
4914 | 5.0298 | 5.1547
4915 | 9.9134 | 10.0383
4916 | 0 | 0.12485
4917 | 1.1049 | 1.2298
4918 | 0 | 0.12485
4919 | 0 | 0.12485
4920 | 0 | 0.12485
4921 | 0 | 0.12485
4922 | 0 | 0.12485
4923 | 0 | 0.12485
4924 | 0 | 0.12485
4925 | 0 | 0.12485
4926 | 9.9565 | 10.0814
4927 | 1.1108 | 1.2356
4928 | 1.4443 | 1.5692
4929 | 0 | 0.12485
4930 | 0 | 0.12485
4931 | 0 | 0.12485
4932 | 0.70153 | 0.82638
4933 | 0 | 0.12485
4934 | 0 | 0.12485
4935 | 0 | 0.12485
4936 | 0 | 0.12485
4937 | 0 | 0.12485
4938 | 5.0265 | 5.1514
4939 | 9.9075 | 10.0324
4940 | 0 | 0.12485
4941 | 1.1042 | 1.2291
4942 | 0 | 0.12485
4943 | 0 | 0.12485
4944 | 0 | 0.12485
4945 | 0 | 0.12485
4946 | 0 | 0.12485
4947 | 0 | 0.12485
4948 | 0 | 0.12485
4949 | 0 | 0.12485
4950 | 9.9506 | 10.0754
4951 | 1.1101 | 1.2349
4952 | 1.4434 | 1.5683
4953 | 0 | 0.12485
4954 | 0 | 0.12485
4955 | 0 | 0.12485
4956 | 0.70109 | 0.82594
4957 | 0 | 0.12485
4958 | 0 | 0.12485
4959 | 0 | 0.12485
4960 | 0 | 0.12485
4961 | 0 | 0.12485
4962 | 5.0234 | 5.1482
4963 | 9.9019 | 10.0267
4964 | 0 | 0.12485
4965 | 1.1036 | 1.2284
4966 | 0 | 0.12485
4967 | 0 | 0.12485
4968 | 0 | 0.12485
4969 | 0 | 0.12485
4970 | 0 | 0.12485
4971 | 0 | 0.12485
4972 | 0 | 0.12485
4973 | 0 | 0.12485
4974 | 9.945 | 10.0698
4975 | 1.1094 | 1.2343
4976 | 1.4426 | 1.5674
4977 | 0 | 0.12485
4978 | 0 | 0.12485
4979 | 0 | 0.12485
4980 | 0.70067 | 0.82552
4981 | 0 | 0.12485
4982 | 0 | 0.12485
4983 | 0 | 0.12485
4984 | 0 | 0.12485
4985 | 0 | 0.12485
4986 | 5.0203 | 5.1452
4987 | 9.8965 | 10.0214
4988 | 0 | 0.12485
4989 | 1.1029 | 1.2278
4990 | 0 | 0.12485
4991 | 0 | 0.12485
4992 | 0 | 0.12485
4993 | 0 | 0.12485
4994 | 0 | 0.12485
4995 | 0 | 0.12485
4996 | 0 | 0.12485
4997 | 0 | 0.12485
4998 | 9.9396 | 10.0644
4999 | 1.1088 | 1.2336
5000 | 1.4418 | 1.5666
5001 | 0 | 0.12485
5002 | 0 | 0.12485
5003 | 0 | 0.12485
5004 | 0.70027 | 0.82512
5005 | 0 | 0.12485
5006 | 0 | 0.12485
5007 | 0 | 0.12485
5008 | 0 | 0.12485
5009 | 0 | 0.12485
5010 | 5.0175 | 5.1423
5011 | 9.8914 | 10.0163
5012 | 0 | 0.12485
5013 | 1.1023 | 1.2272
5014 | 0 | 0.12485
5015 | 0 | 0.12485
5016 | 0 | 0.12485
5017 | 0 | 0.12485
5018 | 0 | 0.12485
5019 | 0 | 0.12485
5020 | 0 | 0.12485
5021 | 0 | 0.12485
5022 | 9.9345 | 10.0594
5023 | 1.1082 | 1.2331
5024 | 1.441 | 1.5659
5025 | 0 | 0.12485
5026 | 0 | 0.12485
5027 | 0 | 0.12485
5028 | 0.6999 | 0.82475
5029 | 0 | 0.12485
5030 | 0 | 0.12485
5031 | 0 | 0.12485
5032 | 0 | 0.12485
5033 | 0 | 0.12485
5034 | 5.0148 | 5.1396
5035 | 9.8866 | 10.0114
5036 | 0 | 0.12485
5037 | 1.1018 | 1.2266
5038 | 0 | 0.12485
5039 | 0 | 0.12485
5040 | 0 | 0.12485
5041 | 0 | 0.12485
5042 | 0 | 0.12485
5043 | 0 | 0.12485
5044 | 0 | 0.12485
5045 | 0 | 0.12485
5046 | 9.9298 | 10.0546
5047 | 1.1077 | 1.2325
5048 | 1.4403 | 1.5651
5049 | 0 | 0.12485
5050 | 0 | 0.12485
5051 | 0 | 0.12485
5052 | 0.69954 | 0.82439
5053 | 0 | 0.12485
5054 | 0 | 0.12485
5055 | 0 | 0.12485
5056 | 0 | 0.12485
5057 | 0 | 0.12485
5058 | 5.0122 | 5.1371
5059 | 9.882 | 10.0069
5060 | 0 | 0.12485
5061 | 1.1012 | 1.2261
5062 | 0 | 0.12485
5063 | 0 | 0.12485
5064 | 0 | 0.12485
5065 | 0 | 0.12485
5066 | 0 | 0.12485
5067 | 0 | 0.12485
5068 | 0 | 0.12485
5069 | 0 | 0.12485
5070 | 9.9253 | 10.0501
5071 | 1.1071 | 1.232
5072 | 1.4396 | 1.5645
5073 | 0 | 0.12485
5074 | 0 | 0.12485
5075 | 0 | 0.12485
5076 | 0.69921 | 0.82406
5077 | 0 | 0.12485
5078 | 0 | 0.12485
5079 | 0 | 0.12485
5080 | 0 | 0.12485
5081 | 0 | 0.12485
5082 | 5.0098 | 5.1347
5083 | 9.8777 | 10.0026
5084 | 0 | 0.12485
5085 | 1.1007 | 1.2256
5086 | 0 | 0.12485
5087 | 0 | 0.12485
5088 | 0 | 0.12485
5089 | 0 | 0.12485
5090 | 0 | 0.12485
5091 | 0 | 0.12485
5092 | 0 | 0.12485
5093 | 0 | 0.12485
5094 | 9.9211 | 10.0459
5095 | 1.1066 | 1.2315
5096 | 1.439 | 1.5638
5097 | 0 | 0.12485
5098 | 0 | 0.12485
5099 | 0 | 0.12485
5100 | 0.69889 | 0.82374
5101 | 0 | 0.12485
5102 | 0 | 0.12485
5103 | 0 | 0.12485
5104 | 0 | 0.12485
5105 | 0 | 0.12485
5106 | 5.0076 | 5.1324
5107 | 9.8737 | 9.9986
5108 | 0 | 0.12485
5109 | 1.1003 | 1.2251
5110 | 0 | 0.12485
5111 | 0 | 0.12485
5112 | 0 | 0.12485
5113 | 0 | 0.12485
5114 | 0 | 0.12485
5115 | 0 | 0.12485
5116 | 0 | 0.12485
5117 | 0 | 0.12485
5118 | 9.9172 | 10.042
5119 | 1.1062 | 1.231
5120 | 1.4384 | 1.5632
5121 | 0 | 0.12485
5122 | 0 | 0.12485
5123 | 0 | 0.12485
5124 | 0.6986 | 0.82345
5125 | 0 | 0.12485
5126 | 0 | 0.12485
5127 | 0 | 0.12485
5128 | 0 | 0.12485
5129 | 0 | 0.12485
5130 | 5.0055 | 5.1303
5131 | 9.87 | 9.9948
5132 | 0 | 0.12485
5133 | 1.0998 | 1.2247
5134 | 0 | 0.12485
5135 | 0 | 0.12485
5136 | 0 | 0.12485
5137 | 0 | 0.12485
5138 | 0 | 0.12485
5139 | 0 | 0.12485
5140 | 0 | 0.12485
5141 | 0 | 0.12485
5142 | 9.9136 | 10.0384
5143 | 1.1058 | 1.2306
5144 | 1.4378 | 1.5627
5145 | 0 | 0.12485
5146 | 0 | 0.12485
5147 | 0 | 0.12485
5148 | 0.69833 | 0.82318
5149 | 0 | 0.12485
5150 | 0 | 0.12485
5151 | 0 | 0.12485
5152 | 0 | 0.12485
5153 | 0 | 0.12485
5154 | 5.0035 | 5.1284
5155 | 9.8665 | 9.9914
5156 | 0 | 0.12485
5157 | 1.0994 | 1.2243
5158 | 0 | 0.12485
5159 | 0 | 0.12485
5160 | 0 | 0.12485
5161 | 0 | 0.12485
5162 | 0 | 0.12485
5163 | 0 | 0.12485
5164 | 0 | 0.12485
5165 | 0 | 0.12485
5166 | 9.9103 | 10.0351
5167 | 1.1054 | 1.2302
5168 | 1.4373 | 1.5622
5169 | 0 | 0.12485
5170 | 0 | 0.12485
5171 | 0 | 0.12485
5172 | 0.69808 | 0.82293
5173 | 0 | 0.12485
5174 | 0 | 0.12485
5175 | 0 | 0.12485
5176 | 0 | 0.12485
5177 | 0 | 0.12485
5178 | 5.0017 | 5.1265
5179 | 9.8631 | 9.9879
5180 | 0 | 0.12485
5181 | 1.099 | 1.2239
5182 | 0 | 0.12485
5183 | 0 | 0.12485
5184 | 0 | 0.12485
5185 | 0 | 0.12485
5186 | 0 | 0.12485
5187 | 0 | 0.12485
5188 | 0 | 0.12485
5189 | 0 | 0.12485
5190 | 9.9071 | 10.0319
5191 | 1.105 | 1.2299
5192 | 1.4369 | 1.5617
5193 | 0 | 0.12485
5194 | 0 | 0.12485
5195 | 0 | 0.12485
5196 | 0.69785 | 0.8227
5197 | 0 | 0.12485
5198 | 0 | 0.12485
5199 | 0 | 0.12485
5200 | 0 | 0.12485
5201 | 0 | 0.12485
5202 | 5 | 5.1248
5203 | 9.8596 | 9.9844
5204 | 0 | 0.12485
5205 | 1.0986 | 1.2235
5206 | 0 | 0.12485
5207 | 0 | 0.12485
5208 | 0 | 0.12485
5209 | 0 | 0.12485
5210 | 0 | 0.12485
5211 | 0 | 0.12485
5212 | 0 | 0.12485
5213 | 0 | 0.12485
5214 | 9.9041 | 10.0289
5215 | 1.1047 | 1.2295
5216 | 1.4364 | 1.5613
5217 | 0 | 0.12485
5218 | 0 | 0.12485
5219 | 0 | 0.12485
5220 | 0.69763 | 0.82248
5221 | 0 | 0.12485
5222 | 0 | 0.12485
5223 | 0 | 0.12485
5224 | 0 | 0.12485
5225 | 0 | 0.12485
5226 | 4.9984 | 5.1232
5227 | 9.8564 | 9.9812
5228 | 0 | 0.12485
5229 | 1.0983 | 1.2231
5230 | 0 | 0.12485
5231 | 0 | 0.12485
5232 | 0 | 0.12485
5233 | 0 | 0.12485
5234 | 0 | 0.12485
5235 | 0 | 0.12485
5236 | 0 | 0.12485
5237 | 0 | 0.12485
5238 | 9.9013 | 10.0262
5239 | 1.1044 | 1.2292
5240 | 1.436 | 1.5609
5241 | 0 | 0.12485
5242 | 0 | 0.12485
5243 | 0 | 0.12485
5244 | 0.69744 | 0.82229
5245 | 0 | 0.12485
5246 | 0 | 0.12485
5247 | 0 | 0.12485
5248 | 0 | 0.12485
5249 | 0 | 0.12485
5250 | 4.9969 | 5.1218
5251 | 9.8535 | 9.9783
5252 | 0 | 0.12485
5253 | 1.098 | 1.2228
5254 | 0 | 0.12485
5255 | 0 | 0.12485
5256 | 0 | 0.12485
5257 | 0 | 0.12485
5258 | 0 | 0.12485
5259 | 0 | 0.12485
5260 | 0 | 0.12485
5261 | 0 | 0.12485
5262 | 9.8989 | 10.0237
5263 | 1.1041 | 1.229
5264 | 1.4357 | 1.5605
5265 | 0 | 0.12485
5266 | 0 | 0.12485
5267 | 0 | 0.12485
5268 | 0.69727 | 0.82212
5269 | 0 | 0.12485
5270 | 0 | 0.12485
5271 | 0 | 0.12485
5272 | 0 | 0.12485
5273 | 0 | 0.12485
5274 | 4.9957 | 5.1205
5275 | 9.8509 | 9.9758
5276 | 0 | 0.12485
5277 | 1.0977 | 1.2225
5278 | 0 | 0.12485
5279 | 0 | 0.12485
5280 | 0 | 0.12485
5281 | 0 | 0.12485
5282 | 0 | 0.12485
5283 | 0 | 0.12485
5284 | 0 | 0.12485
5285 | 0 | 0.12485
5286 | 9.8968 | 10.0217
5287 | 1.1039 | 1.2287
5288 | 1.4354 | 1.5602
5289 | 0 | 0.12485
5290 | 0 | 0.12485
5291 | 0 | 0.12485
5292 | 0.69712 | 0.82197
5293 | 0 | 0.12485
5294 | 0 | 0.12485
5295 | 0 | 0.12485
5296 | 0 | 0.12485
5297 | 0 | 0.12485
5298 | 4.9946 | 5.1194
5299 | 9.8487 | 9.9735
5300 | 0 | 0.12485
5301 | 1.0975 | 1.2223
5302 | 0 | 0.12485
5303 | 0 | 0.12485
5304 | 0 | 0.12485
5305 | 0 | 0.12485
5306 | 0 | 0.12485
5307 | 0 | 0.12485
5308 | 0 | 0.12485
5309 | 0 | 0.12485
5310 | 9.8951 | 10.0199
5311 | 1.1037 | 1.2285
5312 | 1.4351 | 1.56
5313 | 0 | 0.12485
5314 | 0 | 0.12485
5315 | 0 | 0.12485
5316 | 0.69699 | 0.82184
5317 | 0 | 0.12485
5318 | 0 | 0.12485
5319 | 0 | 0.12485
5320 | 0 | 0.12485
5321 | 0 | 0.12485
5322 | 4.9936 | 5.1185
5323 | 9.8468 | 9.9717
5324 | 0 | 0.12485
5325 | 1.0973 | 1.2221
5326 | 0 | 0.12485
5327 | 0 | 0.12485
5328 | 0 | 0.12485
5329 | 0 | 0.12485
5330 | 0 | 0.12485
5331 | 0 | 0.12485
5332 | 0 | 0.12485
5333 | 0 | 0.12485
5334 | 9.8936 | 10.0185
5335 | 1.1035 | 1.2284
5336 | 1.4349 | 1.5597
5337 | 0 | 0.12485
5338 | 0 | 0.12485
5339 | 0 | 0.12485
5340 | 0.69689 | 0.82174
5341 | 0 | 0.12485
5342 | 0 | 0.12485
5343 | 0 | 0.12485
5344 | 0 | 0.12485
5345 | 0 | 0.12485
5346 | 4.9929 | 5.1177
5347 | 9.8453 | 9.9701
5348 | 0 | 0.12485
5349 | 1.0971 | 1.2219
5350 | 0 | 0.12485
5351 | 0 | 0.12485
5352 | 0 | 0.12485
5353 | 0 | 0.12485
5354 | 0 | 0.12485
5355 | 0 | 0.12485
5356 | 0 | 0.12485
5357 | 0 | 0.12485
5358 | 9.8925 | 10.0174
5359 | 1.1034 | 1.2283
5360 | 1.4347 | 1.5596
5361 | 0 | 0.12485
5362 | 0 | 0.12485
5363 | 0 | 0.12485
5364 | 0.69681 | 0.82166
5365 | 0 | 0.12485
5366 | 0 | 0.12485
5367 | 0 | 0.12485
5368 | 0 | 0.12485
5369 | 0 | 0.12485
5370 | 4.9923 | 5.1171
5371 | 9.8441 | 9.9689
5372 | 0 | 0.12485
5373 | 1.097 | 1.2218
5374 | 0 | 0.12485
5375 | 0 | 0.12485
5376 | 0 | 0.12485
5377 | 0 | 0.12485
5378 | 0 | 0.12485
5379 | 0 | 0.12485
5380 | 0 | 0.12485
5381 | 0 | 0.12485
5382 | 9.8918 | 10.0166
5383 | 1.1033 | 1.2282
5384 | 1.4346 | 1.5595
5385 | 0 | 0.12485
5386 | 0 | 0.12485
5387 | 0 | 0.12485
5388 | 0.69675 | 0.8216
5389 | 0 | 0.12485
5390 | 0 | 0.12485
5391 | 0 | 0.12485
5392 | 0 | 0.12485
5393 | 0 | 0.12485
5394 | 4.9919 | 5.1167
5395 | 9.8432 | 9.9681
5396 | 0 | 0.12485
5397 | 1.0969 | 1.2217
5398 | 0 | 0.12485
5399 | 0 | 0.12485
5400 | 0 | 0.12485
5401 | 0 | 0.12485
5402 | 0 | 0.12485
5403 | 0 | 0.12485
5404 | 0 | 0.12485
5405 | 0 | 0.12485
5406 | 9.8914 | 10.0162
5407 | 1.1033 | 1.2281
5408 | 1.4346 | 1.5594
5409 | 0 | 0.12485
5410 | 0 | 0.12485
5411 | 0 | 0.12485
5412 | 0.69672 | 0.82157
5413 | 0 | 0.12485
5414 | 0 | 0.12485
5415 | 0 | 0.12485
5416 | 0 | 0.12485
5417 | 0 | 0.12485
5418 | 4.9916 | 5.1165
5419 | 9.8427 | 9.9676
5420 | 0 | 0.12485
5421 | 1.0968 | 1.2217
5422 | 0 | 0.12485
5423 | 0 | 0.12485
5424 | 0 | 0.12485
5425 | 0 | 0.12485
5426 | 0 | 0.12485
5427 | 0 | 0.12485
5428 | 0 | 0.12485
5429 | 0 | 0.12485
5430 | 9.8913 | 10.0161
5431 | 1.1032 | 1.2281
5432 | 1.4345 | 1.5594
5433 | 0 | 0.12485
5434 | 0 | 0.12485
5435 | 0 | 0.12485
5436 | 0.69671 | 0.82156
5437 | 0 | 0.12485
5438 | 0 | 0.12485
5439 | 0 | 0.12485
5440 | 0 | 0.12485
5441 | 0 | 0.12485
5442 | 4.9915 | 5.1164
5443 | 9.8425 | 9.9674
5444 | 0 | 0.12485
5445 | 1.0968 | 1.2216
5446 | 0 | 0.12485
5447 | 0 | 0.12485
5448 | 0 | 0.12485
5449 | 0 | 0.12485
5450 | 0 | 0.12485
5451 | 0 | 0.12485
5452 | 0 | 0.12485
5453 | 0 | 0.12485
5454 | 9.8915 | 10.0164
5455 | 1.1033 | 1.2281
5456 | 1.4346 | 1.5594
5457 | 0 | 0.12485
5458 | 0 | 0.12485
5459 | 0 | 0.12485
5460 | 0.69672 | 0.82157
5461 | 0 | 0.12485
5462 | 0 | 0.12485
5463 | 0 | 0.12485
5464 | 0 | 0.12485
5465 | 0 | 0.12485
5466 | 4.9916 | 5.1165
5467 | 9.8427 | 9.9675
5468 | 0 | 0.12485
5469 | 1.0968 | 1.2216
5470 | 0 | 0.12485
5471 | 0 | 0.12485
5472 | 0 | 0.12485
5473 | 0 | 0.12485
5474 | 0 | 0.12485
5475 | 0 | 0.12485
5476 | 0 | 0.12485
5477 | 0 | 0.12485
5478 | 9.8921 | 10.0169
5479 | 1.1033 | 1.2282
5480 | 1.4346 | 1.5595
5481 | 0 | 0.12485
5482 | 0 | 0.12485
5483 | 0 | 0.12485
5484 | 0.69676 | 0.82161
5485 | 0 | 0.12485
5486 | 0 | 0.12485
5487 | 0 | 0.12485
5488 | 0 | 0.12485
5489 | 0 | 0.12485
5490 | 4.9919 | 5.1167
5491 | 9.8432 | 9.9681
5492 | 0 | 0.12485
5493 | 1.0969 | 1.2217
5494 | 0 | 0.12485
5495 | 0 | 0.12485
5496 | 0 | 0.12485
5497 | 0 | 0.12485
5498 | 0 | 0.12485
5499 | 0 | 0.12485
5500 | 0 | 0.12485
5501 | 0 | 0.12485
5502 | 9.893 | 10.0179
5503 | 1.1034 | 1.2283
5504 | 1.4348 | 1.5596
5505 | 0 | 0.12485
5506 | 0 | 0.12485
5507 | 0 | 0.12485
5508 | 0.69682 | 0.82167
5509 | 0 | 0.12485
5510 | 0 | 0.12485
5511 | 0 | 0.12485
5512 | 0 | 0.12485
5513 | 0 | 0.12485
5514 | 4.9923 | 5.1172
5515 | 9.844 | 9.9689
5516 | 0 | 0.12485
5517 | 1.0969 | 1.2218
5518 | 0 | 0.12485
5519 | 0 | 0.12485
5520 | 0 | 0.12485
5521 | 0 | 0.12485
5522 | 0 | 0.12485
5523 | 0 | 0.12485
5524 | 0 | 0.12485
5525 | 0 | 0.12485
5526 | 9.8943 | 10.0191
5527 | 1.1035 | 1.2284
5528 | 1.4349 | 1.5598
5529 | 0 | 0.12485
5530 | 0 | 0.12485
5531 | 0 | 0.12485
5532 | 0.6969 | 0.82175
5533 | 0 | 0.12485
5534 | 0 | 0.12485
5535 | 0 | 0.12485
5536 | 0 | 0.12485
5537 | 0 | 0.12485
5538 | 4.9929 | 5.1178
5539 | 9.8452 | 9.9701
5540 | 0 | 0.12485
5541 | 1.0971 | 1.2219
5542 | 0 | 0.12485
5543 | 0 | 0.12485
5544 | 0 | 0.12485
5545 | 0 | 0.12485
5546 | 0 | 0.12485
5547 | 0 | 0.12485
5548 | 0 | 0.12485
5549 | 0 | 0.12485
5550 | 9.8958 | 10.0207
5551 | 1.1037 | 1.2286
5552 | 1.4351 | 1.56
5553 | 0 | 0.12485
5554 | 0 | 0.12485
5555 | 0 | 0.12485
5556 | 0.69701 | 0.82186
5557 | 0 | 0.12485
5558 | 0 | 0.12485
5559 | 0 | 0.12485
5560 | 0 | 0.12485
5561 | 0 | 0.12485
5562 | 4.9937 | 5.1186
5563 | 9.8468 | 9.9716
5564 | 0 | 0.12485
5565 | 1.0972 | 1.2221
5566 | 0 | 0.12485
5567 | 0 | 0.12485
5568 | 0 | 0.12485
5569 | 0 | 0.12485
5570 | 0 | 0.12485
5571 | 0 | 0.12485
5572 | 0 | 0.12485
5573 | 0 | 0.12485
5574 | 9.8977 | 10.0226
5575 | 1.1039 | 1.2288
5576 | 1.4354 | 1.5603
5577 | 0 | 0.12485
5578 | 0 | 0.12485
5579 | 0 | 0.12485
5580 | 0.69714 | 0.82198
5581 | 0 | 0.12485
5582 | 0 | 0.12485
5583 | 0 | 0.12485
5584 | 0 | 0.12485
5585 | 0 | 0.12485
5586 | 4.9947 | 5.1195
5587 | 9.8486 | 9.9735
5588 | 0 | 0.12485
5589 | 1.0974 | 1.2223
5590 | 0 | 0.12485
5591 | 0 | 0.12485
5592 | 0 | 0.12485
5593 | 0 | 0.12485
5594 | 0 | 0.12485
5595 | 0 | 0.12485
5596 | 0 | 0.12485
5597 | 0 | 0.12485
5598 | 9.9 | 10.0248
5599 | 1.1042 | 1.229
5600 | 1.4357 | 1.5606
5601 | 0 | 0.12485
5602 | 0 | 0.12485
5603 | 0 | 0.12485
5604 | 0.69729 | 0.82214
5605 | 0 | 0.12485
5606 | 0 | 0.12485
5607 | 0 | 0.12485
5608 | 0 | 0.12485
5609 | 0 | 0.12485
5610 | 4.9958 | 5.1206
5611 | 9.8508 | 9.9757
5612 | 0 | 0.12485
5613 | 1.0977 | 1.2225
5614 | 0 | 0.12485
5615 | 0 | 0.12485
5616 | 0 | 0.12485
5617 | 0 | 0.12485
5618 | 0 | 0.12485
5619 | 0 | 0.12485
5620 | 0 | 0.12485
5621 | 0 | 0.12485
5622 | 9.9025 | 10.0274
5623 | 1.1044 | 1.2293
5624 | 1.4361 | 1.5609
5625 | 0 | 0.12485
5626 | 0 | 0.12485
5627 | 0 | 0.12485
5628 | 0.69747 | 0.82231
5629 | 0 | 0.12485
5630 | 0 | 0.12485
5631 | 0 | 0.12485
5632 | 0 | 0.12485
5633 | 0 | 0.12485
5634 | 4.9971 | 5.1219
5635 | 9.8534 | 9.9782
5636 | 0 | 0.12485
5637 | 1.0979 | 1.2228
5638 | 0 | 0.12485
5639 | 0 | 0.12485
5640 | 0 | 0.12485
5641 | 0 | 0.12485
5642 | 0 | 0.12485
5643 | 0 | 0.12485
5644 | 0 | 0.12485
5645 | 0 | 0.12485
5646 | 9.9054 | 10.0303
5647 | 1.1047 | 1.2296
5648 | 1.4365 | 1.5613
5649 | 0 | 0.12485
5650 | 0 | 0.12485
5651 | 0 | 0.12485
5652 | 0.69766 | 0.82251
5653 | 0 | 0.12485
5654 | 0 | 0.12485
5655 | 0 | 0.12485
5656 | 0 | 0.12485
5657 | 0 | 0.12485
5658 | 4.9985 | 5.1234
5659 | 9.8562 | 9.9811
5660 | 0 | 0.12485
5661 | 1.0982 | 1.2231
5662 | 0 | 0.12485
5663 | 0 | 0.12485
5664 | 0 | 0.12485
5665 | 0 | 0.12485
5666 | 0 | 0.12485
5667 | 0 | 0.12485
5668 | 0 | 0.12485
5669 | 0 | 0.12485
5670 | 9.9087 | 10.0335
5671 | 1.1051 | 1.2299
5672 | 1.4369 | 1.5618
5673 | 0 | 0.12485
5674 | 0 | 0.12485
5675 | 0 | 0.12485
5676 | 0.69788 | 0.82273
5677 | 0 | 0.12485
5678 | 0 | 0.12485
5679 | 0 | 0.12485
5680 | 0 | 0.12485
5681 | 0 | 0.12485
5682 | 5.0002 | 5.125
5683 | 9.8594 | 9.9843
5684 | 0 | 0.12485
5685 | 1.0986 | 1.2234
5686 | 0 | 0.12485
5687 | 0 | 0.12485
5688 | 0 | 0.12485
5689 | 0 | 0.12485
5690 | 0 | 0.12485
5691 | 0 | 0.12485
5692 | 0 | 0.12485
5693 | 0 | 0.12485
5694 | 9.9122 | 10.0371
5695 | 1.1055 | 1.2303
5696 | 1.4374 | 1.5623
5697 | 0 | 0.12485
5698 | 0 | 0.12485
5699 | 0 | 0.12485
5700 | 0.69813 | 0.82298
5701 | 0 | 0.12485
5702 | 0 | 0.12485
5703 | 0 | 0.12485
5704 | 0 | 0.12485
5705 | 0 | 0.12485
5706 | 5.0019 | 5.1268
5707 | 9.863 | 9.9878
5708 | 0 | 0.12485
5709 | 1.099 | 1.2238
5710 | 0 | 0.12485
5711 | 0 | 0.12485
5712 | 0 | 0.12485
5713 | 0 | 0.12485
5714 | 0 | 0.12485
5715 | 0 | 0.12485
5716 | 0 | 0.12485
5717 | 0 | 0.12485
5718 | 9.9161 | 10.041
5719 | 1.1059 | 1.2307
5720 | 1.438 | 1.5628
5721 | 0 | 0.12485
5722 | 0 | 0.12485
5723 | 0 | 0.12485
5724 | 0.6984 | 0.82325
5725 | 0 | 0.12485
5726 | 0 | 0.12485
5727 | 0 | 0.12485
5728 | 0 | 0.12485
5729 | 0 | 0.12485
5730 | 5.0039 | 5.1288
5731 | 9.8669 | 9.9917
5732 | 0 | 0.12485
5733 | 1.0994 | 1.2242
5734 | 0 | 0.12485
5735 | 0 | 0.12485
5736 | 0 | 0.12485
5737 | 0 | 0.12485
5738 | 0 | 0.12485
5739 | 0 | 0.12485
5740 | 0 | 0.12485
5741 | 0 | 0.12485
5742 | 9.9203 | 10.0452
5743 | 1.1063 | 1.2312
5744 | 1.4386 | 1.5634
5745 | 0 | 0.12485
5746 | 0 | 0.12485
5747 | 0 | 0.12485
5748 | 0.69869 | 0.82354
5749 | 0 | 0.12485
5750 | 0 | 0.12485
5751 | 0 | 0.12485
5752 | 0 | 0.12485
5753 | 0 | 0.12485
5754 | 5.006 | 5.1309
5755 | 9.8709 | 9.9957
5756 | 0 | 0.12485
5757 | 1.0998 | 1.2247
5758 | 0 | 0.12485
5759 | 0 | 0.12485
5760 | 0 | 0.12485
5761 | 0 | 0.12485
5762 | 0 | 0.12485
5763 | 0 | 0.12485
5764 | 0 | 0.12485
5765 | 0 | 0.12485
5766 | 9.9247 | 10.0496
5767 | 1.1068 | 1.2317
5768 | 1.4392 | 1.564
5769 | 0 | 0.12485
5770 | 0 | 0.12485
5771 | 0 | 0.12485
5772 | 0.699 | 0.82384
5773 | 0 | 0.12485
5774 | 0 | 0.12485
5775 | 0 | 0.12485
5776 | 0 | 0.12485
5777 | 0 | 0.12485
5778 | 5.0082 | 5.1331
5779 | 9.8748 | 9.9997
5780 | 0 | 0.12485
5781 | 1.1003 | 1.2251
5782 | 0 | 0.12485
5783 | 0 | 0.12485
5784 | 0 | 0.12485
5785 | 0 | 0.12485
5786 | 0 | 0.12485
5787 | 0 | 0.12485
5788 | 0 | 0.12485
5789 | 0 | 0.12485
5790 | 9.9293 | 10.0541
5791 | 1.1073 | 1.2322
5792 | 1.4398 | 1.5647
5793 | 0 | 0.12485
5794 | 0 | 0.12485
5795 | 0 | 0.12485
5796 | 0.69932 | 0.82417
5797 | 0 | 0.12485
5798 | 0 | 0.12485
5799 | 0 | 0.12485
5800 | 0 | 0.12485
5801 | 0 | 0.12485
5802 | 5.0105 | 5.1354
5803 | 9.8789 | 10.0038
5804 | 0 | 0.12485
5805 | 1.1007 | 1.2256
5806 | 0 | 0.12485
5807 | 0 | 0.12485
5808 | 0 | 0.12485
5809 | 0 | 0.12485
5810 | 0 | 0.12485
5811 | 0 | 0.12485
5812 | 0 | 0.12485
5813 | 0 | 0.12485
5814 | 9.934 | 10.0589
5815 | 1.1078 | 1.2327
5816 | 1.4405 | 1.5654
5817 | 0 | 0.12485
5818 | 0 | 0.12485
5819 | 0 | 0.12485
5820 | 0.69966 | 0.82451
5821 | 0 | 0.12485
5822 | 0 | 0.12485
5823 | 0 | 0.12485
5824 | 0 | 0.12485
5825 | 0 | 0.12485
5826 | 5.013 | 5.1379
5827 | 9.8833 | 10.0082
5828 | 0 | 0.12485
5829 | 1.1012 | 1.2261
5830 | 0 | 0.12485
5831 | 0 | 0.12485
5832 | 0 | 0.12485
5833 | 0 | 0.12485
5834 | 0 | 0.12485
5835 | 0 | 0.12485
5836 | 0 | 0.12485
5837 | 0 | 0.12485
5838 | 9.9391 | 10.0639
5839 | 1.1084 | 1.2333
5840 | 1.4413 | 1.5661
5841 | 0 | 0.12485
5842 | 0 | 0.12485
5843 | 0 | 0.12485
5844 | 0.70002 | 0.82487
5845 | 0 | 0.12485
5846 | 0 | 0.12485
5847 | 0 | 0.12485
5848 | 0 | 0.12485
5849 | 0 | 0.12485
5850 | 5.0156 | 5.1405
5851 | 9.8879 | 10.0128
5852 | 0 | 0.12485
5853 | 1.1018 | 1.2266
5854 | 0 | 0.12485
5855 | 0 | 0.12485
5856 | 0 | 0.12485
5857 | 0 | 0.12485
5858 | 0 | 0.12485
5859 | 0 | 0.12485
5860 | 0 | 0.12485
5861 | 0 | 0.12485
5862 | 9.9444 | 10.0692
5863 | 1.109 | 1.2339
5864 | 1.4421 | 1.5669
5865 | 0 | 0.12485
5866 | 0 | 0.12485
5867 | 0 | 0.12485
5868 | 0.70041 | 0.82525
5869 | 0 | 0.12485
5870 | 0 | 0.12485
5871 | 0 | 0.12485
5872 | 0 | 0.12485
5873 | 0 | 0.12485
5874 | 5.0184 | 5.1432
5875 | 9.8929 | 10.0177
5876 | 0 | 0.12485
5877 | 1.1024 | 1.2272
5878 | 0 | 0.12485
5879 | 0 | 0.12485
5880 | 0 | 0.12485
5881 | 0 | 0.12485
5882 | 0 | 0.12485
5883 | 0 | 0.12485
5884 | 0 | 0.12485
5885 | 0 | 0.12485
5886 | 9.95 | 10.0749
5887 | 1.1096 | 1.2345
5888 | 1.4429 | 1.5677
5889 | 0 | 0.12485
5890 | 0 | 0.12485
5891 | 0 | 0.12485
5892 | 0.70081 | 0.82566
5893 | 0 | 0.12485
5894 | 0 | 0.12485
5895 | 0 | 0.12485
5896 | 0 | 0.12485
5897 | 0 | 0.12485
5898 | 5.0213 | 5.1461
5899 | 9.898 | 10.0229
5900 | 0 | 0.12485
5901 | 1.103 | 1.2278
5902 | 0 | 0.12485
5903 | 0 | 0.12485
5904 | 0 | 0.12485
5905 | 0 | 0.12485
5906 | 0 | 0.12485
5907 | 0 | 0.12485
5908 | 0 | 0.12485
5909 | 0 | 0.12485
5910 | 9.9559 | 10.0807
5911 | 1.1103 | 1.2352
5912 | 1.4437 | 1.5686
5913 | 0 | 0.12485
5914 | 0 | 0.12485
5915 | 0 | 0.12485
5916 | 0.70124 | 0.82609
5917 | 0 | 0.12485
5918 | 0 | 0.12485
5919 | 0 | 0.12485
5920 | 0 | 0.12485
5921 | 0 | 0.12485
5922 | 5.0243 | 5.1492
5923 | 9.9035 | 10.0283
5924 | 0 | 0.12485
5925 | 1.1036 | 1.2284
5926 | 0 | 0.12485
5927 | 0 | 0.12485
5928 | 0 | 0.12485
5929 | 0 | 0.12485
5930 | 0 | 0.12485
5931 | 0 | 0.12485
5932 | 0 | 0.12485
5933 | 0 | 0.12485
5934 | 9.9621 | 10.0869
5935 | 1.111 | 1.2358
5936 | 1.4446 | 1.5695
5937 | 0 | 0.12485
5938 | 0 | 0.12485
5939 | 0 | 0.12485
5940 | 0.70168 | 0.82653
5941 | 0 | 0.12485
5942 | 0 | 0.12485
5943 | 0 | 0.12485
5944 | 0 | 0.12485
5945 | 0 | 0.12485
5946 | 5.0275 | 5.1524
5947 | 9.9092 | 10.0341
5948 | 0 | 0.12485
5949 | 1.1042 | 1.2291
5950 | 0 | 0.12485
5951 | 0 | 0.12485
5952 | 0 | 0.12485
5953 | 0 | 0.12485
5954 | 0 | 0.12485
5955 | 0 | 0.12485
5956 | 0 | 0.12485
5957 | 0 | 0.12485
5958 | 9.9685 | 10.0934
5959 | 1.1117 | 1.2366
5960 | 1.4456 | 1.5704
5961 | 0 | 0.12485
5962 | 0 | 0.12485
5963 | 0 | 0.12485
5964 | 0.70215 | 0.827
5965 | 0 | 0.12485
5966 | 0 | 0.12485
5967 | 0 | 0.12485
5968 | 0 | 0.12485
5969 | 0 | 0.12485
5970 | 5.0309 | 5.1558
5971 | 9.9152 | 10.04
5972 | 0 | 0.12485
5973 | 1.1049 | 1.2298
5974 | 0 | 0.12485
5975 | 0 | 0.12485
5976 | 0 | 0.12485
5977 | 0 | 0.12485
5978 | 0 | 0.12485
5979 | 0 | 0.12485
5980 | 0 | 0.12485
5981 | 0 | 0.12485
5982 | 9.9753 | 10.1001
5983 | 1.1125 | 1.2373
5984 | 1.4466 | 1.5714
5985 | 0 | 0.12485
5986 | 0 | 0.12485
5987 | 0 | 0.12485
5988 | 0.70264 | 0.82749
5989 | 0 | 0.12485
5990 | 0 | 0.12485
5991 | 0 | 0.12485
5992 | 0 | 0.12485
5993 | 0 | 0.12485
5994 | 5.0344 | 5.1593
5995 | 9.9214 | 10.0463
5996 | 0 | 0.12485
5997 | 1.1057 | 1.2305
5998 | 0 | 0.12485
5999 | 0 | 0.12485
6000 | 0 | 0.12485
6001 | 0 | 0.12485
6002 | 0 | 0.12485
6003 | 0 | 0.12485
6004 | 0 | 0.12485
6005 | 0 | 0.12485
6006 | 9.9823 | 10.1071
6007 | 1.1133 | 1.2381
6008 | 1.4476 | 1.5725
6009 | 0 | 0.12485
6010 | 0 | 0.12485
6011 | 0 | 0.12485
6012 | 0.70315 | 0.828
6013 | 0 | 0.12485
6014 | 0 | 0.12485
6015 | 0 | 0.12485
6016 | 0 | 0.12485
6017 | 0 | 0.12485
6018 | 5.0381 | 5.1629
6019 | 9.9279 | 10.0528
6020 | 0 | 0.12485
6021 | 1.1064 | 1.2313
6022 | 0 | 0.12485
6023 | 0 | 0.12485
6024 | 0 | 0.12485
6025 | 0 | 0.12485
6026 | 0 | 0.12485
6027 | 0 | 0.12485
6028 | 0 | 0.12485
6029 | 0 | 0.12485
6030 | 9.9896 | 10.1144
6031 | 1.1141 | 1.2389
6032 | 1.4487 | 1.5735
6033 | 0 | 0.12485
6034 | 0 | 0.12485
6035 | 0 | 0.12485
6036 | 0.70368 | 0.82852
6037 | 0 | 0.12485
6038 | 0 | 0.12485
6039 | 0 | 0.12485
6040 | 0 | 0.12485
6041 | 0 | 0.12485
6042 | 5.0419 | 5.1667
6043 | 9.9347 | 10.0595
6044 | 0 | 0.12485
6045 | 1.1072 | 1.2321
6046 | 0 | 0.12485
6047 | 0 | 0.12485
6048 | 0 | 0.12485
6049 | 0 | 0.12485
6050 | 0 | 0.12485
6051 | 0 | 0.12485
6052 | 0 | 0.12485
6053 | 0 | 0.12485
6054 | 9.9972 | 10.122
6055 | 1.115 | 1.2398
6056 | 1.4498 | 1.5747
6057 | 0 | 0.12485
6058 | 0 | 0.12485
6059 | 0 | 0.12485
6060 | 0.70422 | 0.82907
6061 | 0 | 0.12485
6062 | 0 | 0.12485
6063 | 0 | 0.12485
6064 | 0 | 0.12485
6065 | 0 | 0.12485
6066 | 5.0458 | 5.1706
6067 | 9.9417 | 10.0665
6068 | 0 | 0.12485
6069 | 1.108 | 1.2329
6070 | 0 | 0.12485
6071 | 0 | 0.12485
6072 | 0 | 0.12485
6073 | 0 | 0.12485
6074 | 0 | 0.12485
6075 | 0 | 0.12485
6076 | 0 | 0.12485
6077 | 0 | 0.12485
6078 | 10.005 | 10.1298
6079 | 1.1158 | 1.2407
6080 | 1.451 | 1.5758
6081 | 0 | 0.12485
6082 | 0 | 0.12485
6083 | 0 | 0.12485
6084 | 0.70479 | 0.82964
6085 | 0 | 0.12485
6086 | 0 | 0.12485
6087 | 0 | 0.12485
6088 | 0 | 0.12485
6089 | 0 | 0.12485
6090 | 5.0499 | 5.1747
6091 | 9.949 | 10.0738
6092 | 0 | 0.12485
6093 | 1.1089 | 1.2337
6094 | 0 | 0.12485
6095 | 0 | 0.12485
6096 | 0 | 0.12485
6097 | 0 | 0.12485
6098 | 0 | 0.12485
6099 | 0 | 0.12485
6100 | 0 | 0.12485
6101 | 0 | 0.12485
6102 | 10.0131 | 10.1379
6103 | 1.1168 | 1.2416
6104 | 1.4522 | 1.577
6105 | 0 | 0.12485
6106 | 0 | 0.12485
6107 | 0 | 0.12485
6108 | 0.70538 | 0.83023
6109 | 0 | 0.12485
6110 | 0 | 0.12485
6111 | 0 | 0.12485
6112 | 0 | 0.12485
6113 | 0 | 0.12485
6114 | 5.0541 | 5.179
6115 | 9.9565 | 10.0813
6116 | 0 | 0.12485
6117 | 1.1097 | 1.2346
6118 | 0 | 0.12485
6119 | 0 | 0.12485
6120 | 0 | 0.12485
6121 | 0 | 0.12485
6122 | 0 | 0.12485
6123 | 0 | 0.12485
6124 | 0 | 0.12485
6125 | 0 | 0.12485
6126 | 10.0215 | 10.1463
6127 | 1.1177 | 1.2426
6128 | 1.4534 | 1.5782
6129 | 0 | 0.12485
6130 | 0 | 0.12485
6131 | 0 | 0.12485
6132 | 0.70599 | 0.83084
6133 | 0 | 0.12485
6134 | 0 | 0.12485
6135 | 0 | 0.12485
6136 | 0 | 0.12485
6137 | 0 | 0.12485
6138 | 5.0585 | 5.1833
6139 | 9.9643 | 10.0891
6140 | 0 | 0.12485
6141 | 1.1106 | 1.2355
6142 | 0 | 0.12485
6143 | 0 | 0.12485
6144 | 0 | 0.12485
6145 | 0 | 0.12485
6146 | 0 | 0.12485
6147 | 0 | 0.12485
6148 | 0 | 0.12485
6149 | 0 | 0.12485
6150 | 10.0301 | 10.1549
6151 | 1.1187 | 1.2435
6152 | 1.4547 | 1.5795
6153 | 0 | 0.12485
6154 | 0 | 0.12485
6155 | 0 | 0.12485
6156 | 0.70661 | 0.83146
6157 | 0 | 0.12485
6158 | 0 | 0.12485
6159 | 0 | 0.12485
6160 | 0 | 0.12485
6161 | 0 | 0.12485
6162 | 5.063 | 5.1878
6163 | 9.9723 | 10.0971
6164 | 0 | 0.12485
6165 | 1.1116 | 1.2364
6166 | 0 | 0.12485
6167 | 0 | 0.12485
6168 | 0 | 0.12485
6169 | 0 | 0.12485
6170 | 0 | 0.12485
6171 | 0 | 0.12485
6172 | 0 | 0.12485
6173 | 0 | 0.12485
6174 | 10.039 | 10.1638
6175 | 1.1197 | 1.2445
6176 | 1.456 | 1.5808
6177 | 0 | 0.12485
6178 | 0 | 0.12485
6179 | 0 | 0.12485
6180 | 0.70726 | 0.83211
6181 | 0 | 0.12485
6182 | 0 | 0.12485
6183 | 0 | 0.12485
6184 | 0 | 0.12485
6185 | 0 | 0.12485
6186 | 5.0676 | 5.1925
6187 | 9.9806 | 10.1054
6188 | 0 | 0.12485
6189 | 1.1125 | 1.2374
6190 | 0 | 0.12485
6191 | 0 | 0.12485
6192 | 0 | 0.12485
6193 | 0 | 0.12485
6194 | 0 | 0.12485
6195 | 0 | 0.12485
6196 | 0 | 0.12485
6197 | 0 | 0.12485
6198 | 10.0481 | 10.173
6199 | 1.1207 | 1.2456
6200 | 1.4573 | 1.5822
6201 | 0 | 0.12485
6202 | 0 | 0.12485
6203 | 0 | 0.12485
6204 | 0.70793 | 0.83277
6205 | 0 | 0.12485
6206 | 0 | 0.12485
6207 | 0 | 0.12485
6208 | 0 | 0.12485
6209 | 0 | 0.12485
6210 | 5.0724 | 5.1972
6211 | 9.9891 | 10.1139
6212 | 0 | 0.12485
6213 | 1.1135 | 1.2384
6214 | 0 | 0.12485
6215 | 0 | 0.12485
6216 | 0 | 0.12485
6217 | 0 | 0.12485
6218 | 0 | 0.12485
6219 | 0 | 0.12485
6220 | 0 | 0.12485
6221 | 0 | 0.12485
6222 | 10.0575 | 10.1824
6223 | 1.1218 | 1.2466
6224 | 1.4587 | 1.5836
6225 | 0 | 0.12485
6226 | 0 | 0.12485
6227 | 0 | 0.12485
6228 | 0.70861 | 0.83346
6229 | 0 | 0.12485
6230 | 0 | 0.12485
6231 | 0 | 0.12485
6232 | 0 | 0.12485
6233 | 0 | 0.12485
6234 | 5.0773 | 5.2022
6235 | 9.9978 | 10.1227
6236 | 0 | 0.12485
6237 | 1.1145 | 1.2394
6238 | 0 | 0.12485
6239 | 0 | 0.12485
6240 | 0 | 0.12485
6241 | 0 | 0.12485
6242 | 0 | 0.12485
6243 | 0 | 0.12485
6244 | 0 | 0.12485
6245 | 0 | 0.12485
6246 | 10.0672 | 10.1921
6247 | 1.1229 | 1.2477
6248 | 1.4601 | 1.585
6249 | 0 | 0.12485
6250 | 0 | 0.12485
6251 | 0 | 0.12485
6252 | 0.70931 | 0.83416
6253 | 0 | 0.12485
6254 | 0 | 0.12485
6255 | 0 | 0.12485
6256 | 0 | 0.12485
6257 | 0 | 0.12485
6258 | 5.0824 | 5.2072
6259 | 10.0068 | 10.1317
6260 | 0 | 0.12485
6261 | 1.1156 | 1.2404
6262 | 0 | 0.12485
6263 | 0 | 0.12485
6264 | 0 | 0.12485
6265 | 0 | 0.12485
6266 | 0 | 0.12485
6267 | 0 | 0.12485
6268 | 0 | 0.12485
6269 | 0 | 0.12485
6270 | 10.0771 | 10.202
6271 | 1.124 | 1.2488
6272 | 1.4616 | 1.5865
6273 | 0 | 0.12485
6274 | 0 | 0.12485
6275 | 0 | 0.12485
6276 | 0.71003 | 0.83488
6277 | 0 | 0.12485
6278 | 0 | 0.12485
6279 | 0 | 0.12485
6280 | 0 | 0.12485
6281 | 0 | 0.12485
6282 | 5.0875 | 5.2124
6283 | 10.016 | 10.1409
6284 | 0 | 0.12485
6285 | 1.1166 | 1.2415
6286 | 0 | 0.12485
6287 | 0 | 0.12485
6288 | 0 | 0.12485
6289 | 0 | 0.12485
6290 | 0 | 0.12485
6291 | 0 | 0.12485
6292 | 0 | 0.12485
6293 | 0 | 0.12485
6294 | 10.0873 | 10.2121
6295 | 1.1252 | 1.25
6296 | 1.4631 | 1.588
6297 | 0 | 0.12485
6298 | 0 | 0.12485
6299 | 0 | 0.12485
6300 | 0.71077 | 0.83562
6301 | 0 | 0.12485
6302 | 0 | 0.12485
6303 | 0 | 0.12485
6304 | 0 | 0.12485
6305 | 0 | 0.12485
6306 | 5.0928 | 5.2177
6307 | 10.0255 | 10.1503
6308 | 0 | 0.12485
6309 | 1.1177 | 1.2426
6310 | 0 | 0.12485
6311 | 0 | 0.12485
6312 | 0 | 0.12485
6313 | 0 | 0.12485
6314 | 0 | 0.12485
6315 | 0 | 0.12485
6316 | 0 | 0.12485
6317 | 0 | 0.12485
6318 | 10.0977 | 10.2225
6319 | 1.1263 | 1.2512
6320 | 1.4646 | 1.5895
6321 | 0 | 0.12485
6322 | 0 | 0.12485
6323 | 0 | 0.12485
6324 | 0.71153 | 0.83638
6325 | 0 | 0.12485
6326 | 0 | 0.12485
6327 | 0 | 0.12485
6328 | 0 | 0.12485
6329 | 0 | 0.12485
6330 | 5.0983 | 5.2231
6331 | 10.0352 | 10.16
6332 | 0 | 0.12485
6333 | 1.1189 | 1.2437
6334 | 0 | 0.12485
6335 | 0 | 0.12485
6336 | 0 | 0.12485
6337 | 0 | 0.12485
6338 | 0 | 0.12485
6339 | 0 | 0.12485
6340 | 0 | 0.12485
6341 | 0 | 0.12485
6342 | 10.1083 | 10.2332
6343 | 1.1275 | 1.2524
6344 | 1.4662 | 1.5911
6345 | 0 | 0.12485
6346 | 0 | 0.12485
6347 | 0 | 0.12485
6348 | 0.7123 | 0.83715
6349 | 0 | 0.12485
6350 | 0 | 0.12485
6351 | 0 | 0.12485
6352 | 0 | 0.12485
6353 | 0 | 0.12485
6354 | 5.1038 | 5.2287
6355 | 10.0451 | 10.1699
6356 | 0 | 0.12485
6357 | 1.12 | 1.2449
6358 | 0 | 0.12485
6359 | 0 | 0.12485
6360 | 0 | 0.12485
6361 | 0 | 0.12485
6362 | 0 | 0.12485
6363 | 0 | 0.12485
6364 | 0 | 0.12485
6365 | 0 | 0.12485
6366 | 10.1192 | 10.244
6367 | 1.1288 | 1.2536
6368 | 1.4678 | 1.5927
6369 | 0 | 0.12485
6370 | 0 | 0.12485
6371 | 0 | 0.12485
6372 | 0.7131 | 0.83794
6373 | 0 | 0.12485
6374 | 0 | 0.12485
6375 | 0 | 0.12485
6376 | 0 | 0.12485
6377 | 0 | 0.12485
6378 | 5.1095 | 5.2344
6379 | 10.0552 | 10.1801
6380 | 0 | 0.12485
6381 | 1.1212 | 1.246
6382 | 0 | 0.12485
6383 | 0 | 0.12485
6384 | 0 | 0.12485
6385 | 0 | 0.12485
6386 | 0 | 0.12485
6387 | 0 | 0.12485
6388 | 0 | 0.12485
6389 | 0 | 0.12485
6390 | 10.1303 | 10.2552
6391 | 1.13 | 1.2549
6392 | 1.4695 | 1.5943
6393 | 0 | 0.12485
6394 | 0 | 0.12485
6395 | 0 | 0.12485
6396 | 0.7139 | 0.83875
6397 | 0 | 0.12485
6398 | 0 | 0.12485
6399 | 0 | 0.12485
6400 | 0 | 0.12485
6401 | 0 | 0.12485
6402 | 5.1154 | 5.2402
6403 | 10.0656 | 10.1904
6404 | 0 | 0.12485
6405 | 1.1224 | 1.2473
6406 | 0 | 0.12485
6407 | 0 | 0.12485
6408 | 0 | 0.12485
6409 | 0 | 0.12485
6410 | 0 | 0.12485
6411 | 0 | 0.12485
6412 | 0 | 0.12485
6413 | 0 | 0.12485
6414 | 10.1417 | 10.2665
6415 | 1.1313 | 1.2562
6416 | 1.4711 | 1.596
6417 | 0 | 0.12485
6418 | 0 | 0.12485
6419 | 0 | 0.12485
6420 | 0.71473 | 0.83958
6421 | 0 | 0.12485
6422 | 0 | 0.12485
6423 | 0 | 0.12485
6424 | 0 | 0.12485
6425 | 0 | 0.12485
6426 | 5.1213 | 5.2461
6427 | 10.0761 | 10.201
6428 | 0 | 0.12485
6429 | 1.1236 | 1.2485
6430 | 0 | 0.12485
6431 | 0 | 0.12485
6432 | 0 | 0.12485
6433 | 0 | 0.12485
6434 | 0 | 0.12485
6435 | 0 | 0.12485
6436 | 0 | 0.12485
6437 | 0 | 0.12485
6438 | 10.1532 | 10.2781
6439 | 1.1326 | 1.2575
6440 | 1.4729 | 1.5977
6441 | 0 | 0.12485
6442 | 0 | 0.12485
6443 | 0 | 0.12485
6444 | 0.71557 | 0.84042
6445 | 0 | 0.12485
6446 | 0 | 0.12485
6447 | 0 | 0.12485
6448 | 0 | 0.12485
6449 | 0 | 0.12485
6450 | 5.1273 | 5.2522
6451 | 10.0869 | 10.2118
6452 | 0 | 0.12485
6453 | 1.1249 | 1.2497
6454 | 0 | 0.12485
6455 | 0 | 0.12485
6456 | 0 | 0.12485
6457 | 0 | 0.12485
6458 | 0 | 0.12485
6459 | 0 | 0.12485
6460 | 0 | 0.12485
6461 | 0 | 0.12485
6462 | 10.165 | 10.2899
6463 | 1.134 | 1.2588
6464 | 1.4746 | 1.5995
6465 | 0 | 0.12485
6466 | 0 | 0.12485
6467 | 0 | 0.12485
6468 | 0.71643 | 0.84128
6469 | 0 | 0.12485
6470 | 0 | 0.12485
6471 | 0 | 0.12485
6472 | 0 | 0.12485
6473 | 0 | 0.12485
6474 | 5.1335 | 5.2584
6475 | 10.0979 | 10.2228
6476 | 0 | 0.12485
6477 | 1.1262 | 1.251
6478 | 0 | 0.12485
6479 | 0 | 0.12485
6480 | 0 | 0.12485
6481 | 0 | 0.12485
6482 | 0 | 0.12485
6483 | 0 | 0.12485
6484 | 0 | 0.12485
6485 | 0 | 0.12485
6486 | 10.1771 | 10.3019
6487 | 1.1353 | 1.2602
6488 | 1.4764 | 1.6012
6489 | 0 | 0.12485
6490 | 0 | 0.12485
6491 | 0 | 0.12485
6492 | 0.71731 | 0.84216
6493 | 0 | 0.12485
6494 | 0 | 0.12485
6495 | 0 | 0.12485
6496 | 0 | 0.12485
6497 | 0 | 0.12485
6498 | 5.1398 | 5.2647
6499 | 10.1091 | 10.234
6500 | 0 | 0.12485
6501 | 1.1275 | 1.2523
6502 | 0 | 0.12485
6503 | 0 | 0.12485
6504 | 0 | 0.12485
6505 | 0 | 0.12485
6506 | 0 | 0.12485
6507 | 0 | 0.12485
6508 | 0 | 0.12485
6509 | 0 | 0.12485
6510 | 10.1893 | 10.3141
6511 | 1.1367 | 1.2616
6512 | 1.4782 | 1.603
6513 | 0 | 0.12485
6514 | 0 | 0.12485
6515 | 0 | 0.12485
6516 | 0.7182 | 0.84305
6517 | 0 | 0.12485
6518 | 0 | 0.12485
6519 | 0 | 0.12485
6520 | 0 | 0.12485
6521 | 0 | 0.12485
6522 | 5.1462 | 5.2711
6523 | 10.1206 | 10.2454
6524 | 0 | 0.12485
6525 | 1.1288 | 1.2536
6526 | 0 | 0.12485
6527 | 0 | 0.12485
6528 | 0 | 0.12485
6529 | 0 | 0.12485
6530 | 0 | 0.12485
6531 | 0 | 0.12485
6532 | 0 | 0.12485
6533 | 0 | 0.12485
6534 | 10.2017 | 10.3266
6535 | 1.1381 | 1.263
6536 | 1.48 | 1.6049
6537 | 0 | 0.12485
6538 | 0 | 0.12485
6539 | 0 | 0.12485
6540 | 0.71911 | 0.84396
6541 | 0 | 0.12485
6542 | 0 | 0.12485
6543 | 0 | 0.12485
6544 | 0 | 0.12485
6545 | 0 | 0.12485
6546 | 5.1527 | 5.2776
6547 | 10.1322 | 10.257
6548 | 0 | 0.12485
6549 | 1.1301 | 1.255
6550 | 0 | 0.12485
6551 | 0 | 0.12485
6552 | 0 | 0.12485
6553 | 0 | 0.12485
6554 | 0 | 0.12485
6555 | 0 | 0.12485
6556 | 0 | 0.12485
6557 | 0 | 0.12485
6558 | 10.2144 | 10.3392
6559 | 1.1396 | 1.2644
6560 | 1.4819 | 1.6068
6561 | 0 | 0.12485
6562 | 0 | 0.12485
6563 | 0 | 0.12485
6564 | 0.72003 | 0.84488
6565 | 0 | 0.12485
6566 | 0 | 0.12485
6567 | 0 | 0.12485
6568 | 0 | 0.12485
6569 | 0 | 0.12485
6570 | 5.1594 | 5.2842
6571 | 10.144 | 10.2688
6572 | 0 | 0.12485
6573 | 1.1315 | 1.2564
6574 | 0 | 0.12485
6575 | 0 | 0.12485
6576 | 0 | 0.12485
6577 | 0 | 0.12485
6578 | 0 | 0.12485
6579 | 0 | 0.12485
6580 | 0 | 0.12485
6581 | 0 | 0.12485
6582 | 10.2273 | 10.3521
6583 | 1.141 | 1.2659
6584 | 1.4838 | 1.6087
6585 | 0 | 0.12485
6586 | 0 | 0.12485
6587 | 0 | 0.12485
6588 | 0.72097 | 0.84582
6589 | 0 | 0.12485
6590 | 0 | 0.12485
6591 | 0 | 0.12485
6592 | 0 | 0.12485
6593 | 0 | 0.12485
6594 | 5.1661 | 5.291
6595 | 10.156 | 10.2808
6596 | 0 | 0.12485
6597 | 1.1329 | 1.2578
6598 | 0 | 0.12485
6599 | 0 | 0.12485
6600 | 0 | 0.12485
6601 | 0 | 0.12485
6602 | 0 | 0.12485
6603 | 0 | 0.12485
6604 | 0 | 0.12485
6605 | 0 | 0.12485
6606 | 10.2403 | 10.3652
6607 | 1.1425 | 1.2674
6608 | 1.4858 | 1.6106
6609 | 0 | 0.12485
6610 | 0 | 0.12485
6611 | 0 | 0.12485
6612 | 0.72192 | 0.84677
6613 | 0 | 0.12485
6614 | 0 | 0.12485
6615 | 0 | 0.12485
6616 | 0 | 0.12485
6617 | 0 | 0.12485
6618 | 5.173 | 5.2978
6619 | 10.1682 | 10.293
6620 | 0 | 0.12485
6621 | 1.1343 | 1.2592
6622 | 0 | 0.12485
6623 | 0 | 0.12485
6624 | 0 | 0.12485
6625 | 0 | 0.12485
6626 | 0 | 0.12485
6627 | 0 | 0.12485
6628 | 0 | 0.12485
6629 | 0 | 0.12485
6630 | 10.2536 | 10.3785
6631 | 1.144 | 1.2689
6632 | 1.4877 | 1.6126
6633 | 0 | 0.12485
6634 | 0 | 0.12485
6635 | 0 | 0.12485
6636 | 0.72289 | 0.84774
6637 | 0 | 0.12485
6638 | 0 | 0.12485
6639 | 0 | 0.12485
6640 | 0 | 0.12485
6641 | 0 | 0.12485
6642 | 5.1799 | 5.3048
6643 | 10.1806 | 10.3054
6644 | 0 | 0.12485
6645 | 1.1358 | 1.2606
6646 | 0 | 0.12485
6647 | 0 | 0.12485
6648 | 0 | 0.12485
6649 | 0 | 0.12485
6650 | 0 | 0.12485
6651 | 0 | 0.12485
6652 | 0 | 0.12485
6653 | 0 | 0.12485
6654 | 10.2671 | 10.3919
6655 | 1.1455 | 1.2704
6656 | 1.4897 | 1.6146
6657 | 0 | 0.12485
6658 | 0 | 0.12485
6659 | 0 | 0.12485
6660 | 0.72387 | 0.84872
6661 | 0 | 0.12485
6662 | 0 | 0.12485
6663 | 0 | 0.12485
6664 | 0 | 0.12485
6665 | 0 | 0.12485
6666 | 5.187 | 5.3118
6667 | 10.1932 | 10.318
6668 | 0 | 0.12485
6669 | 1.1372 | 1.2621
6670 | 0 | 0.12485
6671 | 0 | 0.12485
6672 | 0 | 0.12485
6673 | 0 | 0.12485
6674 | 0 | 0.12485
6675 | 0 | 0.12485
6676 | 0 | 0.12485
6677 | 0 | 0.12485
6678 | 10.2807 | 10.4056
6679 | 1.1471 | 1.2719
6680 | 1.4917 | 1.6166
6681 | 0 | 0.12485
6682 | 0 | 0.12485
6683 | 0 | 0.12485
6684 | 0.72487 | 0.84971
6685 | 0 | 0.12485
6686 | 0 | 0.12485
6687 | 0 | 0.12485
6688 | 0 | 0.12485
6689 | 0 | 0.12485
6690 | 5.1941 | 5.319
6691 | 10.2059 | 10.3308
6692 | 0 | 0.12485
6693 | 1.1387 | 1.2636
6694 | 0 | 0.12485
6695 | 0 | 0.12485
6696 | 0 | 0.12485
6697 | 0 | 0.12485
6698 | 0 | 0.12485
6699 | 0 | 0.12485
6700 | 0 | 0.12485
6701 | 0 | 0.12485
6702 | 10.2946 | 10.4194
6703 | 1.1487 | 1.2735
6704 | 1.4938 | 1.6186
6705 | 0 | 0.12485
6706 | 0 | 0.12485
6707 | 0 | 0.12485
6708 | 0.72588 | 0.85072
6709 | 0 | 0.12485
6710 | 0 | 0.12485
6711 | 0 | 0.12485
6712 | 0 | 0.12485
6713 | 0 | 0.12485
6714 | 5.2014 | 5.3262
6715 | 10.6173 | 10.7421
6716 | 0 | 0.12485
6717 | 1.1338 | 1.2586
6718 | 0 | 0.12485
6719 | 0 | 0.12485
6720 | 0 | 0.12485
6721 | 0 | 0.12485
6722 | 0 | 0.12485
6723 | 0 | 0.12485
6724 | 0 | 0.12485
6725 | 0 | 0.12485
6726 | 10.2523 | 10.3771
6727 | 1.1469 | 1.2718
6728 | 1.4915 | 1.6164
6729 | 0 | 0.12485
6730 | 0 | 0.12485
6731 | 0 | 0.12485
6732 | 0.7248 | 0.84964
6733 | 0 | 0.12485
6734 | 0 | 0.12485
6735 | 0 | 0.12485
6736 | 0 | 0.12485
6737 | 0 | 0.12485
6738 | 5.4013 | 5.5261
6739 | 10.5435 | 10.6684
6740 | 0 | 0.12485
6741 | 1.1311 | 1.256
6742 | 0 | 0.12485
6743 | 0 | 0.12485
6744 | 0 | 0.12485
6745 | 0 | 0.12485
6746 | 0 | 0.12485
6747 | 0 | 0.12485
6748 | 0 | 0.12485
6749 | 0 | 0.12485
6750 | 10.6368 | 10.7616
6751 | 1.1399 | 1.2647
6752 | 1.4824 | 1.6072
6753 | 0 | 0.12485
6754 | 0 | 0.12485
6755 | 0 | 0.12485
6756 | 0.72036 | 0.84521
6757 | 0 | 0.12485
6758 | 0 | 0.12485
6759 | 0 | 0.12485
6760 | 0 | 0.12485
6761 | 0 | 0.12485
6762 | 5.3748 | 5.4996
6763 | 10.7048 | 10.8296
6764 | 0 | 0.12485
6765 | 1.1148 | 1.2397
6766 | 0 | 0.12485
6767 | 0 | 0.12485
6768 | 0 | 0.12485
6769 | 0 | 0.12485
6770 | 0 | 0.12485
6771 | 0 | 0.12485
6772 | 0 | 0.12485
6773 | 0 | 0.12485
6774 | 10.7056 | 10.8305
6775 | 1.1187 | 1.2435
6776 | 1.4548 | 1.5797
6777 | 0 | 0.12485
6778 | 0 | 0.12485
6779 | 0 | 0.12485
6780 | 0.70704 | 0.83188
6781 | 0 | 0.12485
6782 | 0 | 0.12485
6783 | 0 | 0.12485
6784 | 0 | 0.12485
6785 | 0 | 0.12485
6786 | 5.2878 | 5.4126
6787 | 10.5735 | 10.6984
6788 | 0 | 0.12485
6789 | 1.1071 | 1.232
6790 | 0 | 0.12485
6791 | 0 | 0.12485
6792 | 0 | 0.12485
6793 | 0 | 0.12485
6794 | 0 | 0.12485
6795 | 0 | 0.12485
6796 | 0 | 0.12485
6797 | 0 | 0.12485
6798 | 10.645 | 10.7698
6799 | 1.1156 | 1.2404
6800 | 1.4508 | 1.5756
6801 | 0 | 0.12485
6802 | 0 | 0.12485
6803 | 0 | 0.12485
6804 | 0.7051 | 0.82995
6805 | 0 | 0.12485
6806 | 0 | 0.12485
6807 | 0 | 0.12485
6808 | 0 | 0.12485
6809 | 0 | 0.12485
6810 | 5.5266 | 5.6514
6811 | 10.4239 | 10.5488
6812 | 0 | 0.12485
6813 | 1.0973 | 1.2221
6814 | 0 | 0.12485
6815 | 0 | 0.12485
6816 | 0 | 0.12485
6817 | 0 | 0.12485
6818 | 0 | 0.12485
6819 | 0 | 0.12485
6820 | 0 | 0.12485
6821 | 0 | 0.12485
6822 | 10.566 | 10.6909
6823 | 1.1112 | 1.2361
6824 | 1.4452 | 1.57
6825 | 0 | 0.12485
6826 | 0 | 0.12485
6827 | 0 | 0.12485
6828 | 0.70239 | 0.82724
6829 | 0 | 0.12485
6830 | 0 | 0.12485
6831 | 0 | 0.12485
6832 | 0 | 0.12485
6833 | 0 | 0.12485
6834 | 5.5044 | 5.6292
6835 | 10.3885 | 10.5133
6836 | 0 | 0.12485
6837 | 1.0944 | 1.2192
6838 | 0 | 0.12485
6839 | 0 | 0.12485
6840 | 0 | 0.12485
6841 | 0 | 0.12485
6842 | 0 | 0.12485
6843 | 0 | 0.12485
6844 | 0 | 0.12485
6845 | 0 | 0.12485
6846 | 10.5413 | 10.6661
6847 | 1.1092 | 1.2341
6848 | 1.4426 | 1.5674
6849 | 0 | 0.12485
6850 | 0 | 0.12485
6851 | 0 | 0.12485
6852 | 0.70116 | 0.82601
6853 | 0 | 0.12485
6854 | 0 | 0.12485
6855 | 0 | 0.12485
6856 | 0 | 0.12485
6857 | 0 | 0.12485
6858 | 5.4927 | 5.6176
6859 | 10.7443 | 10.8691
6860 | 0 | 0.12485
6861 | 1.0863 | 1.2112
6862 | 0 | 0.12485
6863 | 0 | 0.12485
6864 | 0 | 0.12485
6865 | 0 | 0.12485
6866 | 0 | 0.12485
6867 | 0 | 0.12485
6868 | 0 | 0.12485
6869 | 0 | 0.12485
6870 | 10.4709 | 10.5957
6871 | 1.1028 | 1.2276
6872 | 1.4343 | 1.5591
6873 | 0 | 0.12485
6874 | 0 | 0.12485
6875 | 0 | 0.12485
6876 | 0.69713 | 0.82198
6877 | 0 | 0.12485
6878 | 0 | 0.12485
6879 | 0 | 0.12485
6880 | 0 | 0.12485
6881 | 0 | 0.12485
6882 | 5.4759 | 5.6007
6883 | 10.8221 | 10.9469
6884 | 0 | 0.12485
6885 | 1.181 | 1.3058
6886 | 0 | 0.12485
6887 | 0 | 0.12485
6888 | 0 | 0.12485
6889 | 0 | 0.12485
6890 | 0 | 0.12485
6891 | 0 | 0.12485
6892 | 0 | 0.12485
6893 | 0 | 0.12485
6894 | 10.6705 | 10.7953
6895 | 1.1771 | 1.302
6896 | 1.5308 | 1.6557
6897 | 0 | 0.12485
6898 | 0 | 0.12485
6899 | 0 | 0.12485
6900 | 0.74396 | 0.86881
6901 | 0 | 0.12485
6902 | 0 | 0.12485
6903 | 0 | 0.12485
6904 | 0 | 0.12485
6905 | 0 | 0.12485
6906 | 5.329 | 5.4538
6907 | 10.4396 | 10.5644
6908 | 0 | 0.12485
6909 | 1.1597 | 1.2846
6910 | 0 | 0.12485
6911 | 0 | 0.12485
6912 | 0 | 0.12485
6913 | 0 | 0.12485
6914 | 0 | 0.12485
6915 | 0 | 0.12485
6916 | 0 | 0.12485
6917 | 0 | 0.12485
6918 | 10.486 | 10.6109
6919 | 1.1672 | 1.292
6920 | 1.5179 | 1.6428
6921 | 0 | 0.12485
6922 | 0 | 0.12485
6923 | 0 | 0.12485
6924 | 0.73772 | 0.86256
6925 | 0 | 0.12485
6926 | 0 | 0.12485
6927 | 0 | 0.12485
6928 | 0 | 0.12485
6929 | 0 | 0.12485
6930 | 5.4931 | 5.618
6931 | 10.7039 | 10.8288
6932 | 0 | 0.12485
6933 | 1.1464 | 1.2712
6934 | 0 | 0.12485
6935 | 0 | 0.12485
6936 | 0 | 0.12485
6937 | 0 | 0.12485
6938 | 0 | 0.12485
6939 | 0 | 0.12485
6940 | 0 | 0.12485
6941 | 0 | 0.12485
6942 | 10.7773 | 10.9021
6943 | 1.1546 | 1.2794
6944 | 1.5016 | 1.6264
6945 | 0 | 0.12485
6946 | 0 | 0.12485
6947 | 0 | 0.12485
6948 | 0.72981 | 0.85466
6949 | 0 | 0.12485
6950 | 0 | 0.12485
6951 | 0 | 0.12485
6952 | 0 | 0.12485
6953 | 0 | 0.12485
6954 | 5.4429 | 5.5678
6955 | 10.8292 | 10.9541
6956 | 0 | 0.12485
6957 | 1.1281 | 1.253
6958 | 0 | 0.12485
6959 | 0 | 0.12485
6960 | 0 | 0.12485
6961 | 0 | 0.12485
6962 | 0 | 0.12485
6963 | 0 | 0.12485
6964 | 0 | 0.12485
6965 | 0 | 0.12485
6966 | 10.8342 | 10.9591
6967 | 1.1323 | 1.2572
6968 | 1.4727 | 1.5975
6969 | 0 | 0.12485
6970 | 0 | 0.12485
6971 | 0 | 0.12485
6972 | 0.71582 | 0.84067
6973 | 0 | 0.12485
6974 | 0 | 0.12485
6975 | 0 | 0.12485
6976 | 0 | 0.12485
6977 | 0 | 0.12485
6978 | 5.6021 | 5.727
6979 | 10.5563 | 10.6811
6980 | 0 | 0.12485
6981 | 1.1094 | 1.2343
6982 | 0 | 0.12485
6983 | 0 | 0.12485
6984 | 0 | 0.12485
6985 | 0 | 0.12485
6986 | 0 | 0.12485
6987 | 0 | 0.12485
6988 | 0 | 0.12485
6989 | 0 | 0.12485
6990 | 10.6789 | 10.8038
6991 | 1.1218 | 1.2466
6992 | 1.4589 | 1.5838
6993 | 0 | 0.12485
6994 | 0 | 0.12485
6995 | 0 | 0.12485
6996 | 0.70919 | 0.83404
6997 | 0 | 0.12485
6998 | 0 | 0.12485
6999 | 0 | 0.12485
7000 | 0 | 0.12485
7001 | 0 | 0.12485
7002 | 5.5523 | 5.6771
7003 | 10.9461 | 11.071
7004 | 0 | 0.12485
7005 | 1.1925 | 1.3174
7006 | 0 | 0.12485
7007 | 0 | 0.12485
7008 | 0 | 0.12485
7009 | 0 | 0.12485
7010 | 0 | 0.12485
7011 | 0 | 0.12485
7012 | 0 | 0.12485
7013 | 0 | 0.12485
7014 | 10.7756 | 10.9004
7015 | 1.1876 | 1.3124
7016 | 1.5445 | 1.6693
7017 | 0 | 0.12485
7018 | 0 | 0.12485
7019 | 0 | 0.12485
7020 | 0.75066 | 0.87551
7021 | 0 | 0.12485
7022 | 0 | 0.12485
7023 | 0 | 0.12485
7024 | 0 | 0.12485
7025 | 0 | 0.12485
7026 | 5.3769 | 5.5017
7027 | 10.5242 | 10.649
7028 | 0 | 0.12485
7029 | 1.1689 | 1.2938
7030 | 0 | 0.12485
7031 | 0 | 0.12485
7032 | 0 | 0.12485
7033 | 0 | 0.12485
7034 | 0 | 0.12485
7035 | 0 | 0.12485
7036 | 0 | 0.12485
7037 | 0 | 0.12485
7038 | 10.5709 | 10.6958
7039 | 1.1765 | 1.3013
7040 | 1.5301 | 1.6549
7041 | 0 | 0.12485
7042 | 0 | 0.12485
7043 | 0 | 0.12485
7044 | 0.74369 | 0.86854
7045 | 0 | 0.12485
7046 | 0 | 0.12485
7047 | 0 | 0.12485
7048 | 0 | 0.12485
7049 | 0 | 0.12485
7050 | 5.5394 | 5.6642
7051 | 10.9915 | 11.1163
7052 | 0 | 0.12485
7053 | 1.1413 | 1.2662
7054 | 0 | 0.12485
7055 | 0 | 0.12485
7056 | 0 | 0.12485
7057 | 0 | 0.12485
7058 | 0 | 0.12485
7059 | 0 | 0.12485
7060 | 0 | 0.12485
7061 | 0 | 0.12485
7062 | 10.9523 | 11.0772
7063 | 1.1427 | 1.2675
7064 | 1.4862 | 1.611
7065 | 0 | 0.12485
7066 | 0 | 0.12485
7067 | 0 | 0.12485
7068 | 0.72244 | 0.84729
7069 | 0 | 0.12485
7070 | 0 | 0.12485
7071 | 0 | 0.12485
7072 | 0 | 0.12485
7073 | 0 | 0.12485
7074 | 5.6494 | 5.7742
7075 | 10.6388 | 10.7637
7076 | 0 | 0.12485
7077 | 1.117 | 1.2418
7078 | 0 | 0.12485
7079 | 0 | 0.12485
7080 | 0 | 0.12485
7081 | 0 | 0.12485
7082 | 0 | 0.12485
7083 | 0 | 0.12485
7084 | 0 | 0.12485
7085 | 0 | 0.12485
7086 | 10.7485 | 10.8733
7087 | 1.1281 | 1.2529
7088 | 1.4672 | 1.5921
7089 | 0 | 0.12485
7090 | 0 | 0.12485
7091 | 0 | 0.12485
7092 | 0.71327 | 0.83812
7093 | 0 | 0.12485
7094 | 0 | 0.12485
7095 | 0 | 0.12485
7096 | 0 | 0.12485
7097 | 0 | 0.12485
7098 | 5.5879 | 5.7127
7099 | 11.0193 | 11.1441
7100 | 0 | 0.12485
7101 | 1.2003 | 1.3252
7102 | 0 | 0.12485
7103 | 0 | 0.12485
7104 | 0 | 0.12485
7105 | 0 | 0.12485
7106 | 0 | 0.12485
7107 | 0 | 0.12485
7108 | 0 | 0.12485
7109 | 0 | 0.12485
7110 | 10.8475 | 10.9724
7111 | 1.1954 | 1.3202
7112 | 1.5546 | 1.6795
7113 | 0 | 0.12485
7114 | 0 | 0.12485
7115 | 0 | 0.12485
7116 | 0.75566 | 0.88051
7117 | 0 | 0.12485
7118 | 0 | 0.12485
7119 | 0 | 0.12485
7120 | 0 | 0.12485
7121 | 0 | 0.12485
7122 | 5.4127 | 5.5376
7123 | 10.9873 | 11.1121
7124 | 0 | 0.12485
7125 | 1.1697 | 1.2945
7126 | 0 | 0.12485
7127 | 0 | 0.12485
7128 | 0 | 0.12485
7129 | 0 | 0.12485
7130 | 0 | 0.12485
7131 | 0 | 0.12485
7132 | 0 | 0.12485
7133 | 0 | 0.12485
7134 | 10.9883 | 11.1131
7135 | 1.174 | 1.2988
7136 | 1.5269 | 1.6517
7137 | 0 | 0.12485
7138 | 0 | 0.12485
7139 | 0 | 0.12485
7140 | 0.74222 | 0.86707
7141 | 0 | 0.12485
7142 | 0 | 0.12485
7143 | 0 | 0.12485
7144 | 0 | 0.12485
7145 | 0 | 0.12485
7146 | 5.5316 | 5.6565
7147 | 10.988 | 11.1128
7148 | 0 | 0.12485
7149 | 1.144 | 1.2689
7150 | 0 | 0.12485
7151 | 0 | 0.12485
7152 | 0 | 0.12485
7153 | 0 | 0.12485
7154 | 0 | 0.12485
7155 | 0 | 0.12485
7156 | 0 | 0.12485
7157 | 0 | 0.12485
7158 | 10.9849 | 11.1098
7159 | 1.1478 | 1.2726
7160 | 1.4928 | 1.6177
7161 | 0 | 0.12485
7162 | 0 | 0.12485
7163 | 0 | 0.12485
7164 | 0.72575 | 0.8506
7165 | 0 | 0.12485
7166 | 0 | 0.12485
7167 | 0 | 0.12485
7168 | 0 | 0.12485
7169 | 0 | 0.12485
7170 | 5.6699 | 5.7948
7171 | 10.6777 | 10.8025
7172 | 0 | 0.12485
7173 | 1.1208 | 1.2456
7174 | 0 | 0.12485
7175 | 0 | 0.12485
7176 | 0 | 0.12485
7177 | 0 | 0.12485
7178 | 0 | 0.12485
7179 | 0 | 0.12485
7180 | 0 | 0.12485
7181 | 0 | 0.12485
7182 | 10.7849 | 10.9098
7183 | 1.1314 | 1.2562
7184 | 1.4716 | 1.5964
7185 | 0 | 0.12485
7186 | 0 | 0.12485
7187 | 0 | 0.12485
7188 | 0.71545 | 0.8403
7189 | 0 | 0.12485
7190 | 0 | 0.12485
7191 | 0 | 0.12485
7192 | 0 | 0.12485
7193 | 0 | 0.12485
7194 | 5.615 | 5.7399
7195 | 11.0843 | 11.2092
7196 | 0 | 0.12485
7197 | 1.2078 | 1.3326
7198 | 0 | 0.12485
7199 | 0 | 0.12485
7200 | 0 | 0.12485
7201 | 0 | 0.12485
7202 | 0 | 0.12485
7203 | 0 | 0.12485
7204 | 0 | 0.12485
7205 | 0 | 0.12485
7206 | 10.9162 | 11.0411
7207 | 1.203 | 1.3279
7208 | 1.5646 | 1.6895
7209 | 0 | 0.12485
7210 | 0 | 0.12485
7211 | 0 | 0.12485
7212 | 0.7606 | 0.88545
7213 | 0 | 0.12485
7214 | 0 | 0.12485
7215 | 0 | 0.12485
7216 | 0 | 0.12485
7217 | 0 | 0.12485
7218 | 5.4482 | 5.5731
7219 | 11.0505 | 11.1754
7220 | 0 | 0.12485
7221 | 1.1764 | 1.3013
7222 | 0 | 0.12485
7223 | 0 | 0.12485
7224 | 0 | 0.12485
7225 | 0 | 0.12485
7226 | 0 | 0.12485
7227 | 0 | 0.12485
7228 | 0 | 0.12485
7229 | 0 | 0.12485
7230 | 11.0511 | 11.1759
7231 | 1.1803 | 1.3051
7232 | 1.5351 | 1.6599
7233 | 0 | 0.12485
7234 | 0 | 0.12485
7235 | 0 | 0.12485
7236 | 0.74627 | 0.87112
7237 | 0 | 0.12485
7238 | 0 | 0.12485
7239 | 0 | 0.12485
7240 | 0 | 0.12485
7241 | 0 | 0.12485
7242 | 5.561 | 5.6859
7243 | 11.0433 | 11.1681
7244 | 0 | 0.12485
7245 | 1.1506 | 1.2754
7246 | 0 | 0.12485
7247 | 0 | 0.12485
7248 | 0 | 0.12485
7249 | 0 | 0.12485
7250 | 0 | 0.12485
7251 | 0 | 0.12485
7252 | 0 | 0.12485
7253 | 0 | 0.12485
7254 | 11.0489 | 11.1738
7255 | 1.1549 | 1.2798
7256 | 1.5022 | 1.627
7257 | 0 | 0.12485
7258 | 0 | 0.12485
7259 | 0 | 0.12485
7260 | 0.73035 | 0.8552
7261 | 0 | 0.12485
7262 | 0 | 0.12485
7263 | 0 | 0.12485
7264 | 0 | 0.12485
7265 | 0 | 0.12485
7266 | 5.7012 | 5.826
7267 | 11.2043 | 11.3291
7268 | 0 | 0.12485
7269 | 1.2176 | 1.3424
7270 | 0 | 0.12485
7271 | 0 | 0.12485
7272 | 0 | 0.12485
7273 | 0 | 0.12485
7274 | 0 | 0.12485
7275 | 0 | 0.12485
7276 | 0 | 0.12485
7277 | 0 | 0.12485
7278 | 11.0044 | 11.1293
7279 | 1.211 | 1.3359
7280 | 1.575 | 1.6999
7281 | 0 | 0.12485
7282 | 0 | 0.12485
7283 | 0 | 0.12485
7284 | 0.76569 | 0.89054
7285 | 0 | 0.12485
7286 | 0 | 0.12485
7287 | 0 | 0.12485
7288 | 0 | 0.12485
7289 | 0 | 0.12485
7290 | 5.4845 | 5.6093
7291 | 11.1143 | 11.2391
7292 | 0 | 0.12485
7293 | 1.1822 | 1.3071
7294 | 0 | 0.12485
7295 | 0 | 0.12485
7296 | 0 | 0.12485
7297 | 0 | 0.12485
7298 | 0 | 0.12485
7299 | 0 | 0.12485
7300 | 0 | 0.12485
7301 | 0 | 0.12485
7302 | 11.3045 | 11.4293
7303 | 1.1718 | 1.2966
7304 | 1.524 | 1.6489
7305 | 0 | 0.12485
7306 | 0 | 0.12485
7307 | 0 | 0.12485
7308 | 0.74099 | 0.86584
7309 | 0 | 0.12485
7310 | 0 | 0.12485
7311 | 0 | 0.12485
7312 | 0 | 0.12485
7313 | 0 | 0.12485
7314 | 5.7821 | 5.907
7315 | 10.8699 | 10.9948
7316 | 0 | 0.12485
7317 | 1.138 | 1.2628
7318 | 0 | 0.12485
7319 | 0 | 0.12485
7320 | 0 | 0.12485
7321 | 0 | 0.12485
7322 | 0 | 0.12485
7323 | 0 | 0.12485
7324 | 0 | 0.12485
7325 | 0 | 0.12485
7326 | 10.9414 | 11.0663
7327 | 1.1456 | 1.2705
7328 | 1.4901 | 1.615
7329 | 0 | 0.12485
7330 | 0 | 0.12485
7331 | 0 | 0.12485
7332 | 0.80611 | 0.93096
7333 | 0 | 0.12485
7334 | 0 | 0.12485
7335 | 0 | 0.12485
7336 | 0 | 0.12485
7337 | 0 | 0.12485
7338 | 5.6491 | 5.774
7339 | 11.1762 | 11.3011
7340 | 0 | 0.12485
7341 | 1.2188 | 1.3437
7342 | 0 | 0.12485
7343 | 0 | 0.12485
7344 | 0 | 0.12485
7345 | 0 | 0.12485
7346 | 0 | 0.12485
7347 | 0 | 0.12485
7348 | 0 | 0.12485
7349 | 0 | 0.12485
7350 | 11.0177 | 11.1425
7351 | 1.2146 | 1.3395
7352 | 1.5798 | 1.7046
7353 | 0 | 0.12485
7354 | 0 | 0.12485
7355 | 0 | 0.12485
7356 | 0.76804 | 0.89289
7357 | 0 | 0.12485
7358 | 0 | 0.12485
7359 | 0 | 0.12485
7360 | 0 | 0.12485
7361 | 0 | 0.12485
7362 | 5.7117 | 5.8365
7363 | 11.2944 | 11.4193
7364 | 0 | 0.12485
7365 | 1.1704 | 1.2953
7366 | 0 | 0.12485
7367 | 0 | 0.12485
7368 | 0 | 0.12485
7369 | 0 | 0.12485
7370 | 0 | 0.12485
7371 | 0 | 0.12485
7372 | 0 | 0.12485
7373 | 0 | 0.12485
7374 | 11.2247 | 11.3496
7375 | 1.1699 | 1.2948
7376 | 1.5217 | 1.6465
7377 | 0 | 0.12485
7378 | 0 | 0.12485
7379 | 0 | 0.12485
7380 | 0.73992 | 0.86477
7381 | 0 | 0.12485
7382 | 0 | 0.12485
7383 | 0 | 0.12485
7384 | 0 | 0.12485
7385 | 0 | 0.12485
7386 | 5.7694 | 5.8943
7387 | 11.3243 | 11.4491
7388 | 0 | 0.12485
7389 | 1.2293 | 1.3542
7390 | 0 | 0.12485
7391 | 0 | 0.12485
7392 | 0 | 0.12485
7393 | 0 | 0.12485
7394 | 0 | 0.12485
7395 | 0 | 0.12485
7396 | 0 | 0.12485
7397 | 0 | 0.12485
7398 | 11.1114 | 11.2362
7399 | 1.222 | 1.3469
7400 | 1.5894 | 1.7142
7401 | 0 | 0.12485
7402 | 0 | 0.12485
7403 | 0 | 0.12485
7404 | 0.77275 | 0.8976
7405 | 0 | 0.12485
7406 | 0 | 0.12485
7407 | 0 | 0.12485
7408 | 0 | 0.12485
7409 | 0 | 0.12485
7410 | 5.7438 | 5.8687
7411 | 11.3486 | 11.4734
7412 | 0 | 0.12485
7413 | 1.1754 | 1.3003
7414 | 0 | 0.12485
7415 | 0 | 0.12485
7416 | 0 | 0.12485
7417 | 0 | 0.12485
7418 | 0 | 0.12485
7419 | 0 | 0.12485
7420 | 0 | 0.12485
7421 | 0 | 0.12485
7422 | 11.271 | 11.3958
7423 | 1.1744 | 1.2993
7424 | 1.5276 | 1.6524
7425 | 0 | 0.12485
7426 | 0 | 0.12485
7427 | 0 | 0.12485
7428 | 0.74281 | 0.86766
7429 | 0 | 0.12485
7430 | 0 | 0.12485
7431 | 0 | 0.12485
7432 | 0 | 0.12485
7433 | 0 | 0.12485
7434 | 5.7893 | 5.9142
7435 | 11.3645 | 11.4893
7436 | 0 | 0.12485
7437 | 1.2336 | 1.3585
7438 | 0 | 0.12485
7439 | 0 | 0.12485
7440 | 0 | 0.12485
7441 | 0 | 0.12485
7442 | 0 | 0.12485
7443 | 0 | 0.12485
7444 | 0 | 0.12485
7445 | 0 | 0.12485
7446 | 11.1504 | 11.2753
7447 | 1.2262 | 1.3511
7448 | 1.5949 | 1.7197
7449 | 0 | 0.12485
7450 | 0 | 0.12485
7451 | 0 | 0.12485
7452 | 0.77545 | 0.9003
7453 | 0 | 0.12485
7454 | 0 | 0.12485
7455 | 0 | 0.12485
7456 | 0 | 0.12485
7457 | 0 | 0.12485
7458 | 5.7646 | 5.8894
7459 | 11.3886 | 11.5134
7460 | 0 | 0.12485
7461 | 1.1796 | 1.3044
7462 | 0 | 0.12485
7463 | 0 | 0.12485
7464 | 0 | 0.12485
7465 | 0 | 0.12485
7466 | 0 | 0.12485
7467 | 0 | 0.12485
7468 | 0 | 0.12485
7469 | 0 | 0.12485
7470 | 11.3101 | 11.4349
7471 | 1.1785 | 1.3034
7472 | 1.5329 | 1.6577
7473 | 0 | 0.12485
7474 | 0 | 0.12485
7475 | 0 | 0.12485
7476 | 0.74543 | 0.87028
7477 | 0 | 0.12485
7478 | 0 | 0.12485
7479 | 0 | 0.12485
7480 | 0 | 0.12485
7481 | 0 | 0.12485
7482 | 5.8081 | 5.9329
7483 | 11.4036 | 11.5284
7484 | 0 | 0.12485
7485 | 1.2378 | 1.3627
7486 | 0 | 0.12485
7487 | 0 | 0.12485
7488 | 0 | 0.12485
7489 | 0 | 0.12485
7490 | 0 | 0.12485
7491 | 0 | 0.12485
7492 | 0 | 0.12485
7493 | 0 | 0.12485
7494 | 11.1889 | 11.3137
7495 | 1.2304 | 1.3553
7496 | 1.6003 | 1.7252
7497 | 0 | 0.12485
7498 | 0 | 0.12485
7499 | 0 | 0.12485
7500 | 0.77813 | 0.90298
7501 | 0 | 0.12485
7502 | 0 | 0.12485
7503 | 0 | 0.12485
7504 | 0 | 0.12485
7505 | 0 | 0.12485
7506 | 5.7853 | 5.9102
7507 | 11.4286 | 11.5535
7508 | 0 | 0.12485
7509 | 1.1837 | 1.3086
7510 | 0 | 0.12485
7511 | 0 | 0.12485
7512 | 0 | 0.12485
7513 | 0 | 0.12485
7514 | 0 | 0.12485
7515 | 0 | 0.12485
7516 | 0 | 0.12485
7517 | 0 | 0.12485
7518 | 11.3492 | 11.4741
7519 | 1.1826 | 1.3074
7520 | 1.5382 | 1.6631
7521 | 0 | 0.12485
7522 | 0 | 0.12485
7523 | 0 | 0.12485
7524 | 0.74805 | 0.8729
7525 | 0 | 0.12485
7526 | 0 | 0.12485
7527 | 0 | 0.12485
7528 | 0 | 0.12485
7529 | 0 | 0.12485
7530 | 5.8296 | 5.9544
7531 | 11.4457 | 11.5706
7532 | 0 | 0.12485
7533 | 1.2422 | 1.3671
7534 | 0 | 0.12485
7535 | 0 | 0.12485
7536 | 0 | 0.12485
7537 | 0 | 0.12485
7538 | 0 | 0.12485
7539 | 0 | 0.12485
7540 | 0 | 0.12485
7541 | 0 | 0.12485
7542 | 11.229 | 11.3538
7543 | 1.2347 | 1.3595
7544 | 1.6059 | 1.7308
7545 | 0 | 0.12485
7546 | 0 | 0.12485
7547 | 0 | 0.12485
7548 | 0.78088 | 0.90573
7549 | 0 | 0.12485
7550 | 0 | 0.12485
7551 | 0 | 0.12485
7552 | 0 | 0.12485
7553 | 0 | 0.12485
7554 | 5.8052 | 5.93
7555 | 11.4651 | 11.5899
7556 | 0 | 0.12485
7557 | 1.1876 | 1.3125
7558 | 0 | 0.12485
7559 | 0 | 0.12485
7560 | 0 | 0.12485
7561 | 0 | 0.12485
7562 | 0 | 0.12485
7563 | 0 | 0.12485
7564 | 0 | 0.12485
7565 | 0 | 0.12485
7566 | 11.3854 | 11.5103
7567 | 1.186 | 1.3108
7568 | 1.5426 | 1.6675
7569 | 0 | 0.12485
7570 | 0 | 0.12485
7571 | 0 | 0.12485
7572 | 0.75024 | 0.87509
7573 | 0 | 0.12485
7574 | 0 | 0.12485
7575 | 0 | 0.12485
7576 | 0 | 0.12485
7577 | 0 | 0.12485
7578 | 5.849 | 5.9739
7579 | 11.4857 | 11.6105
7580 | 0 | 0.12485
7581 | 1.2465 | 1.3714
7582 | 0 | 0.12485
7583 | 0 | 0.12485
7584 | 0 | 0.12485
7585 | 0 | 0.12485
7586 | 0 | 0.12485
7587 | 0 | 0.12485
7588 | 0 | 0.12485
7589 | 0 | 0.12485
7590 | 11.268 | 11.3928
7591 | 1.2389 | 1.3638
7592 | 1.6114 | 1.7363
7593 | 0 | 0.12485
7594 | 0 | 0.12485
7595 | 0 | 0.12485
7596 | 0.78359 | 0.90844
7597 | 0 | 0.12485
7598 | 0 | 0.12485
7599 | 0 | 0.12485
7600 | 0 | 0.12485
7601 | 0 | 0.12485
7602 | 5.8248 | 5.9496
7603 | 11.5009 | 11.6258
7604 | 0 | 0.12485
7605 | 1.1915 | 1.3163
7606 | 0 | 0.12485
7607 | 0 | 0.12485
7608 | 0 | 0.12485
7609 | 0 | 0.12485
7610 | 0 | 0.12485
7611 | 0 | 0.12485
7612 | 0 | 0.12485
7613 | 0 | 0.12485
7614 | 11.4211 | 11.546
7615 | 1.1893 | 1.3141
7616 | 1.5469 | 1.6718
7617 | 0 | 0.12485
7618 | 0 | 0.12485
7619 | 0 | 0.12485
7620 | 0.75235 | 0.8772
7621 | 0 | 0.12485
7622 | 0 | 0.12485
7623 | 0 | 0.12485
7624 | 0 | 0.12485
7625 | 0 | 0.12485
7626 | 5.868 | 5.9928
7627 | 11.5251 | 11.65
7628 | 0 | 0.12485
7629 | 1.2508 | 1.3756
7630 | 0 | 0.12485
7631 | 0 | 0.12485
7632 | 0 | 0.12485
7633 | 0 | 0.12485
7634 | 0 | 0.12485
7635 | 0 | 0.12485
7636 | 0 | 0.12485
7637 | 0 | 0.12485
7638 | 11.3067 | 11.4316
7639 | 1.2431 | 1.368
7640 | 1.6169 | 1.7418
7641 | 0 | 0.12485
7642 | 0 | 0.12485
7643 | 0 | 0.12485
7644 | 0.78629 | 0.91114
7645 | 0 | 0.12485
7646 | 0 | 0.12485
7647 | 0 | 0.12485
7648 | 0 | 0.12485
7649 | 0 | 0.12485
7650 | 5.8443 | 5.9691
7651 | 11.5367 | 11.6616
7652 | 0 | 0.12485
7653 | 1.1953 | 1.3202
7654 | 0 | 0.12485
7655 | 0 | 0.12485
7656 | 0 | 0.12485
7657 | 0 | 0.12485
7658 | 0 | 0.12485
7659 | 0 | 0.12485
7660 | 0 | 0.12485
7661 | 0 | 0.12485
7662 | 11.4568 | 11.5816
7663 | 1.1925 | 1.3174
7664 | 1.5512 | 1.676
7665 | 0 | 0.12485
7666 | 0 | 0.12485
7667 | 0 | 0.12485
7668 | 0.75446 | 0.87931
7669 | 0 | 0.12485
7670 | 0 | 0.12485
7671 | 0 | 0.12485
7672 | 0 | 0.12485
7673 | 0 | 0.12485
7674 | 5.8869 | 6.0117
7675 | 11.5646 | 11.6894
7676 | 0 | 0.12485
7677 | 1.255 | 1.3799
7678 | 0 | 0.12485
7679 | 0 | 0.12485
7680 | 0 | 0.12485
7681 | 0 | 0.12485
7682 | 0 | 0.12485
7683 | 0 | 0.12485
7684 | 0 | 0.12485
7685 | 0 | 0.12485
7686 | 11.3454 | 11.4703
7687 | 1.2473 | 1.3722
7688 | 1.6224 | 1.7473
7689 | 0 | 0.12485
7690 | 0 | 0.12485
7691 | 0 | 0.12485
7692 | 0.78899 | 0.91384
7693 | 0 | 0.12485
7694 | 0 | 0.12485
7695 | 0 | 0.12485
7696 | 0 | 0.12485
7697 | 0 | 0.12485
7698 | 5.8638 | 5.9886
7699 | 11.5725 | 11.6973
7700 | 0 | 0.12485
7701 | 1.1992 | 1.324
7702 | 0 | 0.12485
7703 | 0 | 0.12485
7704 | 0 | 0.12485
7705 | 0 | 0.12485
7706 | 0 | 0.12485
7707 | 0 | 0.12485
7708 | 0 | 0.12485
7709 | 0 | 0.12485
7710 | 11.4924 | 11.6172
7711 | 1.1958 | 1.3206
7712 | 1.5555 | 1.6803
7713 | 0 | 0.12485
7714 | 0 | 0.12485
7715 | 0 | 0.12485
7716 | 0.75657 | 0.88142
7717 | 0 | 0.12485
7718 | 0 | 0.12485
7719 | 0 | 0.12485
7720 | 0 | 0.12485
7721 | 0 | 0.12485
7722 | 5.9058 | 6.0306
7723 | 11.6039 | 11.7288
7724 | 0 | 0.12485
7725 | 1.2593 | 1.3841
7726 | 0 | 0.12485
7727 | 0 | 0.12485
7728 | 0 | 0.12485
7729 | 0 | 0.12485
7730 | 0 | 0.12485
7731 | 0 | 0.12485
7732 | 0 | 0.12485
7733 | 0 | 0.12485
7734 | 11.384 | 11.5089
7735 | 1.2515 | 1.3764
7736 | 1.6279 | 1.7527
7737 | 0 | 0.12485
7738 | 0 | 0.12485
7739 | 0 | 0.12485
7740 | 0.79169 | 0.91654
7741 | 0 | 0.12485
7742 | 0 | 0.12485
7743 | 0 | 0.12485
7744 | 0 | 0.12485
7745 | 0 | 0.12485
7746 | 5.8833 | 6.0081
7747 | 11.6076 | 11.7325
7748 | 0 | 0.12485
7749 | 1.2028 | 1.3276
7750 | 0 | 0.12485
7751 | 0 | 0.12485
7752 | 0 | 0.12485
7753 | 0 | 0.12485
7754 | 0 | 0.12485
7755 | 0 | 0.12485
7756 | 0 | 0.12485
7757 | 0 | 0.12485
7758 | 11.5255 | 11.6504
7759 | 1.1988 | 1.3237
7760 | 1.5594 | 1.6843
7761 | 0 | 0.12485
7762 | 0 | 0.12485
7763 | 0 | 0.12485
7764 | 0.75854 | 0.88339
7765 | 0 | 0.12485
7766 | 0 | 0.12485
7767 | 0 | 0.12485
7768 | 0 | 0.12485
7769 | 0 | 0.12485
7770 | 5.924 | 6.0489
7771 | 11.6426 | 11.7674
7772 | 0 | 0.12485
7773 | 1.2635 | 1.3883
7774 | 0 | 0.12485
7775 | 0 | 0.12485
7776 | 0 | 0.12485
7777 | 0 | 0.12485
7778 | 0 | 0.12485
7779 | 0 | 0.12485
7780 | 0 | 0.12485
7781 | 0 | 0.12485
7782 | 11.4222 | 11.5471
7783 | 1.2557 | 1.3806
7784 | 1.6333 | 1.7582
7785 | 0 | 0.12485
7786 | 0 | 0.12485
7787 | 0 | 0.12485
7788 | 0.79436 | 0.91921
7789 | 0 | 0.12485
7790 | 0 | 0.12485
7791 | 0 | 0.12485
7792 | 0 | 0.12485
7793 | 0 | 0.12485
7794 | 5.9026 | 6.0274
7795 | 11.6418 | 11.7666
7796 | 0 | 0.12485
7797 | 1.2059 | 1.3307
7798 | 0 | 0.12485
7799 | 0 | 0.12485
7800 | 0 | 0.12485
7801 | 0 | 0.12485
7802 | 0 | 0.12485
7803 | 0 | 0.12485
7804 | 0 | 0.12485
7805 | 0 | 0.12485
7806 | 11.5542 | 11.6791
7807 | 1.2014 | 1.3263
7808 | 1.5629 | 1.6877
7809 | 0 | 0.12485
7810 | 0 | 0.12485
7811 | 0 | 0.12485
7812 | 0.84175 | 0.96659
7813 | 0 | 0.12485
7814 | 0 | 0.12485
7815 | 0 | 0.12485
7816 | 0 | 0.12485
7817 | 0 | 0.12485
7818 | 5.9022 | 6.0271
7819 | 11.6322 | 11.757
7820 | 0 | 0.12485
7821 | 1.2647 | 1.3896
7822 | 0 | 0.12485
7823 | 0 | 0.12485
7824 | 0 | 0.12485
7825 | 0 | 0.12485
7826 | 0 | 0.12485
7827 | 0 | 0.12485
7828 | 0 | 0.12485
7829 | 0 | 0.12485
7830 | 11.4349 | 11.5598
7831 | 1.2584 | 1.3832
7832 | 1.6368 | 1.7617
7833 | 0 | 0.12485
7834 | 0 | 0.12485
7835 | 0 | 0.12485
7836 | 0.79609 | 0.92094
7837 | 0 | 0.12485
7838 | 0 | 0.12485
7839 | 0 | 0.12485
7840 | 0 | 0.12485
7841 | 0 | 0.12485
7842 | 5.9154 | 6.0403
7843 | 11.6648 | 11.7897
7844 | 0 | 0.12485
7845 | 1.208 | 1.3328
7846 | 0 | 0.12485
7847 | 0 | 0.12485
7848 | 0 | 0.12485
7849 | 0 | 0.12485
7850 | 0 | 0.12485
7851 | 0 | 0.12485
7852 | 0 | 0.12485
7853 | 0 | 0.12485
7854 | 11.5739 | 11.6988
7855 | 1.2032 | 1.3281
7856 | 1.5652 | 1.6901
7857 | 0 | 0.12485
7858 | 0 | 0.12485
7859 | 0 | 0.12485
7860 | 0.84261 | 0.96745
7861 | 0 | 0.12485
7862 | 0 | 0.12485
7863 | 0 | 0.12485
7864 | 0 | 0.12485
7865 | 0 | 0.12485
7866 | 5.9087 | 6.0335
7867 | 11.6469 | 11.7718
7868 | 0 | 0.12485
7869 | 1.2675 | 1.3923
7870 | 0 | 0.12485
7871 | 0 | 0.12485
7872 | 0 | 0.12485
7873 | 0 | 0.12485
7874 | 0 | 0.12485
7875 | 0 | 0.12485
7876 | 0 | 0.12485
7877 | 0 | 0.12485
7878 | 11.8682 | 11.9931
7879 | 1.2545 | 1.3794
7880 | 1.6318 | 1.7567
7881 | 0 | 0.12485
7882 | 0 | 0.12485
7883 | 0 | 0.12485
7884 | 0.79372 | 0.91857
7885 | 0 | 0.12485
7886 | 0 | 0.12485
7887 | 0 | 0.12485
7888 | 0 | 0.12485
7889 | 0 | 0.12485
7890 | 5.8998 | 6.0246
7891 | 11.6387 | 11.7636
7892 | 0 | 0.12485
7893 | 1.2056 | 1.3304
7894 | 0 | 0.12485
7895 | 0 | 0.12485
7896 | 0 | 0.12485
7897 | 0 | 0.12485
7898 | 0 | 0.12485
7899 | 0 | 0.12485
7900 | 0 | 0.12485
7901 | 0 | 0.12485
7902 | 11.5539 | 11.6787
7903 | 1.2014 | 1.3263
7904 | 1.5629 | 1.6877
7905 | 0 | 0.12485
7906 | 0 | 0.12485
7907 | 0 | 0.12485
7908 | 0.84192 | 0.96677
7909 | 0 | 0.12485
7910 | 0 | 0.12485
7911 | 0 | 0.12485
7912 | 0 | 0.12485
7913 | 0 | 0.12485
7914 | 5.9043 | 6.0292
7915 | 11.6437 | 11.7685
7916 | 0 | 0.12485
7917 | 1.2691 | 1.3939
7918 | 0 | 0.12485
7919 | 0 | 0.12485
7920 | 0 | 0.12485
7921 | 0 | 0.12485
7922 | 0 | 0.12485
7923 | 0 | 0.12485
7924 | 0 | 0.12485
7925 | 0 | 0.12485
7926 | 11.8842 | 12.009
7927 | 1.256 | 1.3809
7928 | 1.6338 | 1.7587
7929 | 0 | 0.12485
7930 | 0 | 0.12485
7931 | 0 | 0.12485
7932 | 0.79473 | 0.91958
7933 | 0 | 0.12485
7934 | 0 | 0.12485
7935 | 0 | 0.12485
7936 | 0 | 0.12485
7937 | 0 | 0.12485
7938 | 5.9072 | 6.0321
7939 | 11.6519 | 11.7767
7940 | 0 | 0.12485
7941 | 1.2068 | 1.3316
7942 | 0 | 0.12485
7943 | 0 | 0.12485
7944 | 0 | 0.12485
7945 | 0 | 0.12485
7946 | 0 | 0.12485
7947 | 0 | 0.12485
7948 | 0 | 0.12485
7949 | 0 | 0.12485
7950 | 11.5654 | 11.6903
7951 | 1.3058 | 1.4306
7952 | 1.6984 | 1.8233
7953 | 0 | 0.12485
7954 | 0 | 0.12485
7955 | 0 | 0.12485
7956 | 0.82609 | 0.95094
7957 | 0 | 0.12485
7958 | 0 | 0.12485
7959 | 0 | 0.12485
7960 | 0 | 0.12485
7961 | 0 | 0.12485
7962 | 5.9123 | 6.0371
7963 | 12.0636 | 12.1884
7964 | 0 | 0.12485
7965 | 1.2378 | 1.3627
7966 | 0 | 0.12485
7967 | 0 | 0.12485
7968 | 0 | 0.12485
7969 | 0 | 0.12485
7970 | 0 | 0.12485
7971 | 0 | 0.12485
7972 | 0 | 0.12485
7973 | 0 | 0.12485
7974 | 11.8379 | 11.9628
7975 | 1.2271 | 1.3519
7976 | 1.5962 | 1.7211
7977 | 0 | 0.12485
7978 | 0 | 0.12485
7979 | 0 | 0.12485
7980 | 0.77656 | 0.90141
7981 | 0 | 0.12485
7982 | 0 | 0.12485
7983 | 0 | 0.12485
7984 | 0 | 0.12485
7985 | 0 | 0.12485
7986 | 6.0485 | 6.1733
7987 | 11.8609 | 11.9858
7988 | 0 | 0.12485
7989 | 1.2848 | 1.4097
7990 | 0 | 0.12485
7991 | 0 | 0.12485
7992 | 0 | 0.12485
7993 | 0 | 0.12485
7994 | 0 | 0.12485
7995 | 0 | 0.12485
7996 | 0 | 0.12485
7997 | 0 | 0.12485
7998 | 11.6152 | 11.74
7999 | 1.2756 | 1.4004
8000 | 1.6592 | 1.7841
8001 | 0 | 0.12485
8002 | 0 | 0.12485
8003 | 0 | 0.12485
8004 | 0.8071 | 0.93195
8005 | 0 | 0.12485
8006 | 0 | 0.12485
8007 | 0 | 0.12485
8008 | 0 | 0.12485
8009 | 0 | 0.12485
8010 | 5.9943 | 6.1191
8011 | 11.8033 | 11.9282
8012 | 0 | 0.12485
8013 | 1.2206 | 1.3454
8014 | 0 | 0.12485
8015 | 0 | 0.12485
8016 | 0 | 0.12485
8017 | 0 | 0.12485
8018 | 0 | 0.12485
8019 | 0 | 0.12485
8020 | 0 | 0.12485
8021 | 0 | 0.12485
8022 | 11.6889 | 11.8137
8023 | 1.2137 | 1.3385
8024 | 1.5789 | 1.7038
8025 | 0 | 0.12485
8026 | 0 | 0.12485
8027 | 0 | 0.12485
8028 | 0.85015 | 0.975
8029 | 0 | 0.12485
8030 | 0 | 0.12485
8031 | 0 | 0.12485
8032 | 0 | 0.12485
8033 | 0 | 0.12485
8034 | 6.077 | 6.2018
8035 | 11.7131 | 11.838
8036 | 0 | 0.12485
8037 | 1.2787 | 1.4035
8038 | 0 | 0.12485
8039 | 0 | 0.12485
8040 | 0 | 0.12485
8041 | 0 | 0.12485
8042 | 0 | 0.12485
8043 | 0 | 0.12485
8044 | 0 | 0.12485
8045 | 0 | 0.12485
8046 | 12.1736 | 12.2985
8047 | 1.2512 | 1.3761
8048 | 1.6276 | 1.7525
8049 | 0 | 0.12485
8050 | 0 | 0.12485
8051 | 0 | 0.12485
8052 | 0.79183 | 0.91668
8053 | 0 | 0.12485
8054 | 0 | 0.12485
8055 | 0 | 0.12485
8056 | 0 | 0.12485
8057 | 0 | 0.12485
8058 | 6.1381 | 6.263
8059 | 11.9848 | 12.1097
8060 | 0 | 0.12485
8061 | 1.2949 | 1.4197
8062 | 0 | 0.12485
8063 | 0 | 0.12485
8064 | 0 | 0.12485
8065 | 0 | 0.12485
8066 | 0 | 0.12485
8067 | 0 | 0.12485
8068 | 0 | 0.12485
8069 | 0 | 0.12485
8070 | 11.7047 | 11.8295
8071 | 1.2836 | 1.4085
8072 | 1.6697 | 1.7945
8073 | 0 | 0.12485
8074 | 0 | 0.12485
8075 | 0 | 0.12485
8076 | 0.81223 | 0.93708
8077 | 0 | 0.12485
8078 | 0 | 0.12485
8079 | 0 | 0.12485
8080 | 0 | 0.12485
8081 | 0 | 0.12485
8082 | 6.0309 | 6.1557
8083 | 11.8674 | 11.9923
8084 | 0 | 0.12485
8085 | 1.2264 | 1.3513
8086 | 0 | 0.12485
8087 | 0 | 0.12485
8088 | 0 | 0.12485
8089 | 0 | 0.12485
8090 | 0 | 0.12485
8091 | 0 | 0.12485
8092 | 0 | 0.12485
8093 | 0 | 0.12485
8094 | 11.7419 | 11.8667
8095 | 1.3218 | 1.4466
8096 | 1.7193 | 1.8441
8097 | 0 | 0.12485
8098 | 0 | 0.12485
8099 | 0 | 0.12485
8100 | 0.8363 | 0.96115
8101 | 0 | 0.12485
8102 | 0 | 0.12485
8103 | 0 | 0.12485
8104 | 0 | 0.12485
8105 | 0 | 0.12485
8106 | 5.985 | 6.1098
8107 | 12.1936 | 12.3185
8108 | 0 | 0.12485
8109 | 1.2507 | 1.3755
8110 | 0 | 0.12485
8111 | 0 | 0.12485
8112 | 0 | 0.12485
8113 | 0 | 0.12485
8114 | 0 | 0.12485
8115 | 0 | 0.12485
8116 | 0 | 0.12485
8117 | 0 | 0.12485
8118 | 11.9546 | 12.0794
8119 | 1.2377 | 1.3626
8120 | 1.6102 | 1.735
8121 | 0 | 0.12485
8122 | 0 | 0.12485
8123 | 0 | 0.12485
8124 | 0.86508 | 0.98993
8125 | 0 | 0.12485
8126 | 0 | 0.12485
8127 | 0 | 0.12485
8128 | 0 | 0.12485
8129 | 0 | 0.12485
8130 | 6.0678 | 6.1927
8131 | 11.9221 | 12.047
8132 | 0 | 0.12485
8133 | 1.2939 | 1.4187
8134 | 0 | 0.12485
8135 | 0 | 0.12485
8136 | 0 | 0.12485
8137 | 0 | 0.12485
8138 | 0 | 0.12485
8139 | 0 | 0.12485
8140 | 0 | 0.12485
8141 | 0 | 0.12485
8142 | 12.1071 | 12.2319
8143 | 1.2763 | 1.4012
8144 | 1.6603 | 1.7851
8145 | 0 | 0.12485
8146 | 0 | 0.12485
8147 | 0 | 0.12485
8148 | 0.80774 | 0.93258
8149 | 0 | 0.12485
8150 | 0 | 0.12485
8151 | 0 | 0.12485
8152 | 0 | 0.12485
8153 | 0 | 0.12485
8154 | 6.0003 | 6.1251
8155 | 11.815 | 11.9399
8156 | 0 | 0.12485
8157 | 1.3245 | 1.4494
8158 | 0 | 0.12485
8159 | 0 | 0.12485
8160 | 0 | 0.12485
8161 | 0 | 0.12485
8162 | 0 | 0.12485
8163 | 0 | 0.12485
8164 | 0 | 0.12485
8165 | 0 | 0.12485
8166 | 11.9657 | 12.0906
8167 | 1.3025 | 1.4274
8168 | 1.6943 | 1.8192
8169 | 0 | 0.12485
8170 | 0 | 0.12485
8171 | 0 | 0.12485
8172 | 0.82424 | 0.94909
8173 | 0 | 0.12485
8174 | 0 | 0.12485
8175 | 0 | 0.12485
8176 | 0 | 0.12485
8177 | 0 | 0.12485
8178 | 6.1151 | 6.24
8179 | 12.0134 | 12.1383
8180 | 0 | 0.12485
8181 | 1.2397 | 1.3646
8182 | 0 | 0.12485
8183 | 0 | 0.12485
8184 | 0 | 0.12485
8185 | 0 | 0.12485
8186 | 0 | 0.12485
8187 | 0 | 0.12485
8188 | 0 | 0.12485
8189 | 0 | 0.12485
8190 | 11.8611 | 11.986
8191 | 1.3324 | 1.4573
8192 | 1.7332 | 1.858
8193 | 0 | 0.12485
8194 | 0 | 0.12485
8195 | 0 | 0.12485
8196 | 0.84311 | 0.96796
8197 | 0 | 0.12485
8198 | 0 | 0.12485
8199 | 0 | 0.12485
8200 | 0 | 0.12485
8201 | 0 | 0.12485
8202 | 6.0334 | 6.1582
8203 | 12.28 | 12.4049
8204 | 0 | 0.12485
8205 | 1.2591 | 1.384
8206 | 0 | 0.12485
8207 | 0 | 0.12485
8208 | 0 | 0.12485
8209 | 0 | 0.12485
8210 | 0 | 0.12485
8211 | 0 | 0.12485
8212 | 0 | 0.12485
8213 | 0 | 0.12485
8214 | 12.0312 | 12.156
8215 | 1.2447 | 1.3696
8216 | 1.6193 | 1.7441
8217 | 0 | 0.12485
8218 | 0 | 0.12485
8219 | 0 | 0.12485
8220 | 0.86921 | 0.99406
8221 | 0 | 0.12485
8222 | 0 | 0.12485
8223 | 0 | 0.12485
8224 | 0 | 0.12485
8225 | 0 | 0.12485
8226 | 6.0975 | 6.2223
8227 | 11.9775 | 12.1023
8228 | 0 | 0.12485
8229 | 1.3006 | 1.4255
8230 | 0 | 0.12485
8231 | 0 | 0.12485
8232 | 0 | 0.12485
8233 | 0 | 0.12485
8234 | 0 | 0.12485
8235 | 0 | 0.12485
8236 | 0 | 0.12485
8237 | 0 | 0.12485
8238 | 12.3716 | 12.4964
8239 | 1.2697 | 1.3945
8240 | 1.6517 | 1.7765
8241 | 0 | 0.12485
8242 | 0 | 0.12485
8243 | 0 | 0.12485
8244 | 0.80366 | 0.92851
8245 | 0 | 0.12485
8246 | 0 | 0.12485
8247 | 0 | 0.12485
8248 | 0 | 0.12485
8249 | 0 | 0.12485
8250 | 6.2211 | 6.346
8251 | 12.1451 | 12.27
8252 | 0 | 0.12485
8253 | 1.3115 | 1.4363
8254 | 0 | 0.12485
8255 | 0 | 0.12485
8256 | 0 | 0.12485
8257 | 0 | 0.12485
8258 | 0 | 0.12485
8259 | 0 | 0.12485
8260 | 0 | 0.12485
8261 | 0 | 0.12485
8262 | 12.2634 | 12.3882
8263 | 1.2905 | 1.4153
8264 | 1.6787 | 1.8036
8265 | 0 | 0.12485
8266 | 0 | 0.12485
8267 | 0 | 0.12485
8268 | 0.81678 | 0.94162
8269 | 0 | 0.12485
8270 | 0 | 0.12485
8271 | 0 | 0.12485
8272 | 0 | 0.12485
8273 | 0 | 0.12485
8274 | 6.0647 | 6.1896
8275 | 11.928 | 12.0528
8276 | 0 | 0.12485
8277 | 1.3356 | 1.4604
8278 | 0 | 0.12485
8279 | 0 | 0.12485
8280 | 0 | 0.12485
8281 | 0 | 0.12485
8282 | 0 | 0.12485
8283 | 0 | 0.12485
8284 | 0 | 0.12485
8285 | 0 | 0.12485
8286 | 12.0649 | 12.1897
8287 | 1.3127 | 1.4376
8288 | 1.7076 | 1.8325
8289 | 0 | 0.12485
8290 | 0 | 0.12485
8291 | 0 | 0.12485
8292 | 0.83079 | 0.95564
8293 | 0 | 0.12485
8294 | 0 | 0.12485
8295 | 0 | 0.12485
8296 | 0 | 0.12485
8297 | 0 | 0.12485
8298 | 6.1623 | 6.2871
8299 | 12.0965 | 12.2213
8300 | 0 | 0.12485
8301 | 1.2473 | 1.3721
8302 | 0 | 0.12485
8303 | 0 | 0.12485
8304 | 0 | 0.12485
8305 | 0 | 0.12485
8306 | 0 | 0.12485
8307 | 0 | 0.12485
8308 | 0 | 0.12485
8309 | 0 | 0.12485
8310 | 11.9298 | 12.0546
8311 | 1.3407 | 1.4655
8312 | 1.744 | 1.8688
8313 | 0 | 0.12485
8314 | 0 | 0.12485
8315 | 0 | 0.12485
8316 | 0.84844 | 0.97328
8317 | 0 | 0.12485
8318 | 0 | 0.12485
8319 | 0 | 0.12485
8320 | 0 | 0.12485
8321 | 0 | 0.12485
8322 | 6.0718 | 6.1966
8323 | 12.3523 | 12.4772
8324 | 0 | 0.12485
8325 | 1.2673 | 1.3921
8326 | 0 | 0.12485
8327 | 0 | 0.12485
8328 | 0 | 0.12485
8329 | 0 | 0.12485
8330 | 0 | 0.12485
8331 | 0 | 0.12485
8332 | 0 | 0.12485
8333 | 0 | 0.12485
8334 | 12.1059 | 12.2307
8335 | 1.2516 | 1.3764
8336 | 1.6283 | 1.7531
8337 | 0 | 0.12485
8338 | 0 | 0.12485
8339 | 0 | 0.12485
8340 | 0.87364 | 0.99849
8341 | 0 | 0.12485
8342 | 0 | 0.12485
8343 | 0 | 0.12485
8344 | 0 | 0.12485
8345 | 0 | 0.12485
8346 | 6.2437 | 6.3686
8347 | 12.0048 | 12.1296
8348 | 0 | 0.12485
8349 | 1.3072 | 1.4321
8350 | 0 | 0.12485
8351 | 0 | 0.12485
8352 | 0 | 0.12485
8353 | 0 | 0.12485
8354 | 0 | 0.12485
8355 | 0 | 0.12485
8356 | 0 | 0.12485
8357 | 0 | 0.12485
8358 | 12.4365 | 12.5613
8359 | 1.2774 | 1.4022
8360 | 1.6617 | 1.7866
8361 | 0 | 0.12485
8362 | 0 | 0.12485
8363 | 0 | 0.12485
8364 | 0.80862 | 0.93347
8365 | 0 | 0.12485
8366 | 0 | 0.12485
8367 | 0 | 0.12485
8368 | 0 | 0.12485
8369 | 0 | 0.12485
8370 | 6.2642 | 6.389
8371 | 12.2337 | 12.3585
8372 | 0 | 0.12485
8373 | 1.321 | 1.4458
8374 | 0 | 0.12485
8375 | 0 | 0.12485
8376 | 0 | 0.12485
8377 | 0 | 0.12485
8378 | 0 | 0.12485
8379 | 0 | 0.12485
8380 | 0 | 0.12485
8381 | 0 | 0.12485
8382 | 12.5505 | 12.6754
8383 | 1.2852 | 1.4101
8384 | 1.6719 | 1.7968
8385 | 0 | 0.12485
8386 | 0 | 0.12485
8387 | 0 | 0.12485
8388 | 0.81356 | 0.93841
8389 | 0 | 0.12485
8390 | 0 | 0.12485
8391 | 0 | 0.12485
8392 | 0 | 0.12485
8393 | 0 | 0.12485
8394 | 6.2911 | 6.416
8395 | 12.2708 | 12.3957
8396 | 0 | 0.12485
8397 | 1.324 | 1.4488
8398 | 0 | 0.12485
8399 | 0 | 0.12485
8400 | 0 | 0.12485
8401 | 0 | 0.12485
8402 | 0 | 0.12485
8403 | 0 | 0.12485
8404 | 0 | 0.12485
8405 | 0 | 0.12485
8406 | 12.5771 | 12.702
8407 | 1.2876 | 1.4124
8408 | 1.675 | 1.7998
8409 | 0 | 0.12485
8410 | 0 | 0.12485
8411 | 0 | 0.12485
8412 | 0.81507 | 0.93992
8413 | 0 | 0.12485
8414 | 0 | 0.12485
8415 | 0 | 0.12485
8416 | 0 | 0.12485
8417 | 0 | 0.12485
8418 | 6.302 | 6.4269
8419 | 12.2907 | 12.4155
8420 | 0 | 0.12485
8421 | 1.326 | 1.4508
8422 | 0 | 0.12485
8423 | 0 | 0.12485
8424 | 0 | 0.12485
8425 | 0 | 0.12485
8426 | 0 | 0.12485
8427 | 0 | 0.12485
8428 | 0 | 0.12485
8429 | 0 | 0.12485
8430 | 12.5954 | 12.7202
8431 | 1.2894 | 1.4142
8432 | 1.6774 | 1.8022
8433 | 0 | 0.12485
8434 | 0 | 0.12485
8435 | 0 | 0.12485
8436 | 0.81625 | 0.9411
8437 | 0 | 0.12485
8438 | 0 | 0.12485
8439 | 0 | 0.12485
8440 | 0 | 0.12485
8441 | 0 | 0.12485
8442 | 6.3105 | 6.4354
8443 | 12.3078 | 12.4327
8444 | 0 | 0.12485
8445 | 1.3278 | 1.4526
8446 | 0 | 0.12485
8447 | 0 | 0.12485
8448 | 0 | 0.12485
8449 | 0 | 0.12485
8450 | 0 | 0.12485
8451 | 0 | 0.12485
8452 | 0 | 0.12485
8453 | 0 | 0.12485
8454 | 12.6122 | 12.7371
8455 | 1.2911 | 1.416
8456 | 1.6796 | 1.8045
8457 | 0 | 0.12485
8458 | 0 | 0.12485
8459 | 0 | 0.12485
8460 | 0.81736 | 0.94221
8461 | 0 | 0.12485
8462 | 0 | 0.12485
8463 | 0 | 0.12485
8464 | 0 | 0.12485
8465 | 0 | 0.12485
8466 | 6.3196 | 6.4444
8467 | 12.3255 | 12.4504
8468 | 0 | 0.12485
8469 | 1.3296 | 1.4545
8470 | 0 | 0.12485
8471 | 0 | 0.12485
8472 | 0 | 0.12485
8473 | 0 | 0.12485
8474 | 0 | 0.12485
8475 | 0 | 0.12485
8476 | 0 | 0.12485
8477 | 0 | 0.12485
8478 | 12.6293 | 12.7541
8479 | 1.2929 | 1.4177
8480 | 1.6819 | 1.8068
8481 | 0 | 0.12485
8482 | 0 | 0.12485
8483 | 0 | 0.12485
8484 | 0.81848 | 0.94333
8485 | 0 | 0.12485
8486 | 0 | 0.12485
8487 | 0 | 0.12485
8488 | 0 | 0.12485
8489 | 0 | 0.12485
8490 | 6.3286 | 6.4535
8491 | 12.3431 | 12.4679
8492 | 0 | 0.12485
8493 | 1.3315 | 1.4563
8494 | 0 | 0.12485
8495 | 0 | 0.12485
8496 | 0 | 0.12485
8497 | 0 | 0.12485
8498 | 0 | 0.12485
8499 | 0 | 0.12485
8500 | 0 | 0.12485
8501 | 0 | 0.12485
8502 | 12.6461 | 12.771
8503 | 1.2946 | 1.4194
8504 | 1.6841 | 1.809
8505 | 0 | 0.12485
8506 | 0 | 0.12485
8507 | 0 | 0.12485
8508 | 0.81959 | 0.94443
8509 | 0 | 0.12485
8510 | 0 | 0.12485
8511 | 0 | 0.12485
8512 | 0 | 0.12485
8513 | 0 | 0.12485
8514 | 6.3375 | 6.4624
8515 | 12.3605 | 12.4853
8516 | 0 | 0.12485
8517 | 1.3333 | 1.4581
8518 | 0 | 0.12485
8519 | 0 | 0.12485
8520 | 0 | 0.12485
8521 | 0 | 0.12485
8522 | 0 | 0.12485
8523 | 0 | 0.12485
8524 | 0 | 0.12485
8525 | 0 | 0.12485
8526 | 12.6628 | 12.7876
8527 | 1.2963 | 1.4211
8528 | 1.6864 | 1.8112
8529 | 0 | 0.12485
8530 | 0 | 0.12485
8531 | 0 | 0.12485
8532 | 0.82068 | 0.94552
8533 | 0 | 0.12485
8534 | 0 | 0.12485
8535 | 0 | 0.12485
8536 | 0 | 0.12485
8537 | 0 | 0.12485
8538 | 6.3464 | 6.4712
8539 | 12.3776 | 12.5025
8540 | 0 | 0.12485
8541 | 1.335 | 1.4599
8542 | 0 | 0.12485
8543 | 0 | 0.12485
8544 | 0 | 0.12485
8545 | 0 | 0.12485
8546 | 0 | 0.12485
8547 | 0 | 0.12485
8548 | 0 | 0.12485
8549 | 0 | 0.12485
8550 | 12.6792 | 12.804
8551 | 1.298 | 1.4228
8552 | 1.6886 | 1.8134
8553 | 0 | 0.12485
8554 | 0 | 0.12485
8555 | 0 | 0.12485
8556 | 0.82175 | 0.9466
8557 | 0 | 0.12485
8558 | 0 | 0.12485
8559 | 0 | 0.12485
8560 | 0 | 0.12485
8561 | 0 | 0.12485
8562 | 6.3551 | 6.4799
8563 | 12.3945 | 12.5194
8564 | 0 | 0.12485
8565 | 1.3368 | 1.4617
8566 | 0 | 0.12485
8567 | 0 | 0.12485
8568 | 0 | 0.12485
8569 | 0 | 0.12485
8570 | 0 | 0.12485
8571 | 0 | 0.12485
8572 | 0 | 0.12485
8573 | 0 | 0.12485
8574 | 12.6954 | 12.8202
8575 | 1.2996 | 1.4245
8576 | 1.6907 | 1.8156
8577 | 0 | 0.12485
8578 | 0 | 0.12485
8579 | 0 | 0.12485
8580 | 0.82282 | 0.94766
8581 | 0 | 0.12485
8582 | 0 | 0.12485
8583 | 0 | 0.12485
8584 | 0 | 0.12485
8585 | 0 | 0.12485
8586 | 6.3637 | 6.4885
8587 | 12.4112 | 12.5361
8588 | 0 | 0.12485
8589 | 1.3385 | 1.4634
8590 | 0 | 0.12485
8591 | 0 | 0.12485
8592 | 0 | 0.12485
8593 | 0 | 0.12485
8594 | 0 | 0.12485
8595 | 0 | 0.12485
8596 | 0 | 0.12485
8597 | 0 | 0.12485
8598 | 12.7114 | 12.8362
8599 | 1.3013 | 1.4261
8600 | 1.6928 | 1.8177
8601 | 0 | 0.12485
8602 | 0 | 0.12485
8603 | 0 | 0.12485
8604 | 0.82386 | 0.94871
8605 | 0 | 0.12485
8606 | 0 | 0.12485
8607 | 0 | 0.12485
8608 | 0 | 0.12485
8609 | 0 | 0.12485
8610 | 6.3721 | 6.497
8611 | 12.4277 | 12.5525
8612 | 0 | 0.12485
8613 | 1.3403 | 1.4651
8614 | 0 | 0.12485
8615 | 0 | 0.12485
8616 | 0 | 0.12485
8617 | 0 | 0.12485
8618 | 0 | 0.12485
8619 | 0 | 0.12485
8620 | 0 | 0.12485
8621 | 0 | 0.12485
8622 | 12.7271 | 12.852
8623 | 1.3029 | 1.4277
8624 | 1.6949 | 1.8198
8625 | 0 | 0.12485
8626 | 0 | 0.12485
8627 | 0 | 0.12485
8628 | 0.8249 | 0.94974
8629 | 0 | 0.12485
8630 | 0 | 0.12485
8631 | 0 | 0.12485
8632 | 0 | 0.12485
8633 | 0 | 0.12485
8634 | 6.3805 | 6.5053
8635 | 12.4439 | 12.5688
8636 | 0 | 0.12485
8637 | 1.3419 | 1.4668
8638 | 0 | 0.12485
8639 | 0 | 0.12485
8640 | 0 | 0.12485
8641 | 0 | 0.12485
8642 | 0 | 0.12485
8643 | 0 | 0.12485
8644 | 0 | 0.12485
8645 | 0 | 0.12485
8646 | 12.7426 | 12.8675
8647 | 1.3044 | 1.4293
8648 | 1.697 | 1.8218
8649 | 0 | 0.12485
8650 | 0 | 0.12485
8651 | 0 | 0.12485
8652 | 0.82591 | 0.95076
8653 | 0 | 0.12485
8654 | 0 | 0.12485
8655 | 0 | 0.12485
8656 | 0 | 0.12485
8657 | 0 | 0.12485
8658 | 6.3887 | 6.5135
8659 | 12.4599 | 12.5847
8660 | 0 | 0.12485
8661 | 1.3436 | 1.4685
8662 | 0 | 0.12485
8663 | 0 | 0.12485
8664 | 0 | 0.12485
8665 | 0 | 0.12485
8666 | 0 | 0.12485
8667 | 0 | 0.12485
8668 | 0 | 0.12485
8669 | 0 | 0.12485
8670 | 12.7579 | 12.8828
8671 | 1.306 | 1.4309
8672 | 1.699 | 1.8239
8673 | 0 | 0.12485
8674 | 0 | 0.12485
8675 | 0 | 0.12485
8676 | 0.82691 | 0.95176
8677 | 0 | 0.12485
8678 | 0 | 0.12485
8679 | 0 | 0.12485
8680 | 0 | 0.12485
8681 | 0 | 0.12485
8682 | 6.3968 | 6.5216
8683 | 12.4756 | 12.6005
8684 | 0 | 0.12485
8685 | 1.3452 | 1.4701
8686 | 0 | 0.12485
8687 | 0 | 0.12485
8688 | 0 | 0.12485
8689 | 0 | 0.12485
8690 | 0 | 0.12485
8691 | 0 | 0.12485
8692 | 0 | 0.12485
8693 | 0 | 0.12485
8694 | 12.7729 | 12.8978
8695 | 1.3075 | 1.4324
8696 | 1.701 | 1.8259
8697 | 0 | 0.12485
8698 | 0 | 0.12485
8699 | 0 | 0.12485
8700 | 0.8279 | 0.95275
8701 | 0 | 0.12485
8702 | 0 | 0.12485
8703 | 0 | 0.12485
8704 | 0 | 0.12485
8705 | 0 | 0.12485
8706 | 6.4047 | 6.5296
8707 | 12.4911 | 12.616
8708 | 0 | 0.12485
8709 | 1.3469 | 1.4717
8710 | 0 | 0.12485
8711 | 0 | 0.12485
8712 | 0 | 0.12485
8713 | 0 | 0.12485
8714 | 0 | 0.12485
8715 | 0 | 0.12485
8716 | 0 | 0.12485
8717 | 0 | 0.12485
8718 | 12.7877 | 12.9126
8719 | 1.3091 | 1.4339
8720 | 1.703 | 1.8279
8721 | 0 | 0.12485
8722 | 0 | 0.12485
8723 | 0 | 0.12485
8724 | 0.82887 | 0.95372
8725 | 0 | 0.12485
8726 | 0 | 0.12485
8727 | 0 | 0.12485
8728 | 0 | 0.12485
8729 | 0 | 0.12485
8730 | 6.4126 | 6.5374
8731 | 12.5064 | 12.6312
8732 | 0 | 0.12485
8733 | 1.3484 | 1.4733
8734 | 0 | 0.12485
8735 | 0 | 0.12485
8736 | 0 | 0.12485
8737 | 0 | 0.12485
8738 | 0 | 0.12485
8739 | 0 | 0.12485
8740 | 0 | 0.12485
8741 | 0 | 0.12485
8742 | 12.8022 | 12.9271
8743 | 1.3105 | 1.4354
8744 | 1.7049 | 1.8298
8745 | 0 | 0.12485
8746 | 0 | 0.12485
8747 | 0 | 0.12485
8748 | 0.82982 | 0.95467
8749 | 0 | 0.12485
8750 | 0 | 0.12485
8751 | 0 | 0.12485
8752 | 0 | 0.12485
8753 | 0 | 0.12485
8754 | 6.4203 | 6.5451
8755 | 12.5213 | 12.6462
8756 | 0 | 0.12485
8757 | 1.35 | 1.4748
8758 | 0 | 0.12485
8759 | 0 | 0.12485

## Reference Output
hour | draw_kW | source_kW | tank_C
0 | 0 | 0 | 59.9519
1 | 0 | 0 | 59.856
2 | 0 | 0 | 59.7602
3 | 0 | 0 | 59.6647
4 | 0 | 0 | 59.5694
5 | 0 | 0 | 59.4744
6 | 12.5257 | 13.6671 | 59.24
7 | 1.2893 | 0 | 59.2497
8 | 1.6775 | 6.4214 | 61.6253
9 | 0 | 0 | 62.6197
10 | 0 | 0 | 62.5175
11 | 0 | 0 | 62.4155
12 | 0.89846 | 0 | 61.6792
13 | 0 | 0 | 61.5217
14 | 0 | 0 | 61.4221
15 | 0 | 0 | 61.3227
16 | 0 | 0 | 61.2235
17 | 0 | 0 | 61.1245
18 | 6.4206 | 6.844 | 60.4111
19 | 12.9212 | 13.1124 | 60.5926
20 | 0 | 0 | 61.2971
21 | 1.3154 | 0 | 60.2693
22 | 0 | 0 | 60.0886
23 | 0 | 0 | 59.9923
24 | 0 | 0 | 59.8962
25 | 0 | 0 | 59.8004
26 | 0 | 0 | 59.7048
27 | 0 | 0 | 59.6094
28 | 0 | 0 | 59.5143
29 | 0 | 0 | 59.4193
30 | 12.5334 | 13.7037 | 59.2019
31 | 1.2904 | 0 | 59.2164
32 | 1.6788 | 6.4365 | 61.5997
33 | 0 | 0 | 62.597
34 | 0 | 0 | 62.4948
35 | 0 | 0 | 62.3929
36 | 0.89932 | 0 | 61.656
37 | 0 | 0 | 61.4985
38 | 0 | 0 | 61.3989
39 | 0 | 0 | 61.2996
40 | 0 | 0 | 61.2005
41 | 0 | 0 | 61.1016
42 | 6.4267 | 6.8458 | 60.3854
43 | 12.9326 | 13.1275 | 60.5668
44 | 0 | 0 | 61.2738
45 | 1.3166 | 0 | 60.2452
46 | 0 | 0 | 60.0644
47 | 0 | 0 | 59.9682
48 | 0 | 0 | 59.8722
49 | 0 | 0 | 59.7764
50 | 0 | 0 | 59.6809
51 | 0 | 0 | 59.5856
52 | 0 | 0 | 59.4905
53 | 0 | 0 | 59.3956
54 | 12.5448 | 13.706 | 59.1729
55 | 1.2914 | 0 | 59.185
56 | 1.6802 | 6.4508 | 61.5757
57 | 0 | 0 | 62.5756
58 | 0 | 0 | 62.4735
59 | 0 | 0 | 62.3716
60 | 0.90017 | 0 | 61.6342
61 | 0 | 0 | 61.4767
62 | 0 | 0 | 61.3772
63 | 0 | 0 | 61.2778
64 | 0 | 0 | 61.1788
65 | 0 | 0 | 61.0799
66 | 6.4329 | 6.8475 | 60.361
67 | 12.944 | 13.1421 | 60.5419
68 | 0 | 0 | 61.2514
69 | 1.3179 | 0 | 60.222
70 | 0 | 0 | 60.0412
71 | 0 | 0 | 59.945
72 | 0 | 0 | 59.8491
73 | 0 | 0 | 59.7533
74 | 0 | 0 | 59.6578
75 | 0 | 0 | 59.5626
76 | 0 | 0 | 59.4675
77 | 0 | 0 | 59.3727
78 | 12.556 | 13.7082 | 59.1447
79 | 1.2924 | 0 | 59.1546
80 | 1.6815 | 6.4647 | 61.5524
81 | 0 | 0 | 62.5548
82 | 0 | 0 | 62.4528
83 | 0 | 0 | 62.3509
84 | 0.90101 | 0 | 61.613
85 | 0 | 0 | 61.4555
86 | 0 | 0 | 61.356
87 | 0 | 0 | 61.2567
88 | 0 | 0 | 61.1577
89 | 0 | 0 | 61.0589
90 | 6.4389 | 6.8492 | 60.3373
91 | 12.9552 | 13.1564 | 60.5177
92 | 0 | 0 | 61.2296
93 | 1.3191 | 0 | 60.1993
94 | 0 | 0 | 60.0185
95 | 0 | 0 | 59.9224
96 | 0 | 0 | 59.8265
97 | 0 | 0 | 59.7308
98 | 0 | 0 | 59.6354
99 | 0 | 0 | 59.5401
100 | 0 | 0 | 59.4451
101 | 0 | 0 | 59.3504
102 | 12.567 | 13.7103 | 59.1172
103 | 1.2935 | 0 | 59.1249
104 | 1.6829 | 6.4783 | 61.5296
105 | 0 | 0 | 62.5345
106 | 0 | 0 | 62.4325
107 | 0 | 0 | 62.3307
108 | 0.90184 | 0 | 61.5923
109 | 0 | 0 | 61.4348
110 | 0 | 0 | 61.3353
111 | 0 | 0 | 61.2361
112 | 0 | 0 | 61.1371
113 | 0 | 0 | 61.0384
114 | 6.4448 | 6.8508 | 60.3141
115 | 12.9662 | 13.1703 | 60.494
116 | 0 | 0 | 61.2081
117 | 1.3203 | 0 | 60.1771
118 | 0 | 0 | 59.9963
119 | 0 | 0 | 59.9002
120 | 0 | 0 | 59.8043
121 | 0 | 0 | 59.7087
122 | 0 | 0 | 59.6133
123 | 0 | 0 | 59.5182
124 | 0 | 0 | 59.4232
125 | 0 | 0 | 59.3285
126 | 12.5778 | 13.7125 | 59.0903
127 | 1.2944 | 0 | 59.0958
128 | 1.6842 | 6.4916 | 61.5073
129 | 0 | 0 | 62.5147
130 | 0 | 0 | 62.4127
131 | 0 | 0 | 62.311
132 | 0.90265 | 0 | 61.572
133 | 0 | 0 | 61.4145
134 | 0 | 0 | 61.3151
135 | 0 | 0 | 61.2159
136 | 0 | 0 | 61.117
137 | 0 | 0 | 61.0183
138 | 6.4506 | 6.8524 | 60.2914
139 | 12.977 | 13.184 | 60.4708
140 | 0 | 0 | 61.1872
141 | 1.3215 | 0 | 60.1553
142 | 0 | 0 | 59.9745
143 | 0 | 0 | 59.8785
144 | 0 | 0 | 59.7827
145 | 0 | 0 | 59.6871
146 | 0 | 0 | 59.5918
147 | 0 | 0 | 59.4967
148 | 0 | 0 | 59.4018
149 | 0 | 0 | 59.3071
150 | 12.5883 | 13.7145 | 59.064
151 | 1.2954 | 0 | 59.0673
152 | 1.6854 | 6.5046 | 61.4855
153 | 0 | 0 | 62.4952
154 | 0 | 0 | 62.3933
155 | 0 | 0 | 62.2916
156 | 0.90343 | 0 | 61.5521
157 | 0 | 0 | 61.3946
158 | 0 | 0 | 61.2952
159 | 0 | 0 | 61.1961
160 | 0 | 0 | 61.0973
161 | 0 | 0 | 60.9986
162 | 6.4563 | 6.854 | 60.2692
163 | 12.9875 | 13.1973 | 60.4481
164 | 0 | 0 | 61.1667
165 | 1.3226 | 0 | 60.1341
166 | 0 | 0 | 59.9532
167 | 0 | 0 | 59.8572
168 | 0 | 0 | 59.7615
169 | 0 | 0 | 59.666
170 | 0 | 0 | 59.5707
171 | 0 | 0 | 59.4756
172 | 0 | 0 | 59.3808
173 | 0 | 0 | 59.2861
174 | 12.5986 | 13.7166 | 59.0382
175 | 1.2964 | 0 | 59.0394
176 | 1.6867 | 6.5173 | 61.4641
177 | 0 | 0 | 62.4762
178 | 0 | 0 | 62.3743
179 | 0 | 0 | 62.2727
180 | 0.90421 | 0 | 61.5327
181 | 0 | 0 | 61.3752
182 | 0 | 0 | 61.2759
183 | 0 | 0 | 61.1768
184 | 0 | 0 | 61.078
185 | 0 | 0 | 60.9794
186 | 6.4618 | 6.8555 | 60.2475
187 | 12.9978 | 13.2104 | 60.4259
188 | 0 | 0 | 61.1466
189 | 1.3238 | 0 | 60.1133
190 | 0 | 0 | 59.9324
191 | 0 | 0 | 59.8365
192 | 0 | 0 | 59.7408
193 | 0 | 0 | 59.6453
194 | 0 | 0 | 59.5501
195 | 0 | 0 | 59.455
196 | 0 | 0 | 59.3602
197 | 0 | 0 | 59.2657
198 | 12.6086 | 13.7185 | 59.013
199 | 1.2973 | 0 | 59.0122
200 | 1.6879 | 6.5297 | 61.4432
201 | 0 | 0 | 62.4576
202 | 0 | 0 | 62.3558
203 | 0 | 0 | 62.2542
204 | 0.90496 | 0 | 61.5137
205 | 0 | 0 | 61.3562
206 | 0 | 0 | 61.2569
207 | 0 | 0 | 61.1579
208 | 0 | 0 | 61.0591
209 | 0 | 0 | 60.9605
210 | 6.4672 | 6.857 | 60.2263
211 | 13.0078 | 13.2231 | 60.4042
212 | 0 | 0 | 61.127
213 | 1.3249 | 0 | 60.093
214 | 0 | 0 | 59.9121
215 | 0 | 0 | 59.8162
216 | 0 | 0 | 59.7205
217 | 0 | 0 | 59.6251
218 | 0 | 0 | 59.5299
219 | 0 | 0 | 59.4349
220 | 0 | 0 | 59.3402
221 | 0 | 0 | 59.2457
222 | 12.6184 | 19.0693 | 60.7312
223 | 1.4013 | 0 | 63.0231
224 | 1.823 | 0 | 61.5422
225 | 0 | 0 | 61.3261
226 | 0 | 0 | 61.227
227 | 0 | 0 | 61.128
228 | 0.88715 | 0 | 60.403
229 | 0 | 0 | 60.2493
230 | 0 | 0 | 60.1526
231 | 0 | 0 | 60.0562
232 | 0 | 0 | 59.96
233 | 0 | 0 | 59.864
234 | 6.3469 | 7.077 | 59.3029
235 | 12.8387 | 13.4335 | 59.7695
236 | 0 | 0 | 60.5901
237 | 1.313 | 0 | 59.5659
238 | 0 | 0 | 59.387
239 | 0 | 0 | 59.2924
240 | 0 | 0 | 59.198
241 | 0 | 0 | 59.1038
242 | 0 | 0 | 59.0098
243 | 0 | 0 | 58.916
244 | 0 | 0 | 58.8225
245 | 0 | 0 | 58.7292
246 | 12.5154 | 19.265 | 60.3427
247 | 1.3957 | 0 | 62.7418
248 | 1.8156 | 0 | 61.2673
249 | 0 | 0 | 61.0523
250 | 0 | 0 | 60.9538
251 | 0 | 0 | 60.8555
252 | 0.8836 | 0 | 60.1337
253 | 0 | 0 | 59.9808
254 | 0 | 0 | 59.8848
255 | 0 | 0 | 59.789
256 | 0 | 0 | 59.6934
257 | 0 | 0 | 59.598
258 | 6.533 | 6.8512 | 59.7175
259 | 12.7375 | 13.6298 | 59.362
260 | 0 | 0 | 60.2367
261 | 1.3057 | 0 | 59.2187
262 | 0 | 0 | 59.041
263 | 0 | 0 | 58.9472
264 | 0 | 0 | 58.8536
265 | 0 | 0 | 58.7602
266 | 0 | 0 | 58.6671
267 | 0 | 0 | 58.5741
268 | 0 | 0 | 58.4814
269 | 0 | 0 | 58.3889
270 | 12.4505 | 19.3856 | 60.0783
271 | 1.3922 | 0 | 62.5475
272 | 1.8111 | 0 | 61.0769
273 | 0 | 0 | 60.8627
274 | 0 | 0 | 60.7646
275 | 0 | 0 | 60.6667
276 | 0.88143 | 0 | 59.947
277 | 0 | 0 | 59.7947
278 | 0 | 0 | 59.6991
279 | 0 | 0 | 59.6037
280 | 0 | 0 | 59.5086
281 | 0 | 0 | 59.4137
282 | 6.5207 | 6.9087 | 59.5743
283 | 12.7214 | 13.6303 | 59.2419
284 | 0 | 0 | 60.1198
285 | 1.3042 | 0 | 59.1031
286 | 0 | 0 | 58.9259
287 | 0 | 0 | 58.8323
288 | 0 | 0 | 58.739
289 | 0 | 0 | 58.6459
290 | 0 | 0 | 58.553
291 | 0 | 0 | 58.4603
292 | 0 | 0 | 58.3678
293 | 0 | 0 | 58.2756
294 | 12.4376 | 19.4294 | 59.9867
295 | 1.3919 | 0 | 62.4783
296 | 1.8107 | 0 | 61.0083
297 | 0 | 0 | 60.7943
298 | 0 | 0 | 60.6963
299 | 0 | 0 | 60.5986
300 | 0.88124 | 0 | 59.8792
301 | 0 | 0 | 59.7271
302 | 0 | 0 | 59.6316
303 | 0 | 0 | 59.5364
304 | 0 | 0 | 59.4414
305 | 0 | 0 | 59.3467
306 | 6.5197 | 6.9123 | 59.5101
307 | 12.72 | 13.6299 | 59.1793
308 | 0 | 0 | 60.0575
309 | 1.3041 | 0 | 59.041
310 | 0 | 0 | 58.864
311 | 0 | 0 | 58.7705
312 | 0 | 0 | 58.6773
313 | 0 | 0 | 58.5844
314 | 0 | 0 | 58.4916
315 | 0 | 0 | 58.3991
316 | 0 | 0 | 58.3068
317 | 0 | 0 | 58.2146
318 | 12.4364 | 19.4554 | 59.9349
319 | 1.3923 | 0 | 62.4381
320 | 1.8112 | 0 | 60.9679
321 | 0 | 0 | 60.7539
322 | 0 | 0 | 60.656
323 | 0 | 0 | 60.5584
324 | 0.8815 | 0 | 59.8389
325 | 0 | 0 | 59.6869
326 | 0 | 0 | 59.5915
327 | 0 | 0 | 59.4964
328 | 0 | 0 | 59.4015
329 | 0 | 0 | 59.3068
330 | 6.5217 | 6.9146 | 59.4706
331 | 12.7237 | 13.6301 | 59.1379
332 | 0 | 0 | 60.0155
333 | 1.3044 | 0 | 58.9989
334 | 0 | 0 | 58.8219
335 | 0 | 0 | 58.7286
336 | 0 | 0 | 58.6355
337 | 0 | 0 | 58.5426
338 | 0 | 0 | 58.45
339 | 0 | 0 | 58.3575
340 | 0 | 0 | 58.2653
341 | 0 | 0 | 58.1733
342 | 12.4393 | 19.4745 | 59.8982
343 | 1.3929 | 0 | 62.4089
344 | 1.8121 | 0 | 60.9381
345 | 0 | 0 | 60.7241
346 | 0 | 0 | 60.6264
347 | 0 | 0 | 60.5288
348 | 0.88191 | 0 | 59.8091
349 | 0 | 0 | 59.6571
350 | 0 | 0 | 59.5618
351 | 0 | 0 | 59.4668
352 | 0 | 0 | 59.3719
353 | 0 | 0 | 59.2773
354 | 6.5248 | 6.9165 | 59.4405
355 | 12.7292 | 13.6306 | 59.1046
356 | 0 | 0 | 59.9814
357 | 1.3049 | 0 | 58.9646
358 | 0 | 0 | 58.7876
359 | 0 | 0 | 58.6944
360 | 0 | 0 | 58.6014
361 | 0 | 0 | 58.5086
362 | 0 | 0 | 58.416
363 | 0 | 0 | 58.3236
364 | 0 | 0 | 58.2315
365 | 0 | 0 | 58.1396
366 | 12.4437 | 19.491 | 59.8674
367 | 1.3936 | 0 | 62.3841
368 | 1.813 | 0 | 60.9126
369 | 0 | 0 | 60.6987
370 | 0 | 0 | 60.601
371 | 0 | 0 | 60.5035
372 | 0.88236 | 0 | 59.7835
373 | 0 | 0 | 59.6315
374 | 0 | 0 | 59.5363
375 | 0 | 0 | 59.4413
376 | 0 | 0 | 59.3466
377 | 0 | 0 | 59.252
378 | 6.5281 | 6.9182 | 59.4143
379 | 12.7352 | 13.6311 | 59.0749
380 | 0 | 0 | 59.9508
381 | 1.3055 | 0 | 58.9337
382 | 0 | 0 | 58.7567
383 | 0 | 0 | 58.6636
384 | 0 | 0 | 58.5706
385 | 0 | 0 | 58.4779
386 | 0 | 0 | 58.3854
387 | 0 | 0 | 58.2931
388 | 0 | 0 | 58.201
389 | 0 | 0 | 58.1092
390 | 12.4484 | 19.5061 | 59.8393
391 | 1.3943 | 0 | 62.3613
392 | 1.8139 | 0 | 60.8892
393 | 0 | 0 | 60.6753
394 | 0 | 0 | 60.5776
395 | 0 | 0 | 60.4802
396 | 0.88282 | 0 | 59.7599
397 | 0 | 0 | 59.608
398 | 0 | 0 | 59.5128
399 | 0 | 0 | 59.4179
400 | 0 | 0 | 59.3232
401 | 0 | 0 | 59.2287
402 | 6.5315 | 6.9197 | 59.3899
403 | 12.7412 | 13.6316 | 59.047
404 | 0 | 0 | 59.922
405 | 1.306 | 0 | 58.9045
406 | 0 | 0 | 58.7277
407 | 0 | 0 | 58.6346
408 | 0 | 0 | 58.5417
409 | 0 | 0 | 58.449
410 | 0 | 0 | 58.3566
411 | 0 | 0 | 58.2644
412 | 0 | 0 | 58.1724
413 | 0 | 0 | 58.0806
414 | 12.4531 | 19.5205 | 59.8127
415 | 1.395 | 0 | 62.3397
416 | 1.8148 | 0 | 60.867
417 | 0 | 0 | 60.653
418 | 0 | 0 | 60.5554
419 | 0 | 0 | 60.458
420 | 0.88327 | 0 | 59.7375
421 | 0 | 0 | 59.5856
422 | 0 | 0 | 59.4905
423 | 0 | 0 | 59.3956
424 | 0 | 0 | 59.301
425 | 0 | 0 | 59.2065
426 | 6.5348 | 6.9212 | 59.3668
427 | 12.7471 | 18.985 | 60.7644
428 | 0 | 0 | 64.0095
429 | 1.4095 | 0 | 62.9077
430 | 0 | 0 | 62.7147
431 | 0 | 0 | 62.6122
432 | 0 | 0 | 62.51
433 | 0 | 0 | 62.4081
434 | 0 | 0 | 62.3063
435 | 0 | 0 | 62.2048
436 | 0 | 0 | 62.1036
437 | 0 | 0 | 62.0026
438 | 12.72 | 13.6744 | 59.8843
439 | 1.3763 | 0 | 61.5582
440 | 1.7904 | 0 | 60.1062
441 | 0 | 0 | 59.8956
442 | 0 | 0 | 59.7998
443 | 0 | 0 | 59.7042
444 | 0.87146 | 0 | 58.994
445 | 0 | 0 | 58.8445
446 | 0 | 0 | 58.7512
447 | 0 | 0 | 58.658
448 | 0 | 0 | 58.5651
449 | 0 | 0 | 58.4724
450 | 6.454 | 6.9547 | 58.7009
451 | 12.6093 | 19.2071 | 60.2701
452 | 0 | 0 | 63.6434
453 | 1.4016 | 0 | 62.5483
454 | 0 | 0 | 62.3566
455 | 0 | 0 | 62.255
456 | 0 | 0 | 62.1536
457 | 0 | 0 | 62.0525
458 | 0 | 0 | 61.9516
459 | 0 | 0 | 61.851
460 | 0 | 0 | 61.7505
461 | 0 | 0 | 61.6504
462 | 12.6504 | 13.6856 | 59.5794
463 | 1.3702 | 0 | 61.274
464 | 1.7825 | 0 | 59.8288
465 | 0 | 0 | 59.6194
466 | 0 | 0 | 59.5242
467 | 0 | 0 | 59.4293
468 | 0.86764 | 0 | 58.7225
469 | 0 | 0 | 58.574
470 | 0 | 0 | 58.4812
471 | 0 | 0 | 58.3887
472 | 0 | 0 | 58.2964
473 | 0 | 0 | 58.2043
474 | 6.4274 | 6.9577 | 58.4506
475 | 12.5634 | 19.2947 | 60.08
476 | 0 | 0 | 63.5018
477 | 1.3992 | 0 | 62.4088
478 | 0 | 0 | 62.2176
479 | 0 | 0 | 62.1163
480 | 0 | 0 | 62.0153
481 | 0 | 0 | 61.9145
482 | 0 | 0 | 61.8139
483 | 0 | 0 | 61.7136
484 | 0 | 0 | 61.6135
485 | 0 | 0 | 61.5136
486 | 12.6294 | 13.6905 | 59.4578
487 | 1.3683 | 0 | 61.1592
488 | 1.7802 | 0 | 59.7161
489 | 0 | 0 | 59.5071
490 | 0 | 0 | 59.4122
491 | 0 | 0 | 59.3175
492 | 0.86651 | 0 | 58.6118
493 | 0 | 0 | 58.4636
494 | 0 | 0 | 58.3711
495 | 0 | 0 | 58.2788
496 | 0 | 0 | 58.1868
497 | 0 | 0 | 58.095
498 | 6.4196 | 6.9577 | 58.3461
499 | 12.5499 | 19.334 | 59.9975
500 | 0 | 0 | 63.4397
501 | 1.3987 | 0 | 62.3472
502 | 0 | 0 | 62.1562
503 | 0 | 0 | 62.055
504 | 0 | 0 | 61.9541
505 | 0 | 0 | 61.8535
506 | 0 | 0 | 61.753
507 | 0 | 0 | 61.6529
508 | 0 | 0 | 61.5529
509 | 0 | 0 | 61.4532
510 | 13.0353 | 13.7279 | 60.044
511 | 1.3607 | 0 | 60.8189
512 | 1.7703 | 0 | 59.3842
513 | 0 | 0 | 59.1766
514 | 0 | 0 | 59.0825
515 | 0 | 0 | 58.9886
516 | 0.86173 | 0 | 58.2871
517 | 0 | 0 | 58.14
518 | 0 | 0 | 58.0483
519 | 0 | 6.3451 | 61.6483
520 | 0 | 0 | 62.7355
521 | 0 | 0 | 62.633
522 | 6.6348 | 6.6444 | 60.8404
523 | 12.8666 | 13.3844 | 60.2139
524 | 0 | 0 | 62.7246
525 | 1.3819 | 0 | 61.646
526 | 0 | 0 | 61.4577
527 | 0 | 0 | 61.3582
528 | 0 | 0 | 61.2589
529 | 0 | 0 | 61.1599
530 | 0 | 0 | 61.0611
531 | 0 | 0 | 60.9626
532 | 0 | 0 | 60.8642
533 | 0 | 0 | 60.7661
534 | 13.1004 | 13.5136 | 60.107
535 | 1.3393 | 0 | 59.9408
536 | 1.7425 | 0 | 58.5297
537 | 0 | 0 | 58.3259
538 | 0 | 0 | 58.2338
539 | 0 | 0 | 58.1418
540 | 0.84828 | 6.6408 | 61.3147
541 | 0 | 0 | 62.4035
542 | 0 | 0 | 62.3018
543 | 0 | 0 | 62.2003
544 | 0 | 0 | 62.0991
545 | 0 | 0 | 61.9981
546 | 6.5634 | 6.8319 | 60.3099
547 | 12.7768 | 13.5154 | 59.877
548 | 0 | 0 | 62.4623
549 | 1.3763 | 0 | 61.3883
550 | 0 | 0 | 61.201
551 | 0 | 0 | 61.1021
552 | 0 | 0 | 61.0034
553 | 0 | 0 | 60.905
554 | 0 | 0 | 60.8068
555 | 0 | 0 | 60.7088
556 | 0 | 0 | 60.6111
557 | 0 | 0 | 60.5136
558 | 13.0548 | 13.5898 | 59.9184
559 | 1.3363 | 0 | 59.7851
560 | 1.7386 | 0 | 58.3773
561 | 0 | 0 | 58.1742
562 | 0 | 0 | 58.0824
563 | 0 | 6.3659 | 60.0632
564 | 0.92833 | 0 | 62.1334
565 | 0 | 0 | 61.9729
566 | 0 | 0 | 61.8722
567 | 0 | 0 | 61.7718
568 | 0 | 0 | 61.6715
569 | 0 | 0 | 61.5715
570 | 6.5169 | 6.9014 | 59.9343
571 | 12.7087 | 13.5106 | 59.5796
572 | 0 | 0 | 62.1762
573 | 1.3701 | 0 | 61.1073
574 | 0 | 0 | 60.9211
575 | 0 | 0 | 60.8229
576 | 0 | 0 | 60.7249
577 | 0 | 0 | 60.6271
578 | 0 | 0 | 60.5295
579 | 0 | 0 | 60.4322
580 | 0 | 0 | 60.3351
581 | 0 | 0 | 60.2383
582 | 13.0002 | 13.5872 | 59.6745
583 | 1.3314 | 0 | 59.5545
584 | 1.7322 | 0 | 58.1523
585 | 0 | 6.3518 | 62.4588
586 | 0 | 0 | 62.732
587 | 0 | 0 | 62.6295
588 | 0.92456 | 0 | 61.8742
589 | 0 | 0 | 61.7146
590 | 0 | 0 | 61.6145
591 | 0 | 0 | 61.5146
592 | 0 | 0 | 61.415
593 | 0 | 0 | 61.3156
594 | 6.6053 | 6.8435 | 60.4939
595 | 13.2446 | 13.2012 | 60.4939
596 | 0 | 0 | 61.1645
597 | 1.3457 | 0 | 60.1157
598 | 0 | 0 | 59.9333
599 | 0 | 0 | 59.8374
600 | 0 | 0 | 59.7417
601 | 0 | 0 | 59.6463
602 | 0 | 0 | 59.551
603 | 0 | 0 | 59.456
604 | 0 | 0 | 59.3612
605 | 0 | 0 | 59.2666
606 | 12.8006 | 19.1331 | 60.6694
607 | 1.4188 | 0 | 62.9406
608 | 1.8457 | 0 | 61.4428
609 | 0 | 0 | 61.2255
610 | 0 | 0 | 61.1265
611 | 0 | 0 | 61.0278
612 | 0.89833 | 0 | 60.2952
613 | 0 | 0 | 60.141
614 | 0 | 0 | 60.0446
615 | 0 | 0 | 59.9484
616 | 0 | 0 | 59.8524
617 | 0 | 0 | 59.7567
618 | 6.4268 | 7.0917 | 59.1561
619 | 12.9798 | 13.4455 | 59.5363
620 | 0 | 0 | 60.3343
621 | 1.3258 | 0 | 59.3018
622 | 0 | 0 | 59.1227
623 | 0 | 0 | 59.0287
624 | 0 | 0 | 58.9349
625 | 0 | 0 | 58.8413
626 | 0 | 0 | 58.7479
627 | 0 | 0 | 58.6548
628 | 0 | 0 | 58.5619
629 | 0 | 0 | 58.4692
630 | 12.6268 | 19.4238 | 60.0719
631 | 1.4086 | 0 | 62.5097
632 | 1.8325 | 0 | 61.0231
633 | 0 | 0 | 60.8076
634 | 0 | 0 | 60.7097
635 | 0 | 0 | 60.6119
636 | 0.89193 | 0 | 59.8849
637 | 0 | 0 | 59.7321
638 | 0 | 0 | 59.6366
639 | 0 | 0 | 59.5414
640 | 0 | 0 | 59.4464
641 | 0 | 0 | 59.3516
642 | 6.5959 | 6.9181 | 59.4742
643 | 12.8532 | 13.644 | 59.0598
644 | 0 | 0 | 59.917
645 | 1.3162 | 0 | 58.8923
646 | 0 | 0 | 58.7148
647 | 0 | 0 | 58.6217
648 | 0 | 0 | 58.5289
649 | 0 | 0 | 58.4363
650 | 0 | 0 | 58.3439
651 | 0 | 0 | 58.2517
652 | 0 | 0 | 58.1597
653 | 0 | 0 | 58.0679
654 | 12.5416 | 19.5625 | 59.764
655 | 1.4037 | 0 | 62.2852
656 | 1.8261 | 0 | 60.8041
657 | 0 | 0 | 60.5896
658 | 0 | 0 | 60.4921
659 | 0 | 0 | 60.3949
660 | 0.88883 | 0 | 59.6706
661 | 0 | 0 | 59.5185
662 | 0 | 0 | 59.4235
663 | 0 | 0 | 59.3288
664 | 0 | 0 | 59.2343
665 | 0 | 0 | 59.14
666 | 6.5747 | 6.928 | 59.2812
667 | 12.8173 | 19.0538 | 60.6556
668 | 0 | 0 | 63.9168
669 | 1.4171 | 0 | 62.8099
670 | 0 | 0 | 62.6166
671 | 0 | 0 | 62.5144
672 | 0 | 0 | 62.4124
673 | 0 | 0 | 62.3107
674 | 0 | 0 | 62.2092
675 | 0 | 0 | 62.1079
676 | 0 | 0 | 62.0069
677 | 0 | 0 | 61.9061
678 | 12.785 | 13.6857 | 59.7552
679 | 1.3823 | 0 | 61.4167
680 | 1.7983 | 0 | 59.9591
681 | 0 | 0 | 59.7484
682 | 0 | 0 | 59.6529
683 | 0 | 0 | 59.5576
684 | 0.87534 | 0 | 58.8451
685 | 0 | 0 | 58.6958
686 | 0 | 0 | 58.6028
687 | 0 | 0 | 58.51
688 | 0 | 0 | 58.4174
689 | 0 | 0 | 58.325
690 | 6.4821 | 6.9623 | 58.5419
691 | 12.6591 | 19.2984 | 60.1091
692 | 0 | 0 | 63.5128
693 | 1.4077 | 0 | 62.4137
694 | 0 | 0 | 62.2219
695 | 0 | 0 | 62.1206
696 | 0 | 0 | 62.0196
697 | 0 | 0 | 61.9188
698 | 0 | 0 | 61.8182
699 | 0 | 0 | 61.7178
700 | 0 | 0 | 61.6177
701 | 0 | 0 | 61.5179
702 | 12.7032 | 13.6975 | 59.4219
703 | 1.3751 | 0 | 61.1073
704 | 1.789 | 0 | 59.6578
705 | 0 | 0 | 59.4483
706 | 0 | 0 | 59.3536
707 | 0 | 0 | 59.259
708 | 0.87082 | 0 | 58.5504
709 | 0 | 0 | 58.4021
710 | 0 | 0 | 58.3098
711 | 0 | 0 | 58.2176
712 | 0 | 0 | 58.1257
713 | 0 | 0 | 58.0341
714 | 6.6463 | 6.7684 | 58.8944
715 | 13.2842 | 19.6214 | 60.8868
716 | 0 | 0 | 62.71
717 | 1.3883 | 0 | 61.6267
718 | 0 | 0 | 61.4381
719 | 0 | 0 | 61.3387
720 | 0 | 0 | 61.2394
721 | 0 | 0 | 61.1405
722 | 0 | 0 | 61.0417
723 | 0 | 0 | 60.9432
724 | 0 | 0 | 60.8449
725 | 0 | 0 | 60.7468
726 | 13.1564 | 13.5388 | 60.0665
727 | 1.3447 | 0 | 59.8941
728 | 1.7496 | 0 | 58.4777
729 | 0 | 0 | 58.2736
730 | 0 | 0 | 58.1816
731 | 0 | 0 | 58.0898
732 | 0.85175 | 6.6673 | 61.2757
733 | 0 | 0 | 62.3693
734 | 0 | 0 | 62.2677
735 | 0 | 0 | 62.1663
736 | 0 | 0 | 62.0651
737 | 0 | 0 | 61.9642
738 | 6.5906 | 6.8362 | 60.2618
739 | 12.8248 | 13.5197 | 59.7995
740 | 0 | 0 | 62.3775
741 | 1.3807 | 0 | 61.3006
742 | 0 | 0 | 61.1132
743 | 0 | 0 | 61.0145
744 | 0 | 0 | 60.9161
745 | 0 | 0 | 60.8178
746 | 0 | 0 | 60.7199
747 | 0 | 0 | 60.6221
748 | 0 | 0 | 60.5246
749 | 0 | 0 | 60.4273
750 | 13.0917 | 13.5938 | 59.8129
751 | 1.3397 | 0 | 59.6716
752 | 1.743 | 0 | 58.2609
753 | 0 | 0 | 58.0577
754 | 0 | 6.3579 | 61.6651
755 | 0 | 0 | 62.7547
756 | 0.93014 | 0 | 61.9951
757 | 0 | 0 | 61.8348
758 | 0 | 0 | 61.7344
759 | 0 | 0 | 61.6343
760 | 0 | 0 | 61.5344
761 | 0 | 0 | 61.4347
762 | 6.6445 | 6.8325 | 60.5848
763 | 13.3105 | 13.1887 | 60.5299
764 | 0 | 0 | 61.1841
765 | 1.3514 | 0 | 60.1312
766 | 0 | 0 | 59.9485
767 | 0 | 0 | 59.8525
768 | 0 | 0 | 59.7568
769 | 0 | 0 | 59.6613
770 | 0 | 0 | 59.566
771 | 0 | 0 | 59.471
772 | 0 | 0 | 59.3761
773 | 0 | 0 | 59.2815
774 | 12.8491 | 19.1458 | 60.6607
775 | 1.4234 | 0 | 62.9246
776 | 1.8517 | 0 | 61.4223
777 | 0 | 0 | 61.2047
778 | 0 | 0 | 61.1058
779 | 0 | 0 | 61.0071
780 | 0.90126 | 0 | 60.2725
781 | 0 | 0 | 60.1181
782 | 0 | 0 | 60.0218
783 | 0 | 0 | 59.9257
784 | 0 | 0 | 59.8298
785 | 0 | 0 | 59.7341
786 | 6.6561 | 6.8098 | 59.7573
787 | 12.9483 | 13.6498 | 59.2584
788 | 0 | 0 | 60.0992
789 | 1.3248 | 0 | 59.068
790 | 0 | 0 | 58.8895
791 | 0 | 0 | 58.7961
792 | 0 | 0 | 58.7028
793 | 0 | 0 | 58.6098
794 | 0 | 0 | 58.517
795 | 0 | 0 | 58.4244
796 | 0 | 0 | 58.332
797 | 0 | 0 | 58.2398
798 | 12.6162 | 19.5187 | 59.8795
799 | 1.4095 | 0 | 62.3614
800 | 1.8337 | 0 | 60.8744
801 | 0 | 0 | 60.6592
802 | 0 | 0 | 60.5616
803 | 0 | 0 | 60.4642
804 | 0.89252 | 0 | 59.7372
805 | 0 | 0 | 59.5847
806 | 0 | 0 | 59.4896
807 | 0 | 0 | 59.3947
808 | 0 | 0 | 59.3
809 | 0 | 0 | 59.2056
810 | 6.6007 | 6.9265 | 59.3305
811 | 12.8625 | 19.0533 | 60.6741
812 | 0 | 0 | 63.9257
813 | 1.4211 | 0 | 62.816
814 | 0 | 0 | 62.6224
815 | 0 | 0 | 62.5202
816 | 0 | 0 | 62.4182
817 | 0 | 0 | 62.3165
818 | 0 | 0 | 62.2149
819 | 0 | 0 | 62.1137
820 | 0 | 0 | 62.0126
821 | 0 | 0 | 61.9118
822 | 12.8186 | 13.6887 | 59.7425
823 | 1.3853 | 0 | 61.3966
824 | 1.8023 | 0 | 59.9361
825 | 0 | 0 | 59.7252
826 | 0 | 0 | 59.6298
827 | 0 | 0 | 59.5346
828 | 0.87731 | 0 | 58.8207
829 | 0 | 0 | 58.6713
830 | 0 | 0 | 58.5784
831 | 0 | 0 | 58.4856
832 | 0 | 0 | 58.3931
833 | 0 | 0 | 58.3008
834 | 6.4962 | 6.9639 | 58.5105
835 | 12.6838 | 19.3233 | 60.0696
836 | 0 | 0 | 63.4793
837 | 1.4104 | 0 | 62.3783
838 | 0 | 0 | 62.1865
839 | 0 | 0 | 62.0853
840 | 0 | 0 | 61.9843
841 | 0 | 0 | 61.8836
842 | 0 | 0 | 61.7831
843 | 0 | 0 | 61.6828
844 | 0 | 0 | 61.5828
845 | 0 | 0 | 61.483
846 | 13.3374 | 13.259 | 60.5626
847 | 1.3568 | 0 | 60.2642
848 | 1.7653 | 0 | 58.8349
849 | 0 | 0 | 58.629
850 | 0 | 0 | 58.5361
851 | 0 | 0 | 58.4435
852 | 0.85938 | 6.4988 | 61.5256
853 | 0 | 0 | 62.5868
854 | 0 | 0 | 62.4846
855 | 0 | 0 | 62.3827
856 | 0 | 0 | 62.2811
857 | 0 | 0 | 62.1796
858 | 6.6289 | 6.8281 | 60.4517
859 | 12.8896 | 13.5267 | 59.9431
860 | 0 | 0 | 62.5112
861 | 1.3866 | 0 | 61.4298
862 | 0 | 0 | 61.2417
863 | 0 | 0 | 61.1428
864 | 0 | 0 | 61.044
865 | 0 | 0 | 60.9455
866 | 0 | 0 | 60.8472
867 | 0 | 0 | 60.7491
868 | 0 | 0 | 60.6513
869 | 0 | 0 | 60.5537
870 | 13.1421 | 13.5945 | 59.9096
871 | 1.3442 | 0 | 59.756
872 | 1.7489 | 0 | 58.3406
873 | 0 | 0 | 58.1369
874 | 0 | 0 | 58.0452
875 | 0 | 6.3611 | 62.469
876 | 0.93324 | 0 | 62.0835
877 | 0 | 0 | 61.9228
878 | 0 | 0 | 61.8223
879 | 0 | 0 | 61.7219
880 | 0 | 0 | 61.6218
881 | 0 | 0 | 61.5219
882 | 6.5518 | 6.9109 | 59.8677
883 | 12.771 | 13.5163 | 59.4768
884 | 0 | 0 | 62.0639
885 | 1.3758 | 0 | 60.9914
886 | 0 | 0 | 60.805
887 | 0 | 0 | 60.7071
888 | 0 | 0 | 60.6093
889 | 0 | 0 | 60.5118
890 | 0 | 0 | 60.4146
891 | 0 | 0 | 60.3175
892 | 0 | 0 | 60.2207
893 | 0 | 0 | 60.1241
894 | 13.0469 | 13.5919 | 59.5359
895 | 1.3356 | 0 | 59.4058
896 | 1.7378 | 6.3822 | 61.7127
897 | 0 | 0 | 62.6959
898 | 0 | 0 | 62.5935
899 | 0 | 0 | 62.4913
900 | 0.92753 | 0 | 61.7343
901 | 0 | 0 | 61.5748
902 | 0 | 0 | 61.475
903 | 0 | 0 | 61.3755
904 | 0 | 0 | 61.2762
905 | 0 | 0 | 61.1771
906 | 6.6269 | 6.8585 | 60.35
907 | 13.2869 | 13.2773 | 60.3613
908 | 0 | 0 | 61.0478
909 | 1.3507 | 0 | 59.9958
910 | 0 | 0 | 59.8134
911 | 0 | 0 | 59.7178
912 | 0 | 0 | 59.6224
913 | 0 | 0 | 59.5272
914 | 0 | 0 | 59.4322
915 | 0 | 0 | 59.3375
916 | 0 | 0 | 59.243
917 | 0 | 0 | 59.1487
918 | 12.8414 | 19.2051 | 60.5536
919 | 1.4238 | 0 | 62.8434
920 | 1.8522 | 0 | 61.341
921 | 0 | 0 | 61.1235
922 | 0 | 0 | 61.0248
923 | 0 | 0 | 60.9263
924 | 0.90152 | 0 | 60.1917
925 | 0 | 0 | 60.0375
926 | 0 | 0 | 59.9414
927 | 0 | 0 | 59.8454
928 | 0 | 0 | 59.7497
929 | 0 | 0 | 59.6542
930 | 6.6599 | 6.8489 | 59.6983
931 | 12.9586 | 13.6527 | 59.2016
932 | 0 | 0 | 60.0413
933 | 1.3258 | 0 | 59.0095
934 | 0 | 0 | 58.8311
935 | 0 | 0 | 58.7378
936 | 0 | 0 | 58.6447
937 | 0 | 0 | 58.5518
938 | 0 | 0 | 58.4591
939 | 0 | 0 | 58.3666
940 | 0 | 0 | 58.2744
941 | 0 | 0 | 58.1823
942 | 12.6226 | 19.5463 | 59.8275
943 | 1.4106 | 0 | 62.3197
944 | 1.8351 | 0 | 60.8317
945 | 0 | 0 | 60.6165
946 | 0 | 0 | 60.519
947 | 0 | 0 | 60.4217
948 | 0.89323 | 0 | 59.6943
949 | 0 | 0 | 59.5418
950 | 0 | 0 | 59.4468
951 | 0 | 0 | 59.352
952 | 0 | 0 | 59.2575
953 | 0 | 0 | 59.1631
954 | 6.606 | 6.9293 | 59.2867
955 | 12.8719 | 19.0764 | 60.6321
956 | 0 | 0 | 63.892
957 | 1.4224 | 0 | 62.7815
958 | 0 | 0 | 62.5879
959 | 0 | 0 | 62.4858
960 | 0 | 0 | 62.3839
961 | 0 | 0 | 62.2822
962 | 0 | 0 | 62.1808
963 | 0 | 0 | 62.0796
964 | 0 | 0 | 61.9786
965 | 0 | 0 | 61.8779
966 | 12.8278 | 13.6914 | 59.7045
967 | 1.3862 | 0 | 61.3572
968 | 1.8034 | 0 | 59.8959
969 | 0 | 0 | 59.685
970 | 0 | 0 | 59.5897
971 | 0 | 0 | 59.4946
972 | 0.87787 | 0 | 58.7804
973 | 0 | 0 | 58.6311
974 | 0 | 0 | 58.5382
975 | 0 | 0 | 58.4456
976 | 0 | 0 | 58.3531
977 | 0 | 0 | 58.2609
978 | 6.5003 | 6.9646 | 58.4687
979 | 12.691 | 19.3447 | 60.0301
980 | 0 | 0 | 63.4479
981 | 1.4115 | 0 | 62.3463
982 | 0 | 0 | 62.1545
983 | 0 | 0 | 62.0533
984 | 0 | 0 | 61.9524
985 | 0 | 0 | 61.8518
986 | 0 | 0 | 61.7514
987 | 0 | 0 | 61.6512
988 | 0 | 0 | 61.5512
989 | 0 | 0 | 61.4515
990 | 13.3452 | 13.2764 | 60.5348
991 | 1.3578 | 0 | 60.2394
992 | 1.7665 | 0 | 58.8093
993 | 0 | 0 | 58.6033
994 | 0 | 0 | 58.5105
995 | 0 | 0 | 58.418
996 | 0.86 | 6.5114 | 61.507
997 | 0 | 0 | 62.5705
998 | 0 | 0 | 62.4684
999 | 0 | 0 | 62.3666
1000 | 0 | 0 | 62.2649
1001 | 0 | 0 | 62.1635
1002 | 6.6345 | 6.8295 | 60.4328
1003 | 12.8996 | 13.5275 | 59.9184
1004 | 0 | 0 | 62.485
1005 | 1.3875 | 0 | 61.403
1006 | 0 | 0 | 61.2149
1007 | 0 | 0 | 61.116
1008 | 0 | 0 | 61.0173
1009 | 0 | 0 | 60.9189
1010 | 0 | 0 | 60.8206
1011 | 0 | 0 | 60.7226
1012 | 0 | 0 | 60.6249
1013 | 0 | 0 | 60.5273
1014 | 13.148 | 13.5967 | 59.8812
1015 | 1.3448 | 0 | 59.7266
1016 | 1.7497 | 0 | 58.3106
1017 | 0 | 0 | 58.1069
1018 | 0 | 6.3668 | 58.4553
1019 | 0 | 0 | 62.8182
1020 | 0.93364 | 0 | 62.056
1021 | 0 | 0 | 61.8953
1022 | 0 | 0 | 61.7948
1023 | 0 | 0 | 61.6945
1024 | 0 | 0 | 61.5945
1025 | 0 | 0 | 61.4946
1026 | 6.6688 | 6.8115 | 60.6208
1027 | 12.742 | 13.6103 | 59.3453
1028 | 0 | 0 | 61.9671
1029 | 1.3746 | 0 | 60.8956
1030 | 0 | 0 | 60.7096
1031 | 0 | 0 | 60.6118
1032 | 0 | 0 | 60.5143
1033 | 0 | 0 | 60.417
1034 | 0 | 0 | 60.32
1035 | 0 | 0 | 60.2231
1036 | 0 | 0 | 60.1266
1037 | 0 | 0 | 60.0302
1038 | 13.0344 | 13.5903 | 59.4486
1039 | 1.3345 | 0 | 59.3214
1040 | 1.7363 | 6.4182 | 61.6506
1041 | 0 | 0 | 62.6407
1042 | 0 | 0 | 62.5384
1043 | 0 | 0 | 62.4364
1044 | 0.92728 | 0 | 61.6796
1045 | 0 | 0 | 61.5203
1046 | 0 | 0 | 61.4207
1047 | 0 | 0 | 61.3212
1048 | 0 | 0 | 61.2221
1049 | 0 | 0 | 61.1231
1050 | 6.6253 | 6.8614 | 60.2984
1051 | 13.2853 | 13.2984 | 60.3216
1052 | 0 | 0 | 61.0151
1053 | 1.3509 | 0 | 59.963
1054 | 0 | 0 | 59.7808
1055 | 0 | 0 | 59.6852
1056 | 0 | 0 | 59.5899
1057 | 0 | 0 | 59.4947
1058 | 0 | 0 | 59.3999
1059 | 0 | 0 | 59.3052
1060 | 0 | 0 | 59.2107
1061 | 0 | 0 | 59.1165
1062 | 12.8409 | 19.22 | 60.5272
1063 | 1.424 | 0 | 62.8231
1064 | 1.8525 | 0 | 61.3205
1065 | 0 | 0 | 61.1031
1066 | 0 | 0 | 61.0044
1067 | 0 | 0 | 60.906
1068 | 0.90166 | 0 | 60.1713
1069 | 0 | 0 | 60.0172
1070 | 0 | 0 | 59.9211
1071 | 0 | 0 | 59.8252
1072 | 0 | 0 | 59.7295
1073 | 0 | 0 | 59.6341
1074 | 6.6615 | 6.8589 | 59.6831
1075 | 12.9622 | 13.6536 | 59.1864
1076 | 0 | 0 | 60.0256
1077 | 1.3261 | 0 | 58.9937
1078 | 0 | 0 | 58.8153
1079 | 0 | 0 | 58.722
1080 | 0 | 0 | 58.6289
1081 | 0 | 0 | 58.536
1082 | 0 | 0 | 58.4434
1083 | 0 | 0 | 58.351
1084 | 0 | 0 | 58.2588
1085 | 0 | 0 | 58.1668
1086 | 12.6231 | 19.5533 | 59.814
1087 | 1.4108 | 0 | 62.309
1088 | 1.8354 | 0 | 60.8209
1089 | 0 | 0 | 60.6057
1090 | 0 | 0 | 60.5082
1091 | 0 | 0 | 60.411
1092 | 0.89335 | 0 | 59.6835
1093 | 0 | 0 | 59.531
1094 | 0 | 0 | 59.4361
1095 | 0 | 0 | 59.3413
1096 | 0 | 0 | 59.2468
1097 | 0 | 0 | 59.1525
1098 | 6.6069 | 6.9299 | 59.276
1099 | 12.8735 | 19.0817 | 60.6222
1100 | 0 | 0 | 63.8842
1101 | 1.4227 | 0 | 62.7735
1102 | 0 | 0 | 62.5799
1103 | 0 | 0 | 62.4778
1104 | 0 | 0 | 62.3759
1105 | 0 | 0 | 62.2742
1106 | 0 | 0 | 62.1728
1107 | 0 | 0 | 62.0717
1108 | 0 | 0 | 61.9707
1109 | 0 | 0 | 61.87
1110 | 12.8275 | 13.6918 | 59.697
1111 | 1.3862 | 0 | 61.3499
1112 | 1.8034 | 0 | 59.8887
1113 | 0 | 0 | 59.6778
1114 | 0 | 0 | 59.5825
1115 | 0 | 0 | 59.4874
1116 | 0.87786 | 0 | 58.7733
1117 | 0 | 0 | 58.624
1118 | 0 | 0 | 58.5311
1119 | 0 | 0 | 58.4385
1120 | 0 | 0 | 58.3461
1121 | 0 | 0 | 58.2539
1122 | 6.5002 | 6.9647 | 58.4618
1123 | 12.6909 | 19.3477 | 60.0243
1124 | 0 | 0 | 63.4433
1125 | 1.4115 | 0 | 62.3417
1126 | 0 | 0 | 62.1499
1127 | 0 | 0 | 62.0488
1128 | 0 | 0 | 61.9479
1129 | 0 | 0 | 61.8473
1130 | 0 | 0 | 61.7469
1131 | 0 | 0 | 61.6467
1132 | 0 | 0 | 61.5467
1133 | 0 | 0 | 61.447
1134 | 13.3431 | 13.2778 | 60.5323
1135 | 1.3576 | 0 | 60.2378
1136 | 1.7663 | 0 | 58.8078
1137 | 0 | 0 | 58.6019
1138 | 0 | 0 | 58.5091
1139 | 0 | 0 | 58.4165
1140 | 0.8599 | 6.5121 | 61.506
1141 | 0 | 0 | 62.5697
1142 | 0 | 0 | 62.4676
1143 | 0 | 0 | 62.3657
1144 | 0 | 0 | 62.2641
1145 | 0 | 0 | 62.1627
1146 | 6.6338 | 6.8295 | 60.4324
1147 | 12.8984 | 13.5274 | 59.9188
1148 | 0 | 0 | 62.4855
1149 | 1.3874 | 0 | 61.4036
1150 | 0 | 0 | 61.2156
1151 | 0 | 0 | 61.1166
1152 | 0 | 0 | 61.0179
1153 | 0 | 0 | 60.9195
1154 | 0 | 0 | 60.8212
1155 | 0 | 0 | 60.7232
1156 | 0 | 0 | 60.6255
1157 | 0 | 0 | 60.5279
1158 | 13.1444 | 13.5964 | 59.8837
1159 | 1.3445 | 0 | 59.7299
1160 | 1.7492 | 0 | 58.3143
1161 | 0 | 0 | 58.1106
1162 | 0 | 6.3651 | 58.4588
1163 | 0 | 0 | 62.8206
1164 | 0.93341 | 0 | 62.0585
1165 | 0 | 0 | 61.8979
1166 | 0 | 0 | 61.7974
1167 | 0 | 0 | 61.6971
1168 | 0 | 0 | 61.597
1169 | 0 | 0 | 61.4972
1170 | 6.6671 | 6.8097 | 60.6235
1171 | 12.7388 | 13.6099 | 59.3494
1172 | 0 | 0 | 61.9717
1173 | 1.3744 | 0 | 60.9004
1174 | 0 | 0 | 60.7144
1175 | 0 | 0 | 60.6166
1176 | 0 | 0 | 60.5191
1177 | 0 | 0 | 60.4218
1178 | 0 | 0 | 60.3247
1179 | 0 | 0 | 60.2279
1180 | 0 | 0 | 60.1313
1181 | 0 | 0 | 60.0349
1182 | 13.0292 | 13.5899 | 59.4562
1183 | 1.334 | 0 | 59.3302
1184 | 1.7357 | 6.4141 | 61.6574
1185 | 0 | 0 | 62.6467
1186 | 0 | 0 | 62.5445
1187 | 0 | 0 | 62.4424
1188 | 0.92692 | 0 | 61.6859
1189 | 0 | 0 | 61.5266
1190 | 0 | 0 | 61.4269
1191 | 0 | 0 | 61.3275
1192 | 0 | 0 | 61.2283
1193 | 0 | 0 | 61.1294
1194 | 6.6227 | 6.8608 | 60.3058
1195 | 13.2806 | 13.2934 | 60.3299
1196 | 0 | 0 | 61.0227
1197 | 1.3504 | 0 | 59.9709
1198 | 0 | 0 | 59.7887
1199 | 0 | 0 | 59.6931
1200 | 0 | 0 | 59.5977
1201 | 0 | 0 | 59.5026
1202 | 0 | 0 | 59.4077
1203 | 0 | 0 | 59.313
1204 | 0 | 0 | 59.2185
1205 | 0 | 0 | 59.1243
1206 | 12.8337 | 19.2134 | 60.5368
1207 | 1.4232 | 0 | 62.8319
1208 | 1.8515 | 0 | 61.33
1209 | 0 | 0 | 61.1126
1210 | 0 | 0 | 61.0139
1211 | 0 | 0 | 60.9155
1212 | 0.90117 | 0 | 60.1812
1213 | 0 | 0 | 60.027
1214 | 0 | 0 | 59.9309
1215 | 0 | 0 | 59.835
1216 | 0 | 0 | 59.7393
1217 | 0 | 0 | 59.6438
1218 | 6.6577 | 6.8535 | 59.6919
1219 | 12.9552 | 13.6526 | 59.1984
1220 | 0 | 0 | 60.0387
1221 | 1.3255 | 0 | 59.0072
1222 | 0 | 0 | 58.8288
1223 | 0 | 0 | 58.7355
1224 | 0 | 0 | 58.6423
1225 | 0 | 0 | 58.5494
1226 | 0 | 0 | 58.4568
1227 | 0 | 0 | 58.3643
1228 | 0 | 0 | 58.2721
1229 | 0 | 0 | 58.18
1230 | 12.6146 | 19.5441 | 59.829
1231 | 1.4098 | 0 | 62.3224
1232 | 1.8341 | 0 | 60.8351
1233 | 0 | 0 | 60.62
1234 | 0 | 0 | 60.5225
1235 | 0 | 0 | 60.4252
1236 | 0.89275 | 0 | 59.6981
1237 | 0 | 0 | 59.5456
1238 | 0 | 0 | 59.4506
1239 | 0 | 0 | 59.3558
1240 | 0 | 0 | 59.2613
1241 | 0 | 0 | 59.1669
1242 | 6.6025 | 6.9288 | 59.2923
1243 | 12.8658 | 19.0712 | 60.6399
1244 | 0 | 0 | 63.8988
1245 | 1.4218 | 0 | 62.7887
1246 | 0 | 0 | 62.5952
1247 | 0 | 0 | 62.493
1248 | 0 | 0 | 62.3911
1249 | 0 | 0 | 62.2894
1250 | 0 | 0 | 62.188
1251 | 0 | 0 | 62.0868
1252 | 0 | 0 | 61.9858
1253 | 0 | 0 | 61.8851
1254 | 12.8168 | 13.69 | 59.7175
1255 | 1.3852 | 0 | 61.3724
1256 | 1.8021 | 0 | 59.9121
1257 | 0 | 0 | 59.7012
1258 | 0 | 0 | 59.6059
1259 | 0 | 0 | 59.5107
1260 | 0.87722 | 0 | 58.797
1261 | 0 | 0 | 58.6476
1262 | 0 | 0 | 58.5547
1263 | 0 | 0 | 58.462
1264 | 0 | 0 | 58.3696
1265 | 0 | 0 | 58.2773
1266 | 6.4956 | 6.964 | 58.4875
1267 | 12.6828 | 19.3329 | 60.0504
1268 | 0 | 0 | 63.4645
1269 | 1.4105 | 0 | 62.3635
1270 | 0 | 0 | 62.1717
1271 | 0 | 0 | 62.0706
1272 | 0 | 0 | 61.9696
1273 | 0 | 0 | 61.8689
1274 | 0 | 0 | 61.7685
1275 | 0 | 0 | 61.6683
1276 | 0 | 0 | 61.5683
1277 | 0 | 0 | 61.4685
1278 | 13.3308 | 13.2636 | 60.5542
1279 | 1.3563 | 0 | 60.2587
1280 | 1.7646 | 0 | 58.8299
1281 | 0 | 0 | 58.624
1282 | 0 | 0 | 58.5312
1283 | 0 | 0 | 58.4386
1284 | 0.85905 | 6.5011 | 61.5222
1285 | 0 | 0 | 62.5839
1286 | 0 | 0 | 62.4817
1287 | 0 | 0 | 62.3798
1288 | 0 | 0 | 62.2782
1289 | 0 | 0 | 62.1768
1290 | 6.6268 | 6.8281 | 60.45
1291 | 12.8859 | 13.5263 | 59.9439
1292 | 0 | 0 | 62.5126
1293 | 1.3863 | 0 | 61.4314
1294 | 0 | 0 | 61.2433
1295 | 0 | 0 | 61.1443
1296 | 0 | 0 | 61.0456
1297 | 0 | 0 | 60.947
1298 | 0 | 0 | 60.8488
1299 | 0 | 0 | 60.7507
1300 | 0 | 0 | 60.6529
1301 | 0 | 0 | 60.5552
1302 | 13.1312 | 13.5936 | 59.917
1303 | 1.3432 | 0 | 59.7659
1304 | 1.7476 | 0 | 58.3514
1305 | 0 | 0 | 58.1477
1306 | 0 | 0 | 58.056
1307 | 0 | 6.3636 | 61.6668
1308 | 0.93267 | 0 | 62.0985
1309 | 0 | 0 | 61.9379
1310 | 0 | 0 | 61.8372
1311 | 0 | 0 | 61.7368
1312 | 0 | 0 | 61.6367
1313 | 0 | 0 | 61.5368
1314 | 6.5477 | 6.9086 | 59.8841
1315 | 12.7635 | 13.5157 | 59.497
1316 | 0 | 0 | 62.0852
1317 | 1.3751 | 0 | 61.0131
1318 | 0 | 0 | 60.8268
1319 | 0 | 0 | 60.7288
1320 | 0 | 0 | 60.631
1321 | 0 | 0 | 60.5334
1322 | 0 | 0 | 60.4361
1323 | 0 | 0 | 60.339
1324 | 0 | 0 | 60.2421
1325 | 0 | 0 | 60.1455
1326 | 13.0328 | 13.5908 | 59.5649
1327 | 1.3343 | 0 | 59.4379
1328 | 1.7361 | 6.3674 | 61.7375
1329 | 0 | 0 | 62.7179
1330 | 0 | 0 | 62.6154
1331 | 0 | 0 | 62.5132
1332 | 0.92652 | 0 | 61.7568
1333 | 0 | 0 | 61.5974
1334 | 0 | 0 | 61.4975
1335 | 0 | 0 | 61.398
1336 | 0 | 0 | 61.2986
1337 | 0 | 0 | 61.1995
1338 | 6.6197 | 6.8566 | 60.3756
1339 | 13.2735 | 13.2614 | 60.3882
1340 | 0 | 0 | 61.0723
1341 | 1.3492 | 0 | 60.0211
1342 | 0 | 0 | 59.8388
1343 | 0 | 0 | 59.7431
1344 | 0 | 0 | 59.6477
1345 | 0 | 0 | 59.5524
1346 | 0 | 0 | 59.4574
1347 | 0 | 0 | 59.3626
1348 | 0 | 0 | 59.268
1349 | 0 | 0 | 59.1737
1350 | 12.8203 | 19.1849 | 60.5836
1351 | 1.4215 | 0 | 62.8706
1352 | 1.8493 | 0 | 61.3703
1353 | 0 | 0 | 61.153
1354 | 0 | 0 | 61.0542
1355 | 0 | 0 | 60.9556
1356 | 0.90007 | 0 | 60.222
1357 | 0 | 0 | 60.0679
1358 | 0 | 0 | 59.9716
1359 | 0 | 0 | 59.8756
1360 | 0 | 0 | 59.7798
1361 | 0 | 0 | 59.6843
1362 | 6.6488 | 6.8323 | 59.725
1363 | 12.9377 | 13.6498 | 59.2379
1364 | 0 | 0 | 60.0807
1365 | 1.3239 | 0 | 59.0502
1366 | 0 | 0 | 58.8718
1367 | 0 | 0 | 58.7784
1368 | 0 | 0 | 58.6852
1369 | 0 | 0 | 58.5922
1370 | 0 | 0 | 58.4994
1371 | 0 | 0 | 58.4069
1372 | 0 | 0 | 58.3145
1373 | 0 | 0 | 58.2224
1374 | 12.5973 | 19.5186 | 59.8728
1375 | 1.4078 | 0 | 62.3598
1376 | 1.8315 | 0 | 60.8744
1377 | 0 | 0 | 60.6594
1378 | 0 | 0 | 60.5617
1379 | 0 | 0 | 60.4643
1380 | 0.89145 | 0 | 59.7381
1381 | 0 | 0 | 59.5856
1382 | 0 | 0 | 59.4905
1383 | 0 | 0 | 59.3956
1384 | 0 | 0 | 59.301
1385 | 0 | 0 | 59.2065
1386 | 6.5931 | 6.9258 | 59.3356
1387 | 12.8491 | 19.045 | 60.6854
1388 | 0 | 0 | 63.936
1389 | 1.4198 | 0 | 62.8272
1390 | 0 | 0 | 62.6337
1391 | 0 | 0 | 62.5315
1392 | 0 | 0 | 62.4295
1393 | 0 | 0 | 62.3277
1394 | 0 | 0 | 62.2261
1395 | 0 | 0 | 62.1248
1396 | 0 | 0 | 62.0238
1397 | 0 | 0 | 61.923
1398 | 12.796 | 13.686 | 59.7657
1399 | 1.3833 | 0 | 61.4245
1400 | 1.7996 | 0 | 59.9659
1401 | 0 | 0 | 59.7551
1402 | 0 | 0 | 59.6596
1403 | 0 | 0 | 59.5643
1404 | 0.87597 | 0 | 58.8513
1405 | 0 | 0 | 58.7019
1406 | 0 | 0 | 58.6089
1407 | 0 | 0 | 58.5161
1408 | 0 | 0 | 58.4235
1409 | 0 | 0 | 58.3311
1410 | 6.4866 | 6.9627 | 58.5456
1411 | 12.6669 | 19.3004 | 60.1082
1412 | 0 | 0 | 63.5112
1413 | 1.4085 | 0 | 62.4115
1414 | 0 | 0 | 62.2197
1415 | 0 | 0 | 62.1185
1416 | 0 | 0 | 62.0174
1417 | 0 | 0 | 61.9166
1418 | 0 | 0 | 61.816
1419 | 0 | 0 | 61.7157
1420 | 0 | 0 | 61.6156
1421 | 0 | 0 | 61.5157
1422 | 12.697 | 13.6971 | 59.4232
1423 | 1.3745 | 0 | 61.11
1424 | 1.7882 | 0 | 59.661
1425 | 0 | 0 | 59.4516
1426 | 0 | 0 | 59.3568
1427 | 0 | 0 | 59.2623
1428 | 0.87047 | 0 | 58.5539
1429 | 0 | 0 | 58.4056
1430 | 0 | 0 | 58.3133
1431 | 0 | 0 | 58.2211
1432 | 0 | 0 | 58.1292
1433 | 0 | 0 | 58.0375
1434 | 6.6437 | 6.7682 | 58.8993
1435 | 13.2795 | 19.6149 | 60.8919
1436 | 0 | 0 | 62.7139
1437 | 1.3878 | 0 | 61.6311
1438 | 0 | 0 | 61.4425
1439 | 0 | 0 | 61.343
1440 | 0 | 0 | 61.2438
1441 | 0 | 0 | 61.1448
1442 | 0 | 0 | 61.046
1443 | 0 | 0 | 60.9475
1444 | 0 | 0 | 60.8492
1445 | 0 | 0 | 60.7511
1446 | 13.1386 | 13.5309 | 60.0774
1447 | 1.343 | 0 | 59.9071
1448 | 1.7473 | 0 | 58.4924
1449 | 0 | 0 | 58.2885
1450 | 0 | 0 | 58.1964
1451 | 0 | 0 | 58.1045
1452 | 0.85066 | 6.6598 | 61.2868
1453 | 0 | 0 | 62.3791
1454 | 0 | 0 | 62.2774
1455 | 0 | 0 | 62.176
1456 | 0 | 0 | 62.0748
1457 | 0 | 0 | 61.9739
1458 | 6.5821 | 6.8349 | 60.2759
1459 | 12.8098 | 13.5184 | 59.8228
1460 | 0 | 0 | 62.4031
1461 | 1.3793 | 0 | 61.3271
1462 | 0 | 0 | 61.1398
1463 | 0 | 0 | 61.041
1464 | 0 | 0 | 60.9425
1465 | 0 | 0 | 60.8442
1466 | 0 | 0 | 60.7462
1467 | 0 | 0 | 60.6483
1468 | 0 | 0 | 60.5507
1469 | 0 | 0 | 60.4534
1470 | 13.0663 | 13.5915 | 59.8526
1471 | 1.3374 | 0 | 59.717
1472 | 1.74 | 0 | 58.3084
1473 | 0 | 0 | 58.1053
1474 | 0 | 6.359 | 59.2686
1475 | 0 | 0 | 62.8086
1476 | 0.92877 | 0 | 62.0499
1477 | 0 | 0 | 61.8896
1478 | 0 | 0 | 61.7891
1479 | 0 | 0 | 61.6888
1480 | 0 | 0 | 61.5888
1481 | 0 | 0 | 61.489
1482 | 6.5201 | 6.9118 | 59.8535
1483 | 12.7162 | 13.5113 | 59.4989
1484 | 0 | 0 | 62.0944
1485 | 1.3708 | 0 | 61.0253
1486 | 0 | 0 | 60.8392
1487 | 0 | 0 | 60.7412
1488 | 0 | 0 | 60.6433
1489 | 0 | 0 | 60.5458
1490 | 0 | 0 | 60.4484
1491 | 0 | 0 | 60.3513
1492 | 0 | 0 | 60.2544
1493 | 0 | 0 | 60.1577
1494 | 12.9908 | 13.5871 | 59.5997
1495 | 1.3305 | 0 | 59.4822
1496 | 1.7311 | 6.3531 | 60.9633
1497 | 0 | 0 | 62.7571
1498 | 0 | 0 | 62.6545
1499 | 0 | 0 | 62.5522
1500 | 0.92392 | 0 | 61.7976
1501 | 0 | 0 | 61.6381
1502 | 0 | 0 | 61.5382
1503 | 0 | 0 | 61.4385
1504 | 0 | 0 | 61.3391
1505 | 0 | 0 | 61.2399
1506 | 6.6011 | 6.8517 | 60.4245
1507 | 13.2394 | 13.2279 | 60.4434
1508 | 0 | 0 | 61.1234
1509 | 1.3457 | 0 | 60.0747
1510 | 0 | 0 | 59.8925
1511 | 0 | 0 | 59.7967
1512 | 0 | 0 | 59.7011
1513 | 0 | 0 | 59.6057
1514 | 0 | 0 | 59.5105
1515 | 0 | 0 | 59.4156
1516 | 0 | 0 | 59.3209
1517 | 0 | 0 | 59.2264
1518 | 12.7844 | 19.1456 | 60.6431
1519 | 1.4176 | 0 | 62.9234
1520 | 1.8441 | 0 | 61.4269
1521 | 0 | 0 | 61.2097
1522 | 0 | 0 | 61.1108
1523 | 0 | 0 | 61.0121
1524 | 0.89755 | 0 | 60.2801
1525 | 0 | 0 | 60.126
1526 | 0 | 0 | 60.0296
1527 | 0 | 0 | 59.9335
1528 | 0 | 0 | 59.8375
1529 | 0 | 0 | 59.7418
1530 | 6.4213 | 7.0919 | 59.1446
1531 | 12.9702 | 13.4446 | 59.531
1532 | 0 | 0 | 60.3306
1533 | 1.325 | 0 | 59.2987
1534 | 0 | 0 | 59.1196
1535 | 0 | 0 | 59.0256
1536 | 0 | 0 | 58.9318
1537 | 0 | 0 | 58.8383
1538 | 0 | 0 | 58.7449
1539 | 0 | 0 | 58.6518
1540 | 0 | 0 | 58.5589
1541 | 0 | 0 | 58.4662
1542 | 12.6028 | 19.4155 | 60.0798
1543 | 1.4063 | 0 | 62.5204
1544 | 1.8295 | 0 | 61.0361
1545 | 0 | 0 | 60.8208
1546 | 0 | 0 | 60.7228
1547 | 0 | 0 | 60.625
1548 | 0.89046 | 0 | 59.899
1549 | 0 | 0 | 59.7462
1550 | 0 | 0 | 59.6507
1551 | 0 | 0 | 59.5555
1552 | 0 | 0 | 59.4604
1553 | 0 | 0 | 59.3656
1554 | 6.5853 | 6.9165 | 59.4933
1555 | 12.8346 | 13.6421 | 59.0905
1556 | 0 | 0 | 59.9506
1557 | 1.3145 | 0 | 58.927
1558 | 0 | 0 | 58.7495
1559 | 0 | 0 | 58.6564
1560 | 0 | 0 | 58.5634
1561 | 0 | 0 | 58.4707
1562 | 0 | 0 | 58.3782
1563 | 0 | 0 | 58.286
1564 | 0 | 0 | 58.1939
1565 | 0 | 0 | 58.1021
1566 | 12.5099 | 19.5349 | 59.8071
1567 | 1.4003 | 0 | 62.3247
1568 | 1.8218 | 0 | 60.8468
1569 | 0 | 0 | 60.6325
1570 | 0 | 0 | 60.5349
1571 | 0 | 0 | 60.4376
1572 | 0.88668 | 0 | 59.7148
1573 | 0 | 0 | 59.5627
1574 | 0 | 0 | 59.4676
1575 | 0 | 0 | 59.3728
1576 | 0 | 0 | 59.2782
1577 | 0 | 0 | 59.1838
1578 | 6.5592 | 6.9244 | 59.3317
1579 | 12.7899 | 19.0196 | 60.7126
1580 | 0 | 0 | 63.9642
1581 | 1.414 | 0 | 62.8594
1582 | 0 | 0 | 62.6662
1583 | 0 | 0 | 62.5639
1584 | 0 | 0 | 62.4618
1585 | 0 | 0 | 62.3599
1586 | 0 | 0 | 62.2583
1587 | 0 | 0 | 62.1569
1588 | 0 | 0 | 62.0558
1589 | 0 | 0 | 61.9549
1590 | 12.7406 | 13.679 | 59.8268
1591 | 1.3782 | 0 | 61.4971
1592 | 1.7929 | 0 | 60.0433
1593 | 0 | 0 | 59.8327
1594 | 0 | 0 | 59.7371
1595 | 0 | 0 | 59.6416
1596 | 0.8727 | 0 | 58.9307
1597 | 0 | 0 | 58.7813
1598 | 0 | 0 | 58.6881
1599 | 0 | 0 | 58.5951
1600 | 0 | 0 | 58.5023
1601 | 0 | 0 | 58.4098
1602 | 6.4631 | 6.9596 | 58.636
1603 | 12.6257 | 19.2424 | 60.2066
1604 | 0 | 0 | 63.5923
1605 | 1.4037 | 0 | 62.4958
1606 | 0 | 0 | 62.3041
1607 | 0 | 0 | 62.2026
1608 | 0 | 0 | 62.1014
1609 | 0 | 0 | 62.0004
1610 | 0 | 0 | 61.8996
1611 | 0 | 0 | 61.7991
1612 | 0 | 0 | 61.6988
1613 | 0 | 0 | 61.5987
1614 | 12.6499 | 13.6883 | 59.5295
1615 | 1.3701 | 0 | 61.2251
1616 | 1.7825 | 0 | 59.7801
1617 | 0 | 0 | 59.5708
1618 | 0 | 0 | 59.4757
1619 | 0 | 0 | 59.3808
1620 | 0.86765 | 0 | 58.6742
1621 | 0 | 0 | 58.5258
1622 | 0 | 0 | 58.4331
1623 | 0 | 0 | 58.3407
1624 | 0 | 0 | 58.2485
1625 | 0 | 0 | 58.1566
1626 | 6.4276 | 6.9581 | 58.4031
1627 | 12.5638 | 19.3155 | 60.0391
1628 | 0 | 0 | 63.4702
1629 | 1.3996 | 0 | 62.377
1630 | 0 | 0 | 62.1858
1631 | 0 | 0 | 62.0846
1632 | 0 | 0 | 61.9836
1633 | 0 | 0 | 61.8829
1634 | 0 | 0 | 61.7824
1635 | 0 | 0 | 61.6822
1636 | 0 | 0 | 61.5821
1637 | 0 | 0 | 61.4824
1638 | 12.6134 | 13.6906 | 59.4361
1639 | 1.3669 | 0 | 61.1415
1640 | 1.7783 | 0 | 59.6999
1641 | 0 | 0 | 59.491
1642 | 0 | 0 | 59.3961
1643 | 0 | 0 | 59.3015
1644 | 0.86559 | 0 | 58.5965
1645 | 0 | 0 | 58.4484
1646 | 0 | 0 | 58.3559
1647 | 0 | 0 | 58.2637
1648 | 0 | 0 | 58.1717
1649 | 0 | 0 | 58.0799
1650 | 6.4131 | 6.9572 | 58.3345
1651 | 12.5385 | 19.3338 | 59.9935
1652 | 0 | 0 | 63.4379
1653 | 1.3977 | 0 | 62.3461
1654 | 0 | 0 | 62.1552
1655 | 0 | 0 | 62.054
1656 | 0 | 0 | 61.9531
1657 | 0 | 0 | 61.8525
1658 | 0 | 0 | 61.7521
1659 | 0 | 0 | 61.6519
1660 | 0 | 0 | 61.5519
1661 | 0 | 0 | 61.4522
1662 | 12.5961 | 13.6905 | 59.4161
1663 | 1.3653 | 0 | 61.1258
1664 | 1.7763 | 0 | 59.6857
1665 | 0 | 0 | 59.4771
1666 | 0 | 0 | 59.3822
1667 | 0 | 0 | 59.2876
1668 | 0.8646 | 0 | 58.5833
1669 | 0 | 0 | 58.4353
1670 | 0 | 0 | 58.3429
1671 | 0 | 0 | 58.2507
1672 | 0 | 0 | 58.1587
1673 | 0 | 0 | 58.067
1674 | 6.406 | 6.9565 | 58.3253
1675 | 12.5261 | 19.3322 | 59.9919
1676 | 0 | 0 | 63.4382
1677 | 1.3966 | 0 | 62.3472
1678 | 0 | 0 | 62.1563
1679 | 0 | 0 | 62.0552
1680 | 0 | 0 | 61.9543
1681 | 0 | 0 | 61.8536
1682 | 0 | 0 | 61.7532
1683 | 0 | 0 | 61.653
1684 | 0 | 0 | 61.5531
1685 | 0 | 0 | 61.4533
1686 | 12.5855 | 13.6894 | 59.423
1687 | 1.3644 | 0 | 61.1349
1688 | 1.775 | 0 | 59.6958
1689 | 0 | 0 | 59.4872
1690 | 0 | 0 | 59.3923
1691 | 0 | 0 | 59.2976
1692 | 0.86398 | 0 | 58.5938
1693 | 0 | 0 | 58.4458
1694 | 0 | 0 | 58.3533
1695 | 0 | 0 | 58.2611
1696 | 0 | 0 | 58.1691
1697 | 0 | 0 | 58.0773
1698 | 6.4016 | 6.956 | 58.338
1699 | 12.5183 | 19.3232 | 60.0067
1700 | 0 | 0 | 63.4506
1701 | 1.3957 | 0 | 62.3602
1702 | 0 | 0 | 62.1693
1703 | 0 | 0 | 62.0682
1704 | 0 | 0 | 61.9672
1705 | 0 | 0 | 61.8666
1706 | 0 | 0 | 61.7661
1707 | 0 | 0 | 61.6659
1708 | 0 | 0 | 61.5659
1709 | 0 | 0 | 61.4661
1710 | 12.5772 | 13.6879 | 59.44
1711 | 1.3636 | 0 | 61.1535
1712 | 1.774 | 0 | 59.715
1713 | 0 | 0 | 59.5064
1714 | 0 | 0 | 59.4115
1715 | 0 | 0 | 59.3168
1716 | 0.86348 | 0 | 58.6133
1717 | 0 | 0 | 58.4653
1718 | 0 | 0 | 58.3728
1719 | 0 | 0 | 58.2805
1720 | 0 | 0 | 58.1885
1721 | 0 | 0 | 58.0966
1722 | 6.398 | 6.9555 | 58.359
1723 | 12.512 | 19.3112 | 60.028
1724 | 0 | 0 | 63.4678
1725 | 1.3949 | 0 | 62.3779
1726 | 0 | 0 | 62.187
1727 | 0 | 0 | 62.0858
1728 | 0 | 0 | 61.9849
1729 | 0 | 0 | 61.8841
1730 | 0 | 0 | 61.7836
1731 | 0 | 0 | 61.6834
1732 | 0 | 0 | 61.5834
1733 | 0 | 0 | 61.4836
1734 | 12.5695 | 13.6863 | 59.4611
1735 | 1.3629 | 0 | 61.1759
1736 | 1.7731 | 0 | 59.7382
1737 | 0 | 0 | 59.5296
1738 | 0 | 0 | 59.4346
1739 | 0 | 0 | 59.3398
1740 | 0.86302 | 0 | 58.6365
1741 | 0 | 0 | 58.4885
1742 | 0 | 0 | 58.396
1743 | 0 | 0 | 58.3037
1744 | 0 | 0 | 58.2116
1745 | 0 | 0 | 58.1197
1746 | 6.3947 | 6.955 | 58.3836
1747 | 12.5062 | 19.2978 | 60.052
1748 | 0 | 0 | 63.4871
1749 | 1.3941 | 0 | 62.3977
1750 | 0 | 0 | 62.2069
1751 | 0 | 0 | 62.1056
1752 | 0 | 0 | 62.0046
1753 | 0 | 0 | 61.9038
1754 | 0 | 0 | 61.8033
1755 | 0 | 0 | 61.703
1756 | 0 | 0 | 61.6029
1757 | 0 | 0 | 61.5031
1758 | 12.562 | 13.6846 | 59.4841
1759 | 1.3622 | 0 | 61.2003
1760 | 1.7721 | 0 | 59.7632
1761 | 0 | 0 | 59.5546
1762 | 0 | 0 | 59.4595
1763 | 0 | 0 | 59.3647
1764 | 0.86257 | 0 | 58.6617
1765 | 0 | 0 | 58.5136
1766 | 0 | 0 | 58.421
1767 | 0 | 0 | 58.3287
1768 | 0 | 0 | 58.2365
1769 | 0 | 0 | 58.1446
1770 | 6.3914 | 6.9545 | 58.4101
1771 | 12.5003 | 19.2837 | 60.0777
1772 | 0 | 0 | 63.5077
1773 | 1.3933 | 0 | 62.4187
1774 | 0 | 0 | 62.2279
1775 | 0 | 0 | 62.1266
1776 | 0 | 0 | 62.0255
1777 | 0 | 0 | 61.9247
1778 | 0 | 0 | 61.8241
1779 | 0 | 0 | 61.7238
1780 | 0 | 0 | 61.6236
1781 | 0 | 0 | 61.5238
1782 | 12.5543 | 13.6827 | 59.5084
1783 | 1.3615 | 0 | 61.2259
1784 | 1.7712 | 0 | 59.7894
1785 | 0 | 0 | 59.5808
1786 | 0 | 0 | 59.4857
1787 | 0 | 0 | 59.3909
1788 | 0.8621 | 0 | 58.6881
1789 | 0 | 0 | 58.54
1790 | 0 | 0 | 58.4473
1791 | 0 | 0 | 58.3549
1792 | 0 | 0 | 58.2627
1793 | 0 | 0 | 58.1707
1794 | 6.388 | 6.9539 | 58.4377
1795 | 12.4944 | 19.2689 | 60.1044
1796 | 0 | 0 | 63.529
1797 | 1.3925 | 0 | 62.4406
1798 | 0 | 0 | 62.2498
1799 | 0 | 0 | 62.1484
1800 | 0 | 0 | 62.0473
1801 | 0 | 0 | 61.9464
1802 | 0 | 0 | 61.8458
1803 | 0 | 0 | 61.7454
1804 | 0 | 0 | 61.6452
1805 | 0 | 0 | 61.5453
1806 | 12.5464 | 13.6809 | 59.5337
1807 | 1.3607 | 0 | 61.2525
1808 | 1.7703 | 0 | 59.8166
1809 | 0 | 0 | 59.608
1810 | 0 | 0 | 59.5129
1811 | 0 | 0 | 59.4179
1812 | 0.86162 | 0 | 58.7154
1813 | 0 | 0 | 58.5673
1814 | 0 | 0 | 58.4746
1815 | 0 | 0 | 58.3821
1816 | 0 | 0 | 58.2898
1817 | 0 | 0 | 58.1977
1818 | 6.3845 | 6.9533 | 58.4664
1819 | 12.4883 | 19.2537 | 60.132
1820 | 0 | 0 | 63.5512
1821 | 1.3917 | 0 | 62.4633
1822 | 0 | 0 | 62.2724
1823 | 0 | 0 | 62.171
1824 | 0 | 0 | 62.0699
1825 | 0 | 0 | 61.9689
1826 | 0 | 0 | 61.8682
1827 | 0 | 0 | 61.7678
1828 | 0 | 0 | 61.6676
1829 | 0 | 0 | 61.5676
1830 | 12.5383 | 13.6789 | 59.5597
1831 | 1.36 | 0 | 61.2799
1832 | 1.7693 | 0 | 59.8447
1833 | 0 | 0 | 59.6361
1834 | 0 | 0 | 59.5409
1835 | 0 | 0 | 59.4459
1836 | 0.86114 | 0 | 58.7436
1837 | 0 | 0 | 58.5955
1838 | 0 | 0 | 58.5027
1839 | 0 | 0 | 58.4101
1840 | 0 | 0 | 58.3178
1841 | 0 | 0 | 58.2256
1842 | 6.381 | 6.9527 | 58.496
1843 | 12.482 | 19.238 | 60.1605
1844 | 0 | 0 | 63.574
1845 | 1.3908 | 0 | 62.4866
1846 | 0 | 0 | 62.2958
1847 | 0 | 0 | 62.1943
1848 | 0 | 0 | 62.0931
1849 | 0 | 0 | 61.9921
1850 | 0 | 0 | 61.8914
1851 | 0 | 0 | 61.7908
1852 | 0 | 0 | 61.6906
1853 | 0 | 0 | 61.5905
1854 | 12.5301 | 13.677 | 59.5865
1855 | 1.3592 | 0 | 61.3082
1856 | 1.7683 | 0 | 59.8736
1857 | 0 | 0 | 59.665
1858 | 0 | 0 | 59.5697
1859 | 0 | 0 | 59.4747
1860 | 0.86064 | 0 | 58.7727
1861 | 0 | 0 | 58.6245
1862 | 0 | 0 | 58.5316
1863 | 0 | 0 | 58.439
1864 | 0 | 0 | 58.3466
1865 | 0 | 0 | 58.2544
1866 | 6.3774 | 6.9521 | 58.5264
1867 | 12.4756 | 19.2219 | 60.1898
1868 | 0 | 0 | 63.5974
1869 | 1.3899 | 0 | 62.5106
1870 | 0 | 0 | 62.3198
1871 | 0 | 0 | 62.2183
1872 | 0 | 0 | 62.117
1873 | 0 | 0 | 62.016
1874 | 0 | 0 | 61.9151
1875 | 0 | 0 | 61.8146
1876 | 0 | 0 | 61.7142
1877 | 0 | 0 | 61.6141
1878 | 12.5216 | 13.6749 | 59.6141
1879 | 1.3584 | 0 | 61.3372
1880 | 1.7672 | 0 | 59.9034
1881 | 0 | 0 | 59.6947
1882 | 0 | 0 | 59.5994
1883 | 0 | 0 | 59.5042
1884 | 0.86012 | 0 | 58.8026
1885 | 0 | 0 | 58.6543
1886 | 0 | 0 | 58.5614
1887 | 0 | 0 | 58.4687
1888 | 0 | 0 | 58.3762
1889 | 0 | 0 | 58.2839
1890 | 6.3736 | 6.9515 | 58.5577
1891 | 12.4691 | 19.2053 | 60.22
1892 | 0 | 0 | 63.6215
1893 | 1.389 | 0 | 62.5353
1894 | 0 | 0 | 62.3445
1895 | 0 | 0 | 62.2429
1896 | 0 | 0 | 62.1416
1897 | 0 | 0 | 62.0405
1898 | 0 | 0 | 61.9396
1899 | 0 | 0 | 61.839
1900 | 0 | 0 | 61.7386
1901 | 0 | 0 | 61.6384
1902 | 12.5129 | 13.6728 | 59.6424
1903 | 1.3576 | 0 | 61.367
1904 | 1.7662 | 0 | 59.9339
1905 | 0 | 0 | 59.7253
1906 | 0 | 0 | 59.6298
1907 | 0 | 0 | 59.5346
1908 | 0.85959 | 0 | 58.8332
1909 | 0 | 0 | 58.685
1910 | 0 | 0 | 58.592
1911 | 0 | 0 | 58.4992
1912 | 0 | 0 | 58.4066
1913 | 0 | 0 | 58.3143
1914 | 6.3698 | 6.9509 | 58.5898
1915 | 12.4623 | 19.1883 | 60.2509
1916 | 0 | 0 | 63.6463
1917 | 1.3881 | 0 | 62.5606
1918 | 0 | 0 | 62.3698
1919 | 0 | 0 | 62.2682
1920 | 0 | 0 | 62.1668
1921 | 0 | 0 | 62.0656
1922 | 0 | 0 | 61.9647
1923 | 0 | 0 | 61.864
1924 | 0 | 0 | 61.7636
1925 | 0 | 0 | 61.6633
1926 | 12.504 | 13.6707 | 59.6715
1927 | 1.3568 | 0 | 61.3976
1928 | 1.7651 | 0 | 59.9652
1929 | 0 | 0 | 59.7566
1930 | 0 | 0 | 59.6611
1931 | 0 | 0 | 59.5658
1932 | 0.85906 | 0 | 58.8647
1933 | 0 | 0 | 58.7164
1934 | 0 | 0 | 58.6233
1935 | 0 | 0 | 58.5305
1936 | 0 | 0 | 58.4378
1937 | 0 | 0 | 58.3454
1938 | 6.3659 | 6.9502 | 58.6228
1939 | 12.4554 | 19.1708 | 60.2826
1940 | 0 | 0 | 63.6716
1941 | 1.3872 | 0 | 62.5866
1942 | 0 | 0 | 62.3958
1943 | 0 | 0 | 62.2941
1944 | 0 | 0 | 62.1926
1945 | 0 | 0 | 62.0914
1946 | 0 | 0 | 61.9904
1947 | 0 | 0 | 61.8897
1948 | 0 | 0 | 61.7892
1949 | 0 | 0 | 61.6889
1950 | 12.4949 | 13.6685 | 59.7013
1951 | 1.3559 | 0 | 61.4289
1952 | 1.764 | 0 | 59.9973
1953 | 0 | 0 | 59.7887
1954 | 0 | 0 | 59.6931
1955 | 0 | 0 | 59.5977
1956 | 0.8585 | 0 | 58.8969
1957 | 0 | 0 | 58.7486
1958 | 0 | 0 | 58.6555
1959 | 0 | 0 | 58.5625
1960 | 0 | 0 | 58.4698
1961 | 0 | 0 | 58.3773
1962 | 6.3619 | 6.9495 | 58.6566
1963 | 12.4484 | 19.1529 | 60.3151
1964 | 0 | 0 | 63.6976
1965 | 1.3862 | 0 | 62.6132
1966 | 0 | 0 | 62.4224
1967 | 0 | 0 | 62.3206
1968 | 0 | 0 | 62.2191
1969 | 0 | 0 | 62.1178
1970 | 0 | 0 | 62.0168
1971 | 0 | 0 | 61.916
1972 | 0 | 0 | 61.8154
1973 | 0 | 0 | 61.7151
1974 | 12.4856 | 13.6662 | 59.7318
1975 | 1.355 | 0 | 61.4611
1976 | 1.7628 | 0 | 60.0302
1977 | 0 | 0 | 59.8215
1978 | 0 | 0 | 59.7259
1979 | 0 | 0 | 59.6304
1980 | 0.85794 | 0 | 58.93
1981 | 0 | 0 | 58.7816
1982 | 0 | 0 | 58.6884
1983 | 0 | 0 | 58.5954
1984 | 0 | 0 | 58.5026
1985 | 0 | 0 | 58.41
1986 | 6.3578 | 6.9489 | 58.6912
1987 | 12.4412 | 19.1346 | 60.3484
1988 | 0 | 0 | 63.7243
1989 | 1.3852 | 0 | 62.6405
1990 | 0 | 0 | 62.4496
1991 | 0 | 0 | 62.3478
1992 | 0 | 0 | 62.2462
1993 | 0 | 0 | 62.1449
1994 | 0 | 0 | 62.0438
1995 | 0 | 0 | 61.9429
1996 | 0 | 0 | 61.8423
1997 | 0 | 0 | 61.7419
1998 | 12.4761 | 13.6639 | 59.7631
1999 | 1.3542 | 0 | 61.4939
2000 | 1.7617 | 0 | 60.0638
2001 | 0 | 0 | 59.8552
2002 | 0 | 0 | 59.7594
2003 | 0 | 0 | 59.6639
2004 | 0.85736 | 0 | 58.9638
2005 | 0 | 0 | 58.8153
2006 | 0 | 0 | 58.722
2007 | 0 | 0 | 58.6289
2008 | 0 | 0 | 58.5361
2009 | 0 | 0 | 58.4434
2010 | 6.3536 | 6.9482 | 58.7265
2011 | 12.4338 | 19.1159 | 60.3824
2012 | 0 | 0 | 63.7515
2013 | 1.3842 | 0 | 62.6683
2014 | 0 | 0 | 62.4775
2015 | 0 | 0 | 62.3756
2016 | 0 | 0 | 62.274
2017 | 0 | 0 | 62.1725
2018 | 0 | 0 | 62.0714
2019 | 0 | 0 | 61.9704
2020 | 0 | 0 | 61.8697
2021 | 0 | 0 | 61.7693
2022 | 12.4663 | 13.6616 | 59.795
2023 | 1.3533 | 0 | 61.5275
2024 | 1.7605 | 0 | 60.0982
2025 | 0 | 0 | 59.8895
2026 | 0 | 0 | 59.7937
2027 | 0 | 0 | 59.6981
2028 | 0.85677 | 0 | 58.9983
2029 | 0 | 0 | 58.8498
2030 | 0 | 0 | 58.7564
2031 | 0 | 0 | 58.6633
2032 | 0 | 0 | 58.5703
2033 | 0 | 0 | 58.4776
2034 | 6.3493 | 6.9467 | 58.7623
2035 | 12.4261 | 19.0969 | 60.4168
2036 | 0 | 0 | 63.779
2037 | 1.3831 | 0 | 62.6966
2038 | 0 | 0 | 62.5057
2039 | 0 | 0 | 62.4037
2040 | 0 | 0 | 62.302
2041 | 0 | 0 | 62.2006
2042 | 0 | 0 | 62.0993
2043 | 0 | 0 | 61.9983
2044 | 0 | 0 | 61.8975
2045 | 0 | 0 | 61.797
2046 | 12.4564 | 13.6592 | 59.8274
2047 | 1.3523 | 0 | 61.5616
2048 | 1.7593 | 0 | 60.1331
2049 | 0 | 0 | 59.9244
2050 | 0 | 0 | 59.8285
2051 | 0 | 0 | 59.7329
2052 | 0.85617 | 0 | 59.0334
2053 | 0 | 0 | 58.8849
2054 | 0 | 0 | 58.7914
2055 | 0 | 0 | 58.6982
2056 | 0 | 0 | 58.6051
2057 | 0 | 0 | 58.5123
2058 | 6.3449 | 6.9441 | 58.798
2059 | 12.4181 | 19.078 | 60.4512
2060 | 0 | 0 | 63.8066
2061 | 1.382 | 0 | 62.7248
2062 | 0 | 0 | 62.534
2063 | 0 | 0 | 62.4319
2064 | 0 | 0 | 62.3302
2065 | 0 | 0 | 62.2286
2066 | 0 | 0 | 62.1273
2067 | 0 | 0 | 62.0262
2068 | 0 | 0 | 61.9254
2069 | 0 | 0 | 61.8248
2070 | 12.4461 | 13.652 | 59.8585
2071 | 1.3513 | 0 | 61.5924
2072 | 1.7579 | 0 | 60.1648
2073 | 0 | 0 | 59.9562
2074 | 0 | 0 | 59.8602
2075 | 0 | 0 | 59.7645
2076 | 0.85549 | 0 | 59.0654
2077 | 0 | 0 | 58.9168
2078 | 0 | 0 | 58.8233
2079 | 0 | 0 | 58.73
2080 | 0 | 0 | 58.6369
2081 | 0 | 0 | 58.544
2082 | 6.3399 | 6.9417 | 58.8311
2083 | 12.4092 | 19.0597 | 60.4839
2084 | 0 | 0 | 63.8329
2085 | 1.3809 | 0 | 62.7519
2086 | 0 | 0 | 62.561
2087 | 0 | 0 | 62.459
2088 | 0 | 0 | 62.3571
2089 | 0 | 0 | 62.2555
2090 | 0 | 0 | 62.1541
2091 | 0 | 0 | 62.053
2092 | 0 | 0 | 61.9521
2093 | 0 | 0 | 61.8515
2094 | 12.4352 | 13.6351 | 59.8856
2095 | 1.35 | 0 | 61.6152
2096 | 1.7562 | 0 | 60.1889
2097 | 0 | 0 | 59.9803
2098 | 0 | 0 | 59.8843
2099 | 0 | 0 | 59.7885
2100 | 0.85466 | 0 | 59.0899
2101 | 0 | 0 | 58.9413
2102 | 0 | 0 | 58.8477
2103 | 0 | 0 | 58.7544
2104 | 0 | 0 | 58.6612
2105 | 0 | 0 | 58.5683
2106 | 6.3338 | 6.9398 | 58.8577
2107 | 12.3985 | 19.0434 | 60.512
2108 | 0 | 0 | 63.856
2109 | 1.3796 | 0 | 62.7758
2110 | 0 | 0 | 62.585
2111 | 0 | 0 | 62.4828
2112 | 0 | 0 | 62.3809
2113 | 0 | 0 | 62.2793
2114 | 0 | 0 | 62.1778
2115 | 0 | 0 | 62.0766
2116 | 0 | 0 | 61.9757
2117 | 0 | 0 | 61.875
2118 | 12.4233 | 13.6193 | 59.9106
2119 | 1.3486 | 0 | 61.6366
2120 | 1.7544 | 0 | 60.2116
2121 | 0 | 0 | 60.003
2122 | 0 | 0 | 59.907
2123 | 0 | 0 | 59.8111
2124 | 0.85379 | 0 | 59.1131
2125 | 0 | 0 | 58.9645
2126 | 0 | 0 | 58.8709
2127 | 0 | 0 | 58.7775
2128 | 0 | 0 | 58.6842
2129 | 0 | 0 | 58.5913
2130 | 6.3275 | 6.9381 | 58.8833
2131 | 12.3873 | 19.0274 | 60.5395
2132 | 0 | 0 | 63.8786
2133 | 1.3783 | 0 | 62.7993
2134 | 0 | 0 | 62.6085
2135 | 0 | 0 | 62.5063
2136 | 0 | 0 | 62.4043
2137 | 0 | 0 | 62.3026
2138 | 0 | 0 | 62.2011
2139 | 0 | 0 | 62.0999
2140 | 0 | 0 | 61.9989
2141 | 0 | 0 | 61.8981
2142 | 12.411 | 13.6036 | 59.9354
2143 | 1.3472 | 0 | 61.658
2144 | 1.7526 | 0 | 60.2343
2145 | 0 | 0 | 60.0258
2146 | 0 | 0 | 59.9296
2147 | 0 | 0 | 59.8337
2148 | 0.85289 | 0 | 59.1363
2149 | 0 | 0 | 58.9877
2150 | 0 | 0 | 58.894
2151 | 0 | 0 | 58.8006
2152 | 0 | 0 | 58.7073
2153 | 0 | 0 | 58.6143
2154 | 6.321 | 6.9363 | 58.909
2155 | 12.3758 | 19.0111 | 60.5673
2156 | 0 | 0 | 63.9015
2157 | 1.377 | 0 | 62.823
2158 | 0 | 0 | 62.6323
2159 | 0 | 0 | 62.53
2160 | 0 | 0 | 62.428
2161 | 0 | 0 | 62.3262
2162 | 0 | 0 | 62.2247
2163 | 0 | 0 | 62.1234
2164 | 0 | 0 | 62.0223
2165 | 0 | 0 | 61.9215
2166 | 12.3985 | 13.5876 | 59.9605
2167 | 1.3458 | 0 | 61.6796
2168 | 1.7507 | 0 | 60.2573
2169 | 0 | 0 | 60.0488
2170 | 0 | 0 | 59.9527
2171 | 0 | 0 | 59.8567
2172 | 0.85197 | 0 | 59.1598
2173 | 0 | 0 | 59.0113
2174 | 0 | 0 | 58.9175
2175 | 0 | 0 | 58.824
2176 | 0 | 0 | 58.7307
2177 | 0 | 0 | 58.6376
2178 | 6.3144 | 6.9345 | 58.9351
2179 | 12.3641 | 18.9946 | 60.5954
2180 | 0 | 0 | 63.9247
2181 | 1.3756 | 0 | 62.8471
2182 | 0 | 0 | 62.6564
2183 | 0 | 0 | 62.5541
2184 | 0 | 0 | 62.452
2185 | 0 | 0 | 62.3502
2186 | 0 | 0 | 62.2486
2187 | 0 | 0 | 62.1473
2188 | 0 | 0 | 62.0461
2189 | 0 | 0 | 61.9453
2190 | 12.3857 | 13.5713 | 59.9861
2191 | 1.3443 | 0 | 61.7016
2192 | 1.7489 | 0 | 60.2806
2193 | 0 | 0 | 60.0723
2194 | 0 | 0 | 59.976
2195 | 0 | 0 | 59.88
2196 | 0.85104 | 0 | 59.1838
2197 | 0 | 0 | 59.0352
2198 | 0 | 0 | 58.9414
2199 | 0 | 0 | 58.8478
2200 | 0 | 0 | 58.7544
2201 | 0 | 0 | 58.6613
2202 | 6.3076 | 6.9326 | 58.9616
2203 | 12.3522 | 18.9778 | 60.6241
2204 | 0 | 0 | 63.9483
2205 | 1.3742 | 0 | 62.8717
2206 | 0 | 0 | 62.681
2207 | 0 | 0 | 62.5786
2208 | 0 | 0 | 62.4765
2209 | 0 | 0 | 62.3746
2210 | 0 | 0 | 62.2729
2211 | 0 | 0 | 62.1715
2212 | 0 | 0 | 62.0704
2213 | 0 | 0 | 61.9694
2214 | 12.3728 | 13.5548 | 60.0121
2215 | 1.3429 | 0 | 61.724
2216 | 1.7469 | 0 | 60.3044
2217 | 0 | 0 | 60.0961
2218 | 0 | 0 | 59.9998
2219 | 0 | 0 | 59.9037
2220 | 0.85009 | 0 | 59.2081
2221 | 0 | 0 | 59.0595
2222 | 0 | 0 | 58.9657
2223 | 0 | 0 | 58.872
2224 | 0 | 0 | 58.7786
2225 | 0 | 0 | 58.6854
2226 | 6.3008 | 6.9308 | 58.9885
2227 | 12.3401 | 18.9607 | 60.6532
2228 | 0 | 0 | 63.9723
2229 | 1.3728 | 0 | 62.8966
2230 | 0 | 0 | 62.7059
2231 | 0 | 0 | 62.6035
2232 | 0 | 0 | 62.5013
2233 | 0 | 0 | 62.3994
2234 | 0 | 0 | 62.2976
2235 | 0 | 0 | 62.1962
2236 | 0 | 0 | 62.095
2237 | 0 | 0 | 61.994
2238 | 12.3596 | 13.538 | 60.0384
2239 | 1.3414 | 0 | 61.7467
2240 | 1.745 | 0 | 60.3285
2241 | 0 | 0 | 60.1203
2242 | 0 | 0 | 60.0239
2243 | 0 | 0 | 59.9278
2244 | 0.84913 | 0 | 59.2328
2245 | 0 | 0 | 59.0842
2246 | 0 | 0 | 58.9903
2247 | 0 | 0 | 58.8966
2248 | 0 | 0 | 58.8031
2249 | 0 | 0 | 58.7098
2250 | 6.2938 | 6.9289 | 59.0159
2251 | 12.3278 | 18.9433 | 60.6828
2252 | 0 | 0 | 63.9967
2253 | 1.3714 | 0 | 62.9219
2254 | 0 | 0 | 62.7313
2255 | 0 | 0 | 62.6288
2256 | 0 | 0 | 62.5265
2257 | 0 | 0 | 62.4245
2258 | 0 | 0 | 62.3228
2259 | 0 | 0 | 62.2212
2260 | 0 | 0 | 62.1199
2261 | 0 | 0 | 62.0189
2262 | 12.3462 | 13.521 | 60.0652
2263 | 1.3399 | 0 | 61.7698
2264 | 1.743 | 0 | 60.353
2265 | 0 | 0 | 60.1449
2266 | 0 | 0 | 60.0485
2267 | 0 | 0 | 59.9523
2268 | 0.84815 | 0 | 59.2579
2269 | 0 | 0 | 59.1093
2270 | 0 | 0 | 59.0153
2271 | 0 | 0 | 58.9216
2272 | 0 | 0 | 58.828
2273 | 0 | 0 | 58.7347
2274 | 6.2868 | 6.9269 | 59.0436
2275 | 12.3153 | 13.5845 | 58.9725
2276 | 0 | 0 | 59.9153
2277 | 1.2672 | 0 | 58.9252
2278 | 0 | 0 | 58.7508
2279 | 0 | 0 | 58.6576
2280 | 0 | 0 | 58.5647
2281 | 0 | 0 | 58.472
2282 | 0 | 0 | 58.3795
2283 | 0 | 0 | 58.2872
2284 | 0 | 0 | 58.1952
2285 | 0 | 0 | 58.1033
2286 | 12.0709 | 19.3536 | 59.9966
2287 | 1.3578 | 0 | 62.5544
2288 | 1.7663 | 0 | 61.1178
2289 | 0 | 0 | 60.9063
2290 | 0 | 0 | 60.8081
2291 | 0 | 0 | 60.7101
2292 | 0.85942 | 0 | 60.0058
2293 | 0 | 0 | 59.8548
2294 | 0 | 0 | 59.759
2295 | 0 | 0 | 59.6635
2296 | 0 | 0 | 59.5683
2297 | 0 | 0 | 59.4732
2298 | 6.363 | 6.8781 | 59.7076
2299 | 12.4436 | 13.6004 | 59.5452
2300 | 0 | 0 | 60.4668
2301 | 1.2789 | 0 | 59.467
2302 | 0 | 0 | 59.2905
2303 | 0 | 0 | 59.1961
2304 | 0 | 0 | 59.1019
2305 | 0 | 0 | 59.008
2306 | 0 | 0 | 58.9142
2307 | 0 | 0 | 58.8207
2308 | 0 | 0 | 58.7274
2309 | 0 | 0 | 58.6343
2310 | 12.1736 | 19.1656 | 60.4081
2311 | 1.3633 | 0 | 62.8564
2312 | 1.7735 | 0 | 61.4135
2313 | 0 | 0 | 61.2009
2314 | 0 | 0 | 61.102
2315 | 0 | 0 | 61.0033
2316 | 0.8629 | 0 | 60.2958
2317 | 0 | 0 | 60.1438
2318 | 0 | 0 | 60.0474
2319 | 0 | 0 | 59.9512
2320 | 0 | 0 | 59.8553
2321 | 0 | 0 | 59.7595
2322 | 6.1749 | 7.0639 | 59.2929
2323 | 12.5373 | 13.4065 | 59.9497
2324 | 0 | 0 | 60.819
2325 | 1.2856 | 0 | 59.8135
2326 | 0 | 0 | 59.6358
2327 | 0 | 0 | 59.5406
2328 | 0 | 0 | 59.4456
2329 | 0 | 0 | 59.3508
2330 | 0 | 0 | 59.2562
2331 | 0 | 0 | 59.1619
2332 | 0 | 0 | 59.0678
2333 | 0 | 0 | 58.9739
2334 | 12.2318 | 13.699 | 58.9331
2335 | 1.2631 | 0 | 59.0202
2336 | 1.6434 | 6.5052 | 61.4705
2337 | 0 | 0 | 62.4831
2338 | 0 | 0 | 62.3812
2339 | 0 | 0 | 62.2796
2340 | 0.88282 | 0 | 61.5547
2341 | 0 | 0 | 61.3985
2342 | 0 | 0 | 61.2991
2343 | 0 | 0 | 61.2
2344 | 0 | 0 | 61.1011
2345 | 0 | 0 | 61.0024
2346 | 6.3098 | 6.8414 | 60.3526
2347 | 12.5266 | 13.5822 | 60.1221
2348 | 0 | 0 | 61.9183
2349 | 1.3109 | 0 | 60.892
2350 | 0 | 0 | 60.71
2351 | 0 | 0 | 60.6123
2352 | 0 | 0 | 60.5148
2353 | 0 | 0 | 60.4175
2354 | 0 | 0 | 60.3205
2355 | 0 | 0 | 60.2236
2356 | 0 | 0 | 60.127
2357 | 0 | 0 | 60.0307
2358 | 12.4378 | 13.5386 | 59.7712
2359 | 1.2803 | 0 | 59.7787
2360 | 1.6656 | 0 | 58.4261
2361 | 0 | 0 | 58.2275
2362 | 0 | 0 | 58.1355
2363 | 0 | 0 | 58.0438
2364 | 0.85524 | 6.5265 | 61.9787
2365 | 0 | 0 | 62.2122
2366 | 0 | 0 | 62.1109
2367 | 0 | 0 | 62.0099
2368 | 0 | 0 | 61.9091
2369 | 0 | 0 | 61.8085
2370 | 6.2812 | 6.8373 | 60.2866
2371 | 12.2884 | 13.3372 | 60.1325
2372 | 0 | 0 | 62.7336
2373 | 1.3291 | 0 | 61.6922
2374 | 0 | 0 | 61.5072
2375 | 0 | 0 | 61.4076
2376 | 0 | 0 | 61.3082
2377 | 0 | 0 | 61.2091
2378 | 0 | 0 | 61.1101
2379 | 0 | 0 | 61.0115
2380 | 0 | 0 | 60.913
2381 | 0 | 0 | 60.8148
2382 | 12.5887 | 13.3191 | 60.3627
2383 | 1.2905 | 0 | 60.2674
2384 | 1.6788 | 0 | 58.9034
2385 | 0 | 0 | 58.7028
2386 | 0 | 0 | 58.6098
2387 | 0 | 0 | 58.517
2388 | 0.81699 | 6.4474 | 61.599
2389 | 0 | 0 | 62.6532
2390 | 0 | 0 | 62.5509
2391 | 0 | 0 | 62.4488
2392 | 0 | 0 | 62.347
2393 | 0 | 0 | 62.2454
2394 | 6.323 | 6.7152 | 60.6582
2395 | 12.3388 | 13.2185 | 60.3727
2396 | 0 | 0 | 62.912
2397 | 1.3314 | 0 | 61.8685
2398 | 0 | 0 | 61.6829
2399 | 0 | 0 | 61.5829
2400 | 0 | 0 | 61.4831
2401 | 0 | 0 | 61.3836
2402 | 0 | 0 | 61.2843
2403 | 0 | 0 | 61.1852
2404 | 0 | 0 | 61.0863
2405 | 0 | 0 | 60.9877
2406 | 12.6046 | 13.2437 | 60.4901
2407 | 1.2908 | 0 | 60.3692
2408 | 1.6792 | 0 | 59.0045
2409 | 0 | 0 | 58.8037
2410 | 0 | 0 | 58.7104
2411 | 0 | 0 | 58.6174
2412 | 0.81717 | 6.3988 | 61.6709
2413 | 0 | 0 | 62.7159
2414 | 0 | 0 | 62.6134
2415 | 0 | 0 | 62.5112
2416 | 0 | 0 | 62.4092
2417 | 0 | 0 | 62.3075
2418 | 6.3197 | 6.684 | 60.7119
2419 | 12.3274 | 13.195 | 60.4117
2420 | 0 | 0 | 62.9431
2421 | 1.3299 | 0 | 61.9005
2422 | 0 | 0 | 61.7149
2423 | 0 | 0 | 61.6148
2424 | 0 | 0 | 61.515
2425 | 0 | 0 | 61.4154
2426 | 0 | 0 | 61.316
2427 | 0 | 0 | 61.2168
2428 | 0 | 0 | 61.1179
2429 | 0 | 0 | 61.0192
2430 | 12.5902 | 13.2242 | 60.5206
2431 | 1.2892 | 0 | 60.3977
2432 | 1.6772 | 0 | 59.0345
2433 | 0 | 0 | 58.8337
2434 | 0 | 0 | 58.7404
2435 | 0 | 0 | 58.6473
2436 | 0.81615 | 6.3839 | 61.6929
2437 | 0 | 0 | 62.7351
2438 | 0 | 0 | 62.6326
2439 | 0 | 0 | 62.5303
2440 | 0 | 0 | 62.4283
2441 | 0 | 0 | 62.3265
2442 | 6.311 | 6.6715 | 60.7318
2443 | 12.3102 | 13.1806 | 60.4328
2444 | 0 | 0 | 62.9613
2445 | 1.3281 | 0 | 61.92
2446 | 0 | 0 | 61.7345
2447 | 0 | 0 | 61.6343
2448 | 0 | 0 | 61.5344
2449 | 0 | 0 | 61.4347
2450 | 0 | 0 | 61.3353
2451 | 0 | 0 | 61.2361
2452 | 0 | 0 | 61.1371
2453 | 0 | 0 | 61.0384
2454 | 12.5729 | 13.2094 | 60.5429
2455 | 1.2875 | 0 | 60.4199
2456 | 1.6749 | 0 | 59.0585
2457 | 0 | 0 | 58.8578
2458 | 0 | 0 | 58.7644
2459 | 0 | 0 | 58.6712
2460 | 0.81501 | 6.3719 | 61.7106
2461 | 0 | 0 | 62.7506
2462 | 0 | 0 | 62.648
2463 | 0 | 0 | 62.5457
2464 | 0 | 0 | 62.4437
2465 | 0 | 0 | 62.3419
2466 | 6.3018 | 6.6607 | 60.749
2467 | 12.2923 | 13.1669 | 60.4526
2468 | 0 | 0 | 62.9786
2469 | 1.3262 | 0 | 61.9385
2470 | 0 | 0 | 61.7531
2471 | 0 | 0 | 61.6529
2472 | 0 | 0 | 61.5529
2473 | 0 | 0 | 61.4532
2474 | 0 | 0 | 61.3537
2475 | 0 | 0 | 61.2545
2476 | 0 | 0 | 61.1555
2477 | 0 | 0 | 61.0567
2478 | 12.5552 | 13.1949 | 60.5646
2479 | 1.2857 | 0 | 60.4419
2480 | 1.6725 | 0 | 59.0821
2481 | 0 | 0 | 58.8815
2482 | 0 | 0 | 58.7881
2483 | 0 | 0 | 58.6948
2484 | 0.81386 | 6.3674 | 60.9167
2485 | 0 | 0 | 62.7735
2486 | 0 | 0 | 62.6709
2487 | 0 | 0 | 62.5685
2488 | 0 | 0 | 62.4664
2489 | 0 | 0 | 62.3646
2490 | 6.2934 | 6.6466 | 60.7719
2491 | 12.2751 | 13.1516 | 60.4756
2492 | 0 | 0 | 62.9982
2493 | 1.3244 | 0 | 61.9593
2494 | 0 | 0 | 61.774
2495 | 0 | 0 | 61.6738
2496 | 0 | 0 | 61.5738
2497 | 0 | 0 | 61.474
2498 | 0 | 0 | 61.3745
2499 | 0 | 0 | 61.2752
2500 | 0 | 0 | 61.1761
2501 | 0 | 0 | 61.0773
2502 | 12.5378 | 13.1795 | 60.588
2503 | 1.2839 | 0 | 60.4651
2504 | 1.6702 | 0 | 59.1071
2505 | 0 | 0 | 58.9066
2506 | 0 | 0 | 58.8131
2507 | 0 | 0 | 58.7198
2508 | 0.81271 | 6.3697 | 59.3106
2509 | 0 | 0 | 62.8047
2510 | 0 | 0 | 62.7021
2511 | 0 | 0 | 62.5997
2512 | 0 | 0 | 62.4975
2513 | 0 | 0 | 62.3955
2514 | 6.2858 | 6.6288 | 60.8014
2515 | 12.2588 | 13.1343 | 60.5021
2516 | 0 | 0 | 63.0204
2517 | 1.3226 | 0 | 61.9828
2518 | 0 | 0 | 61.7975
2519 | 0 | 0 | 61.6972
2520 | 0 | 0 | 61.5971
2521 | 0 | 0 | 61.4973
2522 | 0 | 0 | 61.3977
2523 | 0 | 0 | 61.2984
2524 | 0 | 0 | 61.1993
2525 | 0 | 0 | 61.1004
2526 | 12.3202 | 13.6756 | 60.0886
2527 | 1.2957 | 0 | 61.0233
2528 | 1.6855 | 0 | 59.6521
2529 | 0 | 0 | 59.4493
2530 | 0 | 0 | 59.3545
2531 | 0 | 0 | 59.2599
2532 | 0.82013 | 0 | 58.5871
2533 | 0 | 0 | 58.4419
2534 | 0 | 0 | 58.3495
2535 | 0 | 0 | 58.2573
2536 | 0 | 0 | 58.1653
2537 | 0 | 0 | 58.0735
2538 | 6.0888 | 6.9245 | 58.4976
2539 | 11.9703 | 19.0045 | 60.4238
2540 | 0 | 0 | 63.8393
2541 | 1.3408 | 0 | 62.7866
2542 | 0 | 0 | 62.5983
2543 | 0 | 0 | 62.4961
2544 | 0 | 0 | 62.3942
2545 | 0 | 0 | 62.2925
2546 | 0 | 0 | 62.191
2547 | 0 | 0 | 62.0898
2548 | 0 | 0 | 61.9888
2549 | 0 | 0 | 61.8881
2550 | 12.068 | 13.4712 | 60.0795
2551 | 1.314 | 0 | 61.8337
2552 | 1.7093 | 0 | 60.4422
2553 | 0 | 0 | 60.236
2554 | 0 | 0 | 60.1394
2555 | 0 | 0 | 60.043
2556 | 0.8316 | 0 | 59.36
2557 | 0 | 0 | 59.2123
2558 | 0 | 0 | 59.1181
2559 | 0 | 0 | 59.0241
2560 | 0 | 0 | 58.9303
2561 | 0 | 0 | 58.8367
2562 | 6.1683 | 6.9119 | 59.2055
2563 | 12.1075 | 13.5631 | 59.2636
2564 | 0 | 0 | 60.2391
2565 | 1.2483 | 0 | 59.2615
2566 | 0 | 0 | 59.0874
2567 | 0 | 0 | 58.9935
2568 | 0 | 0 | 58.8998
2569 | 0 | 0 | 58.8063
2570 | 0 | 0 | 58.713
2571 | 0 | 0 | 58.62
2572 | 0 | 0 | 58.5271
2573 | 0 | 0 | 58.4345
2574 | 11.8947 | 19.1374 | 60.3563
2575 | 1.3379 | 0 | 62.868
2576 | 1.7404 | 0 | 61.45
2577 | 0 | 0 | 61.2394
2578 | 0 | 0 | 61.1404
2579 | 0 | 0 | 61.0416
2580 | 0.84669 | 0 | 60.3454
2581 | 0 | 0 | 60.1944
2582 | 0 | 0 | 60.0979
2583 | 0 | 0 | 60.0016
2584 | 0 | 0 | 59.9055
2585 | 0 | 0 | 59.8097
2586 | 6.0594 | 7.0485 | 59.4031
2587 | 12.3309 | 13.2954 | 60.1451
2588 | 0 | 0 | 61.0188
2589 | 1.2654 | 0 | 60.027
2590 | 0 | 0 | 59.8501
2591 | 0 | 0 | 59.7543
2592 | 0 | 0 | 59.6588
2593 | 0 | 0 | 59.5636
2594 | 0 | 0 | 59.4685
2595 | 0 | 0 | 59.3737
2596 | 0 | 0 | 59.2791
2597 | 0 | 0 | 59.1847
2598 | 12.0441 | 13.6704 | 59.2374
2599 | 1.246 | 0 | 59.3643
2600 | 1.621 | 6.3446 | 61.7378
2601 | 0 | 0 | 62.7213
2602 | 0 | 0 | 62.6188
2603 | 0 | 0 | 62.5166
2604 | 0.86974 | 0 | 61.8003
2605 | 0 | 0 | 61.6444
2606 | 0 | 0 | 61.5444
2607 | 0 | 0 | 61.4447
2608 | 0 | 0 | 61.3453
2609 | 0 | 0 | 61.246
2610 | 6.2155 | 6.7875 | 60.6259
2611 | 11.9519 | 13.5039 | 59.8464
2612 | 0 | 0 | 62.5755
2613 | 1.3019 | 0 | 61.5537
2614 | 0 | 0 | 61.3708
2615 | 0 | 0 | 61.2715
2616 | 0 | 0 | 61.1724
2617 | 0 | 0 | 61.0736
2618 | 0 | 0 | 60.975
2619 | 0 | 0 | 60.8767
2620 | 0 | 0 | 60.7785
2621 | 0 | 0 | 60.6806
2622 | 12.3413 | 13.2985 | 60.3639
2623 | 1.268 | 0 | 60.3241
2624 | 1.6495 | 0 | 58.982
2625 | 0 | 0 | 58.7831
2626 | 0 | 0 | 58.6899
2627 | 0 | 0 | 58.5969
2628 | 0.80259 | 6.4032 | 61.6634
2629 | 0 | 0 | 62.7101
2630 | 0 | 0 | 62.6077
2631 | 0 | 0 | 62.5055
2632 | 0 | 0 | 62.4035
2633 | 0 | 0 | 62.3018
2634 | 6.2165 | 6.6482 | 60.7545
2635 | 12.1421 | 13.0999 | 60.5332
2636 | 0 | 0 | 63.0587
2637 | 1.3115 | 0 | 62.0288
2638 | 0 | 0 | 61.8442
2639 | 0 | 0 | 61.7438
2640 | 0 | 0 | 61.6436
2641 | 0 | 0 | 61.5437
2642 | 0 | 0 | 61.444
2643 | 0 | 0 | 61.3445
2644 | 0 | 0 | 61.2453
2645 | 0 | 0 | 61.1463
2646 | 12.2183 | 13.6633 | 60.1879
2647 | 1.2864 | 0 | 61.1445
2648 | 1.6734 | 0 | 59.7821
2649 | 0 | 0 | 59.5797
2650 | 0 | 0 | 59.4846
2651 | 0 | 0 | 59.3898
2652 | 0.81416 | 0 | 58.7208
2653 | 0 | 0 | 58.5757
2654 | 0 | 0 | 58.483
2655 | 0 | 0 | 58.3904
2656 | 0 | 0 | 58.2981
2657 | 0 | 0 | 58.206
2658 | 6.046 | 6.9204 | 58.6523
2659 | 11.8952 | 18.9029 | 60.5948
2660 | 0 | 0 | 63.9807
2661 | 1.3321 | 0 | 62.9337
2662 | 0 | 0 | 62.7456
2663 | 0 | 0 | 62.6431
2664 | 0 | 0 | 62.5408
2665 | 0 | 0 | 62.4387
2666 | 0 | 0 | 62.3369
2667 | 0 | 0 | 62.2354
2668 | 0 | 0 | 62.1341
2669 | 0 | 0 | 62.033
2670 | 11.988 | 13.3713 | 60.2362
2671 | 1.3049 | 0 | 61.9691
2672 | 1.6975 | 0 | 60.5861
2673 | 0 | 0 | 60.3803
2674 | 0 | 0 | 60.2833
2675 | 0 | 0 | 60.1866
2676 | 0.82579 | 0 | 59.5074
2677 | 0 | 0 | 59.3597
2678 | 0 | 0 | 59.2651
2679 | 0 | 0 | 59.1707
2680 | 0 | 0 | 59.0766
2681 | 0 | 0 | 58.9827
2682 | 6.1263 | 6.9005 | 59.369
2683 | 12.0331 | 13.5559 | 59.4722
2684 | 0 | 0 | 60.4593
2685 | 1.2415 | 0 | 59.4859
2686 | 0 | 0 | 59.3117
2687 | 0 | 0 | 59.2173
2688 | 0 | 0 | 59.123
2689 | 0 | 0 | 59.029
2690 | 0 | 0 | 58.9352
2691 | 0 | 0 | 58.8416
2692 | 0 | 0 | 58.7483
2693 | 0 | 0 | 58.6551
2694 | 11.8313 | 19.0155 | 60.5729
2695 | 1.3299 | 0 | 63.0488
2696 | 1.73 | 0 | 61.6381
2697 | 0 | 0 | 61.4277
2698 | 0 | 0 | 61.3283
2699 | 0 | 0 | 61.2291
2700 | 0.84154 | 0 | 60.5361
2701 | 0 | 0 | 60.3849
2702 | 0 | 0 | 60.288
2703 | 0 | 0 | 60.1912
2704 | 0 | 0 | 60.0947
2705 | 0 | 0 | 59.9984
2706 | 6.0223 | 7.034 | 59.6064
2707 | 12.2606 | 13.1831 | 60.3397
2708 | 0 | 0 | 61.1915
2709 | 1.2573 | 0 | 60.205
2710 | 0 | 0 | 60.0281
2711 | 0 | 0 | 59.932
2712 | 0 | 0 | 59.836
2713 | 0 | 0 | 59.7403
2714 | 0 | 0 | 59.6449
2715 | 0 | 0 | 59.5496
2716 | 0 | 0 | 59.4546
2717 | 0 | 0 | 59.3598
2718 | 11.9684 | 13.6544 | 59.4473
2719 | 1.239 | 0 | 59.5895
2720 | 1.6119 | 0 | 58.2779
2721 | 0 | 0 | 58.0831
2722 | 0 | 6.3461 | 60.0575
2723 | 0 | 0 | 62.7747
2724 | 0.86571 | 0 | 62.0606
2725 | 0 | 0 | 61.9043
2726 | 0 | 0 | 61.8038
2727 | 0 | 0 | 61.7035
2728 | 0 | 0 | 61.6034
2729 | 0 | 0 | 61.5036
2730 | 6.0725 | 6.8681 | 60.1138
2731 | 11.9322 | 13.2488 | 60.1895
2732 | 0 | 0 | 62.8208
2733 | 1.2955 | 0 | 61.8028
2734 | 0 | 0 | 61.6197
2735 | 0 | 0 | 61.5198
2736 | 0 | 0 | 61.4202
2737 | 0 | 0 | 61.3208
2738 | 0 | 0 | 61.2216
2739 | 0 | 0 | 61.1227
2740 | 0 | 0 | 61.024
2741 | 0 | 0 | 60.9255
2742 | 12.2764 | 13.1625 | 60.5815
2743 | 1.2602 | 0 | 60.5186
2744 | 1.6392 | 0 | 59.1837
2745 | 0 | 0 | 58.985
2746 | 0 | 0 | 58.8913
2747 | 0 | 0 | 58.7978
2748 | 0.79753 | 0 | 58.1421
2749 | 0 | 6.3633 | 60.071
2750 | 0 | 0 | 62.7959
2751 | 0 | 0 | 62.6932
2752 | 0 | 0 | 62.5908
2753 | 0 | 0 | 62.4887
2754 | 6.1785 | 6.5436 | 60.9289
2755 | 12.0573 | 13.0028 | 60.6843
2756 | 0 | 0 | 63.1842
2757 | 1.3021 | 0 | 62.1606
2758 | 0 | 0 | 61.9762
2759 | 0 | 0 | 61.8755
2760 | 0 | 0 | 61.7751
2761 | 0 | 0 | 61.6748
2762 | 0 | 0 | 61.5748
2763 | 0 | 0 | 61.475
2764 | 0 | 0 | 61.3755
2765 | 0 | 0 | 61.2762
2766 | 11.7225 | 13.6135 | 59.7186
2767 | 1.2856 | 0 | 61.6196
2768 | 1.6724 | 0 | 60.2565
2769 | 0 | 0 | 60.0531
2770 | 0 | 0 | 59.9569
2771 | 0 | 0 | 59.861
2772 | 0.81355 | 0 | 59.1912
2773 | 0 | 0 | 59.045
2774 | 0 | 0 | 58.9512
2775 | 0 | 0 | 58.8576
2776 | 0 | 0 | 58.7642
2777 | 0 | 0 | 58.671
2778 | 6.0405 | 6.9112 | 59.1141
2779 | 11.8845 | 13.5389 | 59.3136
2780 | 0 | 0 | 60.3245
2781 | 1.228 | 0 | 59.361
2782 | 0 | 0 | 59.188
2783 | 0 | 0 | 59.0939
2784 | 0 | 0 | 58.9999
2785 | 0 | 0 | 58.9062
2786 | 0 | 0 | 58.8127
2787 | 0 | 0 | 58.7194
2788 | 0 | 0 | 58.6263
2789 | 0 | 0 | 58.5334
2790 | 11.7087 | 19.0178 | 60.521
2791 | 1.3191 | 0 | 63.0311
2792 | 1.7158 | 0 | 61.6313
2793 | 0 | 0 | 61.4218
2794 | 0 | 0 | 61.3224
2795 | 0 | 0 | 61.2232
2796 | 0.8346 | 0 | 60.5351
2797 | 0 | 0 | 60.3844
2798 | 0 | 0 | 60.2874
2799 | 0 | 0 | 60.1907
2800 | 0 | 0 | 60.0941
2801 | 0 | 0 | 59.9978
2802 | 5.9729 | 7.0286 | 59.6321
2803 | 12.1726 | 13.1389 | 60.4037
2804 | 0 | 0 | 61.2583
2805 | 1.2488 | 0 | 60.2777
2806 | 0 | 0 | 60.1012
2807 | 0 | 0 | 60.0048
2808 | 0 | 0 | 59.9088
2809 | 0 | 0 | 59.8129
2810 | 0 | 0 | 59.7173
2811 | 0 | 0 | 59.6219
2812 | 0 | 0 | 59.5267
2813 | 0 | 0 | 59.4317
2814 | 11.8896 | 13.6434 | 59.5591
2815 | 1.2318 | 0 | 59.7182
2816 | 1.6024 | 0 | 58.4134
2817 | 0 | 0 | 58.2188
2818 | 0 | 0 | 58.1269
2819 | 0 | 0 | 58.0352
2820 | 0.82424 | 6.5163 | 61.985
2821 | 0 | 0 | 62.2196
2822 | 0 | 0 | 62.1183
2823 | 0 | 0 | 62.0173
2824 | 0 | 0 | 61.9165
2825 | 0 | 0 | 61.8159
2826 | 6.0604 | 6.816 | 60.4153
2827 | 11.9018 | 13.1141 | 60.4429
2828 | 0 | 0 | 63.0203
2829 | 1.2902 | 0 | 62.0055
2830 | 0 | 0 | 61.8223
2831 | 0 | 0 | 61.7219
2832 | 0 | 0 | 61.6218
2833 | 0 | 0 | 61.5219
2834 | 0 | 0 | 61.4223
2835 | 0 | 0 | 61.3229
2836 | 0 | 0 | 61.2237
2837 | 0 | 0 | 61.1247
2838 | 12.025 | 13.6455 | 60.2714
2839 | 1.2688 | 0 | 61.2705
2840 | 1.6504 | 0 | 59.925
2841 | 0 | 0 | 59.7238
2842 | 0 | 0 | 59.6284
2843 | 0 | 0 | 59.5332
2844 | 0.80287 | 0 | 58.8718
2845 | 0 | 0 | 58.7271
2846 | 0 | 0 | 58.634
2847 | 0 | 0 | 58.5411
2848 | 0 | 0 | 58.4484
2849 | 0 | 0 | 58.356
2850 | 5.9653 | 6.9122 | 58.8441
2851 | 11.7536 | 13.5239 | 59.127
2852 | 0 | 0 | 60.159
2853 | 1.2161 | 0 | 59.2044
2854 | 0 | 0 | 59.0325
2855 | 0 | 0 | 58.9387
2856 | 0 | 0 | 58.8451
2857 | 0 | 0 | 58.7517
2858 | 0 | 0 | 58.6586
2859 | 0 | 0 | 58.5657
2860 | 0 | 0 | 58.473
2861 | 0 | 0 | 58.3805
2862 | 11.6011 | 19.0398 | 60.4359
2863 | 1.3099 | 0 | 62.9848
2864 | 1.7039 | 0 | 61.594
2865 | 0 | 0 | 61.3854
2866 | 0 | 0 | 61.2861
2867 | 0 | 0 | 61.187
2868 | 0.82875 | 0 | 60.5031
2869 | 0 | 0 | 60.3528
2870 | 0 | 0 | 60.2559
2871 | 0 | 0 | 60.1593
2872 | 0 | 0 | 60.0628
2873 | 0 | 0 | 59.9666
2874 | 5.9314 | 7.0258 | 59.6238
2875 | 12.0994 | 13.1147 | 60.4335
2876 | 0 | 0 | 61.2946
2877 | 1.2418 | 0 | 60.3187
2878 | 0 | 0 | 60.1425
2879 | 0 | 0 | 60.0461
2880 | 0 | 0 | 59.9499
2881 | 0 | 0 | 59.854
2882 | 0 | 0 | 59.7582
2883 | 0 | 0 | 59.6627
2884 | 0 | 0 | 59.5674
2885 | 0 | 0 | 59.4724
2886 | 11.8261 | 13.6354 | 59.6324
2887 | 1.226 | 0 | 59.8054
2888 | 1.5949 | 0 | 58.506
2889 | 0 | 0 | 58.3118
2890 | 0 | 0 | 58.2196
2891 | 0 | 0 | 58.1277
2892 | 0.77591 | 6.6088 | 61.3331
2893 | 0 | 0 | 62.4205
2894 | 0 | 0 | 62.3188
2895 | 0 | 0 | 62.2173
2896 | 0 | 0 | 62.116
2897 | 0 | 0 | 62.0149
2898 | 6.0464 | 6.7233 | 60.5917
2899 | 11.8608 | 13.0341 | 60.5774
2900 | 0 | 0 | 63.1279
2901 | 1.285 | 0 | 62.1165
2902 | 0 | 0 | 61.9333
2903 | 0 | 0 | 61.8327
2904 | 0 | 0 | 61.7323
2905 | 0 | 0 | 61.6322
2906 | 0 | 0 | 61.5323
2907 | 0 | 0 | 61.4326
2908 | 0 | 0 | 61.3332
2909 | 0 | 0 | 61.234
2910 | 11.5685 | 13.5784 | 59.7539
2911 | 1.2712 | 0 | 61.6793
2912 | 1.6535 | 0 | 60.3303
2913 | 0 | 0 | 60.1279
2914 | 0 | 0 | 60.0315
2915 | 0 | 0 | 59.9354
2916 | 0.80429 | 0 | 59.272
2917 | 0 | 0 | 59.1262
2918 | 0 | 0 | 59.0322
2919 | 0 | 0 | 58.9384
2920 | 0 | 0 | 58.8448
2921 | 0 | 0 | 58.7514
2922 | 5.9742 | 6.9013 | 59.2272
2923 | 11.768 | 13.5269 | 59.4988
2924 | 0 | 0 | 60.5281
2925 | 1.2174 | 0 | 59.5715
2926 | 0 | 0 | 59.3987
2927 | 0 | 0 | 59.304
2928 | 0 | 0 | 59.2096
2929 | 0 | 0 | 59.1154
2930 | 0 | 0 | 59.0214
2931 | 0 | 0 | 58.9276
2932 | 0 | 0 | 58.834
2933 | 0 | 0 | 58.7407
2934 | 11.6107 | 13.6344 | 59.0292
2935 | 1.2066 | 0 | 59.2553
2936 | 1.5696 | 6.3678 | 61.6812
2937 | 0 | 0 | 62.6724
2938 | 0 | 0 | 62.5701
2939 | 0 | 0 | 62.468
2940 | 0.84487 | 0 | 61.7694
2941 | 0 | 0 | 61.6151
2942 | 0 | 0 | 61.5152
2943 | 0 | 0 | 61.4156
2944 | 0 | 0 | 61.3162
2945 | 0 | 0 | 61.217
2946 | 5.9252 | 6.8849 | 59.9192
2947 | 11.6797 | 13.2181 | 60.1657
2948 | 0 | 0 | 62.8327
2949 | 1.2724 | 0 | 61.8311
2950 | 0 | 0 | 61.6494
2951 | 0 | 0 | 61.5494
2952 | 0 | 0 | 61.4497
2953 | 0 | 0 | 61.3502
2954 | 0 | 0 | 61.251
2955 | 0 | 0 | 61.152
2956 | 0 | 0 | 61.0532
2957 | 0 | 0 | 60.9547
2958 | 11.8647 | 13.6385 | 60.1936
2959 | 1.2543 | 0 | 61.2293
2960 | 1.6315 | 0 | 59.8983
2961 | 0 | 0 | 59.6984
2962 | 0 | 0 | 59.603
2963 | 0 | 0 | 59.5078
2964 | 0.79359 | 0 | 58.8531
2965 | 0 | 0 | 58.709
2966 | 0 | 0 | 58.6159
2967 | 0 | 0 | 58.5231
2968 | 0 | 0 | 58.4305
2969 | 0 | 0 | 58.3381
2970 | 5.8991 | 6.9049 | 58.8606
2971 | 11.6376 | 13.5118 | 59.2158
2972 | 0 | 0 | 60.2662
2973 | 1.2055 | 0 | 59.3188
2974 | 0 | 0 | 59.1473
2975 | 0 | 0 | 59.0532
2976 | 0 | 0 | 58.9594
2977 | 0 | 0 | 58.8657
2978 | 0 | 0 | 58.7723
2979 | 0 | 0 | 58.6791
2980 | 0 | 0 | 58.5861
2981 | 0 | 0 | 58.4934
2982 | 11.5042 | 13.6224 | 58.8382
2983 | 1.1969 | 0 | 59.0884
2984 | 1.557 | 6.4346 | 61.5629
2985 | 0 | 0 | 62.5676
2986 | 0 | 0 | 62.4655
2987 | 0 | 0 | 62.3637
2988 | 0.83954 | 0 | 61.6691
2989 | 0 | 0 | 61.5154
2990 | 0 | 0 | 61.4158
2991 | 0 | 0 | 61.3164
2992 | 0 | 0 | 61.2172
2993 | 0 | 0 | 61.1183
2994 | 6.0014 | 6.7811 | 60.6202
2995 | 11.5794 | 13.34 | 60.0394
2996 | 0 | 0 | 62.7687
2997 | 1.2654 | 0 | 61.7721
2998 | 0 | 0 | 61.591
2999 | 0 | 0 | 61.4912
3000 | 0 | 0 | 61.3916
3001 | 0 | 0 | 61.2923
3002 | 0 | 0 | 61.1932
3003 | 0 | 0 | 61.0943
3004 | 0 | 0 | 60.9957
3005 | 0 | 0 | 60.8973
3006 | 11.8023 | 13.6352 | 60.1717
3007 | 1.2486 | 0 | 61.2217
3008 | 1.6241 | 0 | 59.8963
3009 | 0 | 0 | 59.6968
3010 | 0 | 0 | 59.6014
3011 | 0 | 0 | 59.5063
3012 | 0.78998 | 0 | 58.8541
3013 | 0 | 0 | 58.7102
3014 | 0 | 0 | 58.6172
3015 | 0 | 0 | 58.5243
3016 | 0 | 0 | 58.4317
3017 | 0 | 0 | 58.3393
3018 | 5.8733 | 6.9022 | 58.8751
3019 | 11.5924 | 13.5071 | 59.2586
3020 | 0 | 0 | 60.3162
3021 | 1.2014 | 0 | 59.3715
3022 | 0 | 0 | 59.2002
3023 | 0 | 0 | 59.106
3024 | 0 | 0 | 59.012
3025 | 0 | 0 | 58.9183
3026 | 0 | 0 | 58.8247
3027 | 0 | 0 | 58.7314
3028 | 0 | 0 | 58.6383
3029 | 0 | 0 | 58.5454
3030 | 11.4665 | 13.6186 | 58.9102
3031 | 1.1935 | 0 | 59.1687
3032 | 1.5525 | 6.3975 | 61.6249
3033 | 0 | 0 | 62.6229
3034 | 0 | 0 | 62.5206
3035 | 0 | 0 | 62.4186
3036 | 0.83686 | 0 | 61.7258
3037 | 0 | 0 | 61.5722
3038 | 0 | 0 | 61.4724
3039 | 0 | 0 | 61.3729
3040 | 0 | 0 | 61.2736
3041 | 0 | 0 | 61.1745
3042 | 5.8684 | 6.8817 | 59.9087
3043 | 11.5807 | 13.1793 | 60.2089
3044 | 0 | 0 | 62.8779
3045 | 1.2627 | 0 | 61.883
3046 | 0 | 0 | 61.7017
3047 | 0 | 0 | 61.6017
3048 | 0 | 0 | 61.5018
3049 | 0 | 0 | 61.4022
3050 | 0 | 0 | 61.3029
3051 | 0 | 0 | 61.2037
3052 | 0 | 0 | 61.1048
3053 | 0 | 0 | 61.0062
3054 | 11.777 | 13.6272 | 60.2906
3055 | 1.2463 | 0 | 61.3451
3056 | 1.6211 | 0 | 60.0216
3057 | 0 | 0 | 59.8221
3058 | 0 | 0 | 59.7264
3059 | 0 | 0 | 59.631
3060 | 0.78844 | 0 | 58.9795
3061 | 0 | 0 | 58.8354
3062 | 0 | 0 | 58.7421
3063 | 0 | 0 | 58.649
3064 | 0 | 0 | 58.5561
3065 | 0 | 0 | 58.4634
3066 | 5.8622 | 6.9013 | 59.0049
3067 | 11.5728 | 13.5051 | 59.4005
3068 | 0 | 0 | 60.4609
3069 | 1.1996 | 0 | 59.5171
3070 | 0 | 0 | 59.3455
3071 | 0 | 0 | 59.251
3072 | 0 | 0 | 59.1566
3073 | 0 | 0 | 59.0626
3074 | 0 | 0 | 58.9687
3075 | 0 | 0 | 58.875
3076 | 0 | 0 | 58.7816
3077 | 0 | 0 | 58.6884
3078 | 11.4494 | 13.6173 | 59.0621
3079 | 1.1919 | 0 | 59.3242
3080 | 1.5505 | 6.3288 | 61.7417
3081 | 0 | 0 | 62.7268
3082 | 0 | 0 | 62.6243
3083 | 0 | 0 | 62.5221
3084 | 0.83497 | 0 | 61.8303
3085 | 0 | 0 | 61.6765
3086 | 0 | 0 | 61.5765
3087 | 0 | 0 | 61.4768
3088 | 0 | 0 | 61.3772
3089 | 0 | 0 | 61.2779
3090 | 5.8547 | 6.8746 | 60.0174
3091 | 11.5558 | 13.1226 | 60.3127
3092 | 0 | 0 | 62.9613
3093 | 1.2594 | 0 | 61.9685
3094 | 0 | 0 | 61.7873
3095 | 0 | 0 | 61.6871
3096 | 0 | 0 | 61.587
3097 | 0 | 0 | 61.4872
3098 | 0 | 0 | 61.3877
3099 | 0 | 0 | 61.2883
3100 | 0 | 0 | 61.1892
3101 | 0 | 0 | 61.0904
3102 | 11.7459 | 13.6145 | 60.387
3103 | 1.2433 | 0 | 61.4452
3104 | 1.6172 | 0 | 60.1243
3105 | 0 | 0 | 59.9247
3106 | 0 | 0 | 59.8288
3107 | 0 | 0 | 59.7332
3108 | 0.78652 | 0 | 59.0828
3109 | 0 | 0 | 58.9386
3110 | 0 | 0 | 58.845
3111 | 0 | 0 | 58.7517
3112 | 0 | 0 | 58.6585
3113 | 0 | 0 | 58.5656
3114 | 5.8482 | 6.8977 | 59.113
3115 | 11.548 | 13.5027 | 59.5234
3116 | 0 | 0 | 60.5876
3117 | 1.1973 | 0 | 59.6451
3118 | 0 | 0 | 59.4734
3119 | 0 | 0 | 59.3785
3120 | 0 | 0 | 59.2839
3121 | 0 | 0 | 59.1895
3122 | 0 | 0 | 59.0953
3123 | 0 | 0 | 59.0014
3124 | 0 | 0 | 58.9076
3125 | 0 | 0 | 58.8141
3126 | 11.4282 | 13.6154 | 59.1991
3127 | 1.19 | 0 | 59.4657
3128 | 1.548 | 0 | 58.2027
3129 | 0 | 6.3326 | 59.2619
3130 | 0 | 0 | 62.7869
3131 | 0 | 0 | 62.6843
3132 | 0.83404 | 0 | 61.9927
3133 | 0 | 0 | 61.8386
3134 | 0 | 0 | 61.7382
3135 | 0 | 0 | 61.6381
3136 | 0 | 0 | 61.5382
3137 | 0 | 0 | 61.4385
3138 | 5.8478 | 6.8551 | 60.1752
3139 | 11.5403 | 13.051 | 60.4485
3140 | 0 | 0 | 63.0682
3141 | 1.2566 | 0 | 62.077
3142 | 0 | 0 | 61.8958
3143 | 0 | 0 | 61.7952
3144 | 0 | 0 | 61.6949
3145 | 0 | 0 | 61.5949
3146 | 0 | 0 | 61.4951
3147 | 0 | 0 | 61.3955
3148 | 0 | 0 | 61.2961
3149 | 0 | 0 | 61.197
3150 | 11.3121 | 13.4933 | 59.8369
3151 | 1.2466 | 0 | 61.7917
3152 | 1.6214 | 0 | 60.4667
3153 | 0 | 0 | 60.266
3154 | 0 | 0 | 60.1693
3155 | 0 | 0 | 60.0729
3156 | 0.78855 | 0 | 59.4202
3157 | 0 | 0 | 59.2751
3158 | 0 | 0 | 59.1807
3159 | 0 | 0 | 59.0866
3160 | 0 | 0 | 58.9926
3161 | 0 | 0 | 58.8989
3162 | 5.8613 | 6.8842 | 59.43
3163 | 11.5698 | 13.5066 | 59.8244
3164 | 0 | 0 | 60.8848
3165 | 1.1993 | 0 | 59.9401
3166 | 0 | 0 | 59.7675
3167 | 0 | 0 | 59.672
3168 | 0 | 0 | 59.5767
3169 | 0 | 0 | 59.4816
3170 | 0 | 0 | 59.3868
3171 | 0 | 0 | 59.2921
3172 | 0 | 0 | 59.1977
3173 | 0 | 0 | 59.1035
3174 | 11.4444 | 13.6164 | 59.4788
3175 | 1.1915 | 0 | 59.7411
3176 | 1.5498 | 0 | 58.4759
3177 | 0 | 0 | 58.2845
3178 | 0 | 0 | 58.1925
3179 | 0 | 0 | 58.1007
3180 | 0.75383 | 6.6071 | 61.3206
3181 | 0 | 0 | 62.4092
3182 | 0 | 0 | 62.3075
3183 | 0 | 0 | 62.206
3184 | 0 | 0 | 62.1047
3185 | 0 | 0 | 62.0037
3186 | 5.8894 | 6.6701 | 60.6544
3187 | 11.579 | 12.8903 | 60.7608
3188 | 0 | 0 | 63.3028
3189 | 1.2571 | 0 | 62.3107
3190 | 0 | 0 | 62.1289
3191 | 0 | 0 | 62.0278
3192 | 0 | 0 | 61.927
3193 | 0 | 0 | 61.8264
3194 | 0 | 0 | 61.726
3195 | 0 | 0 | 61.6259
3196 | 0 | 0 | 61.526
3197 | 0 | 0 | 61.4263
3198 | 11.314 | 13.3864 | 60.028
3199 | 1.2448 | 0 | 61.9378
3200 | 1.619 | 0 | 60.6141
3201 | 0 | 0 | 60.4133
3202 | 0 | 0 | 60.3162
3203 | 0 | 0 | 60.2194
3204 | 0.78734 | 0 | 59.5672
3205 | 0 | 0 | 59.4218
3206 | 0 | 0 | 59.3271
3207 | 0 | 0 | 59.2326
3208 | 0 | 0 | 59.1383
3209 | 0 | 0 | 59.0443
3210 | 5.8521 | 6.8755 | 59.5754
3211 | 11.552 | 13.4781 | 59.9668
3212 | 0 | 0 | 61.0214
3213 | 1.1973 | 0 | 60.0777
3214 | 0 | 0 | 59.905
3215 | 0 | 0 | 59.8091
3216 | 0 | 0 | 59.7135
3217 | 0 | 0 | 59.6181
3218 | 0 | 0 | 59.5229
3219 | 0 | 0 | 59.428
3220 | 0 | 0 | 59.3332
3221 | 0 | 0 | 59.2387
3222 | 11.4246 | 13.6096 | 59.6214
3223 | 1.1896 | 0 | 59.887
3224 | 1.5474 | 0 | 58.6232
3225 | 0 | 0 | 58.4317
3226 | 0 | 0 | 58.3393
3227 | 0 | 0 | 58.2471
3228 | 0.75262 | 6.5426 | 61.4303
3229 | 0 | 0 | 62.5067
3230 | 0 | 0 | 62.4047
3231 | 0 | 0 | 62.303
3232 | 0 | 0 | 62.2015
3233 | 0 | 0 | 62.1003
3234 | 5.8748 | 6.6179 | 60.7423
3235 | 11.5441 | 12.8448 | 60.8329
3236 | 0 | 0 | 63.362
3237 | 1.2531 | 0 | 62.3725
3238 | 0 | 0 | 62.1908
3239 | 0 | 0 | 62.0896
3240 | 0 | 0 | 61.9886
3241 | 0 | 0 | 61.8878
3242 | 0 | 0 | 61.7873
3243 | 0 | 0 | 61.6871
3244 | 0 | 0 | 61.587
3245 | 0 | 0 | 61.4872
3246 | 11.2776 | 13.3433 | 60.0951
3247 | 1.2407 | 0 | 61.9962
3248 | 1.6137 | 0 | 60.6763
3249 | 0 | 0 | 60.4757
3250 | 0 | 0 | 60.3785
3251 | 0 | 0 | 60.2815
3252 | 0.78473 | 0 | 59.631
3253 | 0 | 0 | 59.4856
3254 | 0 | 0 | 59.3908
3255 | 0 | 0 | 59.2961
3256 | 0 | 0 | 59.2017
3257 | 0 | 0 | 59.1075
3258 | 5.8332 | 6.8705 | 59.6465
3259 | 11.5171 | 13.4341 | 60.0404
3260 | 0 | 0 | 61.088
3261 | 1.1935 | 0 | 60.1468
3262 | 0 | 0 | 59.9741
3263 | 0 | 0 | 59.8781
3264 | 0 | 0 | 59.7823
3265 | 0 | 0 | 59.6867
3266 | 0 | 0 | 59.5914
3267 | 0 | 0 | 59.4963
3268 | 0 | 0 | 59.4014
3269 | 0 | 0 | 59.3067
3270 | 11.3895 | 13.6029 | 59.706
3271 | 1.1864 | 0 | 59.9788
3272 | 1.5432 | 0 | 58.7179
3273 | 0 | 0 | 58.5264
3274 | 0 | 0 | 58.4338
3275 | 0 | 0 | 58.3414
3276 | 0.75054 | 6.5003 | 61.5013
3277 | 0 | 0 | 62.5698
3278 | 0 | 0 | 62.4677
3279 | 0 | 0 | 62.3659
3280 | 0 | 0 | 62.2642
3281 | 0 | 0 | 62.1628
3282 | 5.856 | 6.5806 | 60.8034
3283 | 11.5049 | 12.8066 | 60.8908
3284 | 0 | 0 | 63.4109
3285 | 1.2488 | 0 | 62.4243
3286 | 0 | 0 | 62.2427
3287 | 0 | 0 | 62.1414
3288 | 0 | 0 | 62.0403
3289 | 0 | 0 | 61.9394
3290 | 0 | 0 | 61.8388
3291 | 0 | 0 | 61.7384
3292 | 0 | 0 | 61.6382
3293 | 0 | 0 | 61.5383
3294 | 11.239 | 13.3039 | 60.155
3295 | 1.2365 | 0 | 62.0494
3296 | 1.6082 | 0 | 60.7336
3297 | 0 | 0 | 60.5331
3298 | 0 | 0 | 60.4358
3299 | 0 | 0 | 60.3387
3300 | 0.78203 | 0 | 59.69
3301 | 0 | 0 | 59.5446
3302 | 0 | 0 | 59.4496
3303 | 0 | 0 | 59.3549
3304 | 0 | 0 | 59.2603
3305 | 0 | 0 | 59.166
3306 | 5.8137 | 6.8657 | 59.7134
3307 | 11.4814 | 13.3917 | 60.1111
3308 | 0 | 0 | 61.1522
3309 | 1.1896 | 0 | 60.2135
3310 | 0 | 0 | 60.041
3311 | 0 | 0 | 59.9448
3312 | 0 | 0 | 59.8488
3313 | 0 | 0 | 59.7531
3314 | 0 | 0 | 59.6576
3315 | 0 | 0 | 59.5624
3316 | 0 | 0 | 59.4673
3317 | 0 | 0 | 59.3725
3318 | 11.3539 | 13.5962 | 59.7887
3319 | 1.1831 | 0 | 60.0688
3320 | 1.5389 | 0 | 58.8109
3321 | 0 | 0 | 58.6194
3322 | 0 | 0 | 58.5266
3323 | 0 | 0 | 58.434
3324 | 0.74843 | 6.4587 | 61.5711
3325 | 0 | 0 | 62.6318
3326 | 0 | 0 | 62.5296
3327 | 0 | 0 | 62.4276
3328 | 0 | 0 | 62.3258
3329 | 0 | 0 | 62.2243
3330 | 5.8371 | 6.5439 | 60.8637
3331 | 11.4655 | 12.7687 | 60.9482
3332 | 0 | 0 | 63.4594
3333 | 1.2446 | 0 | 62.4758
3334 | 0 | 0 | 62.2943
3335 | 0 | 0 | 62.1928
3336 | 0 | 0 | 62.0916
3337 | 0 | 0 | 61.9906
3338 | 0 | 0 | 61.8899
3339 | 0 | 0 | 61.7894
3340 | 0 | 0 | 61.6891
3341 | 0 | 0 | 61.5891
3342 | 11.2003 | 13.2646 | 60.2147
3343 | 1.2323 | 0 | 62.1025
3344 | 1.6028 | 0 | 60.7906
3345 | 0 | 0 | 60.5904
3346 | 0 | 0 | 60.4929
3347 | 0 | 0 | 60.3957
3348 | 0.77934 | 0 | 59.7487
3349 | 0 | 0 | 59.6034
3350 | 0 | 0 | 59.5083
3351 | 0 | 0 | 59.4134
3352 | 0 | 0 | 59.3187
3353 | 0 | 0 | 59.2242
3354 | 5.7942 | 6.8609 | 59.7801
3355 | 11.4457 | 13.3493 | 60.1816
3356 | 0 | 0 | 61.2162
3357 | 1.1858 | 0 | 60.2801
3358 | 0 | 0 | 60.1077
3359 | 0 | 0 | 60.0113
3360 | 0 | 0 | 59.9152
3361 | 0 | 0 | 59.8194
3362 | 0 | 0 | 59.7237
3363 | 0 | 0 | 59.6283
3364 | 0 | 0 | 59.5331
3365 | 0 | 0 | 59.4381
3366 | 11.3184 | 13.5896 | 59.8712
3367 | 1.1799 | 0 | 60.1586
3368 | 1.5347 | 0 | 58.9037
3369 | 0 | 0 | 58.7123
3370 | 0 | 0 | 58.6192
3371 | 0 | 0 | 58.5264
3372 | 0.74633 | 6.4164 | 61.6403
3373 | 0 | 0 | 62.6931
3374 | 0 | 0 | 62.5907
3375 | 0 | 0 | 62.4886
3376 | 0 | 0 | 62.3867
3377 | 0 | 0 | 62.285
3378 | 5.8181 | 6.5075 | 60.9234
3379 | 11.4261 | 12.731 | 61.0053
3380 | 0 | 0 | 63.5077
3381 | 1.2403 | 0 | 62.5269
3382 | 0 | 0 | 62.3456
3383 | 0 | 0 | 62.244
3384 | 0 | 0 | 62.1427
3385 | 0 | 0 | 62.0416
3386 | 0 | 0 | 61.9407
3387 | 0 | 0 | 61.8401
3388 | 0 | 0 | 61.7397
3389 | 0 | 0 | 61.6395
3390 | 11.1617 | 13.2255 | 60.274
3391 | 1.2281 | 0 | 62.1553
3392 | 1.5973 | 0 | 60.8475
3393 | 0 | 0 | 60.6475
3394 | 0 | 0 | 60.5499
3395 | 0 | 0 | 60.4525
3396 | 0.77665 | 0 | 59.8073
3397 | 0 | 0 | 59.662
3398 | 0 | 0 | 59.5667
3399 | 0 | 0 | 59.4716
3400 | 0 | 0 | 59.3768
3401 | 0 | 0 | 59.2822
3402 | 5.7747 | 6.8555 | 59.8461
3403 | 11.4099 | 13.3072 | 60.2515
3404 | 0 | 0 | 61.2798
3405 | 1.1819 | 0 | 60.3462
3406 | 0 | 0 | 60.1739
3407 | 0 | 0 | 60.0774
3408 | 0 | 0 | 59.9811
3409 | 0 | 0 | 59.8851
3410 | 0 | 0 | 59.7893
3411 | 0 | 0 | 59.6937
3412 | 0 | 0 | 59.5983
3413 | 0 | 0 | 59.5032
3414 | 11.282 | 13.556 | 59.9413
3415 | 1.1761 | 0 | 60.2282
3416 | 1.5298 | 0 | 58.9768
3417 | 0 | 0 | 58.7855
3418 | 0 | 0 | 58.6923
3419 | 0 | 0 | 58.5993
3420 | 0.74391 | 6.3801 | 61.6938
3421 | 0 | 0 | 62.7399
3422 | 0 | 0 | 62.6374
3423 | 0 | 0 | 62.5351
3424 | 0 | 0 | 62.4331
3425 | 0 | 0 | 62.3313
3426 | 5.7976 | 6.4774 | 60.9718
3427 | 11.3849 | 12.6964 | 61.0562
3428 | 0 | 0 | 63.5516
3429 | 1.236 | 0 | 62.5737
3430 | 0 | 0 | 62.3926
3431 | 0 | 0 | 62.2909
3432 | 0 | 0 | 62.1894
3433 | 0 | 0 | 62.0882
3434 | 0 | 0 | 61.9873
3435 | 0 | 0 | 61.8865
3436 | 0 | 0 | 61.786
3437 | 0 | 0 | 61.6858
3438 | 11.1224 | 13.188 | 60.3302
3439 | 1.2239 | 0 | 62.2059
3440 | 1.5918 | 0 | 60.902
3441 | 0 | 0 | 60.7022
3442 | 0 | 0 | 60.6045
3443 | 0 | 0 | 60.507
3444 | 0.77393 | 0 | 59.8636
3445 | 0 | 0 | 59.7183
3446 | 0 | 0 | 59.6229
3447 | 0 | 0 | 59.5277
3448 | 0 | 0 | 59.4328
3449 | 0 | 0 | 59.338
3450 | 5.7539 | 6.8246 | 59.8958
3451 | 11.3697 | 13.2714 | 60.306
3452 | 0 | 0 | 61.331
3453 | 1.1778 | 0 | 60.4003
3454 | 0 | 0 | 60.228
3455 | 0 | 0 | 60.1314
3456 | 0 | 0 | 60.035
3457 | 0 | 0 | 59.9389
3458 | 0 | 0 | 59.8429
3459 | 0 | 0 | 59.7472
3460 | 0 | 0 | 59.6517
3461 | 0 | 0 | 59.5565
3462 | 11.243 | 13.5178 | 59.9992
3463 | 1.1721 | 0 | 60.2848
3464 | 1.5245 | 0 | 59.0372
3465 | 0 | 0 | 58.8461
3466 | 0 | 0 | 58.7528
3467 | 0 | 0 | 58.6596
3468 | 0.7413 | 6.3648 | 60.116
3469 | 0 | 0 | 62.794
3470 | 0 | 0 | 62.6914
3471 | 0 | 0 | 62.589
3472 | 0 | 0 | 62.4868
3473 | 0 | 0 | 62.3849
3474 | 5.778 | 6.4442 | 61.0258
3475 | 11.345 | 12.6604 | 61.1101
3476 | 0 | 0 | 63.5975
3477 | 1.2317 | 0 | 62.6226
3478 | 0 | 0 | 62.4416
3479 | 0 | 0 | 62.3398
3480 | 0 | 0 | 62.2382
3481 | 0 | 0 | 62.1369
3482 | 0 | 0 | 62.0358
3483 | 0 | 0 | 61.9349
3484 | 0 | 0 | 61.8343
3485 | 0 | 0 | 61.7339
3486 | 11.0837 | 13.15 | 60.3877
3487 | 1.2197 | 0 | 62.2573
3488 | 1.5863 | 0 | 60.9574
3489 | 0 | 0 | 60.7579
3490 | 0 | 0 | 60.66
3491 | 0 | 0 | 60.5624
3492 | 0.77125 | 0 | 59.9207
3493 | 0 | 0 | 59.7755
3494 | 0 | 0 | 59.6799
3495 | 0 | 0 | 59.5846
3496 | 0 | 0 | 59.4895
3497 | 0 | 0 | 59.3946
3498 | 5.7332 | 6.7933 | 59.9461
3499 | 11.3299 | 13.2356 | 60.3606
3500 | 0 | 0 | 61.3823
3501 | 1.1736 | 0 | 60.4543
3502 | 0 | 0 | 60.2822
3503 | 0 | 0 | 60.1855
3504 | 0 | 0 | 60.089
3505 | 0 | 0 | 59.9927
3506 | 0 | 0 | 59.8966
3507 | 0 | 0 | 59.8008
3508 | 0 | 0 | 59.7052
3509 | 0 | 0 | 59.6098
3510 | 11.2042 | 13.4796 | 60.0569
3511 | 1.168 | 0 | 60.3412
3512 | 1.5192 | 0 | 59.0974
3513 | 0 | 0 | 58.9066
3514 | 0 | 0 | 58.8131
3515 | 0 | 0 | 58.7198
3516 | 0.7387 | 0 | 58.1057
3517 | 0 | 6.3643 | 61.6696
3518 | 0 | 0 | 62.7604
3519 | 0 | 0 | 62.6578
3520 | 0 | 0 | 62.5555
3521 | 0 | 0 | 62.4534
3522 | 5.7603 | 6.4044 | 61.0914
3523 | 11.3072 | 12.6213 | 61.17
3524 | 0 | 0 | 63.6478
3525 | 1.2276 | 0 | 62.6756
3526 | 0 | 0 | 62.4947
3527 | 0 | 0 | 62.3928
3528 | 0 | 0 | 62.2911
3529 | 0 | 0 | 62.1897
3530 | 0 | 0 | 62.0884
3531 | 0 | 0 | 61.9875
3532 | 0 | 0 | 61.8867
3533 | 0 | 0 | 61.7862
3534 | 11.0462 | 13.1104 | 60.4481
3535 | 1.2156 | 0 | 62.3107
3536 | 1.581 | 0 | 61.0147
3537 | 0 | 0 | 60.8154
3538 | 0 | 0 | 60.7174
3539 | 0 | 0 | 60.6196
3540 | 0.76862 | 0 | 59.9796
3541 | 0 | 0 | 59.8345
3542 | 0 | 0 | 59.7388
3543 | 0 | 0 | 59.6433
3544 | 0 | 0 | 59.5481
3545 | 0 | 0 | 59.453
3546 | 5.7128 | 6.7613 | 59.9974
3547 | 11.2905 | 13.1992 | 60.4156
3548 | 0 | 0 | 61.4338
3549 | 1.1696 | 0 | 60.5085
3550 | 0 | 0 | 60.3365
3551 | 0 | 0 | 60.2397
3552 | 0 | 0 | 60.143
3553 | 0 | 0 | 60.0466
3554 | 0 | 0 | 59.9504
3555 | 0 | 0 | 59.8545
3556 | 0 | 0 | 59.7587
3557 | 0 | 0 | 59.6632
3558 | 11.1658 | 13.4416 | 60.1146
3559 | 1.164 | 0 | 60.3975
3560 | 1.514 | 0 | 59.1575
3561 | 0 | 0 | 58.9668
3562 | 0 | 0 | 58.8732
3563 | 0 | 0 | 58.7797
3564 | 0.73613 | 0 | 58.1674
3565 | 0 | 6.364 | 58.4684
3566 | 0 | 0 | 62.8293
3567 | 0 | 0 | 62.7266
3568 | 0 | 0 | 62.6241
3569 | 0 | 0 | 62.5218
3570 | 5.7428 | 6.3648 | 61.1569
3571 | 11.2697 | 12.5824 | 61.2297
3572 | 0 | 0 | 63.6978
3573 | 1.2235 | 0 | 62.7284
3574 | 0 | 0 | 62.5476
3575 | 0 | 0 | 62.4456
3576 | 0 | 0 | 62.3438
3577 | 0 | 0 | 62.2422
3578 | 0 | 0 | 62.1409
3579 | 0 | 0 | 62.0398
3580 | 0 | 0 | 61.9389
3581 | 0 | 0 | 61.8383
3582 | 11.0091 | 13.0712 | 60.5082
3583 | 1.2115 | 0 | 62.3638
3584 | 1.5757 | 0 | 61.0717
3585 | 0 | 0 | 60.8725
3586 | 0 | 0 | 60.7744
3587 | 0 | 0 | 60.6765
3588 | 0.76601 | 0 | 60.0382
3589 | 0 | 0 | 59.8931
3590 | 0 | 0 | 59.7972
3591 | 0 | 0 | 59.7016
3592 | 0 | 0 | 59.6063
3593 | 0 | 0 | 59.5111
3594 | 5.4867 | 7.0016 | 59.4172
3595 | 11.3169 | 12.9052 | 60.6601
3596 | 0 | 0 | 61.6049
3597 | 1.1685 | 0 | 60.6799
3598 | 0 | 0 | 60.5076
3599 | 0 | 0 | 60.4103
3600 | 0 | 0 | 60.3133
3601 | 0 | 0 | 60.2165
3602 | 0 | 0 | 60.1199
3603 | 0 | 0 | 60.0235
3604 | 0 | 0 | 59.9274
3605 | 0 | 0 | 59.8315
3606 | 11.1523 | 13.3585 | 60.251
3607 | 1.1616 | 0 | 60.5134
3608 | 1.5108 | 0 | 59.2755
3609 | 0 | 0 | 59.0847
3610 | 0 | 0 | 58.9908
3611 | 0 | 0 | 58.8971
3612 | 0.73454 | 0 | 58.2855
3613 | 0 | 0 | 58.1466
3614 | 0 | 0 | 58.0548
3615 | 0 | 6.366 | 61.667
3616 | 0 | 0 | 62.7581
3617 | 0 | 0 | 62.6555
3618 | 5.7333 | 0 | 59.2236
3619 | 10.7874 | 13.7119 | 58.9582
3620 | 0 | 0 | 60.1971
3621 | 1.1307 | 0 | 59.3026
3622 | 0 | 0 | 59.136
3623 | 0 | 0 | 59.0419
3624 | 0 | 0 | 58.9481
3625 | 0 | 0 | 58.8545
3626 | 0 | 0 | 58.7611
3627 | 0 | 0 | 58.6679
3628 | 0 | 0 | 58.575
3629 | 0 | 0 | 58.4822
3630 | 10.827 | 13.5503 | 59.1845
3631 | 1.1352 | 0 | 59.5855
3632 | 1.4766 | 0 | 58.376
3633 | 0 | 0 | 58.1896
3634 | 0 | 0 | 58.0978
3635 | 0 | 6.336 | 59.2566
3636 | 0.79943 | 0 | 62.2187
3637 | 0 | 0 | 62.0663
3638 | 0 | 0 | 61.9654
3639 | 0 | 0 | 61.8647
3640 | 0 | 0 | 61.7642
3641 | 0 | 0 | 61.664
3642 | 5.6016 | 6.7268 | 60.5013
3643 | 11.0902 | 12.7312 | 60.9176
3644 | 0 | 0 | 63.4837
3645 | 1.2102 | 0 | 62.5242
3646 | 0 | 0 | 62.3448
3647 | 0 | 0 | 62.2432
3648 | 0 | 0 | 62.1419
3649 | 0 | 0 | 62.0408
3650 | 0 | 0 | 61.9399
3651 | 0 | 0 | 61.8393
3652 | 0 | 0 | 61.7389
3653 | 0 | 0 | 61.6388
3654 | 10.8911 | 13.1177 | 60.3937
3655 | 1.2018 | 0 | 62.2985
3656 | 1.563 | 0 | 61.0162
3657 | 0 | 0 | 60.8179
3658 | 0 | 0 | 60.7199
3659 | 0 | 0 | 60.6222
3660 | 0.75981 | 0 | 59.9884
3661 | 0 | 0 | 59.8438
3662 | 0 | 0 | 59.748
3663 | 0 | 0 | 59.6526
3664 | 0 | 0 | 59.5573
3665 | 0 | 0 | 59.4623
3666 | 5.6495 | 6.7445 | 60.0336
3667 | 11.177 | 13.1394 | 60.4985
3668 | 0 | 0 | 61.5199
3669 | 1.1585 | 0 | 60.6022
3670 | 0 | 0 | 60.4307
3671 | 0 | 0 | 60.3336
3672 | 0 | 0 | 60.2368
3673 | 0 | 0 | 60.1401
3674 | 0 | 0 | 60.0437
3675 | 0 | 0 | 59.9476
3676 | 0 | 0 | 59.8516
3677 | 0 | 0 | 59.7559
3678 | 11.063 | 13.3632 | 60.2299
3679 | 1.1536 | 0 | 60.5158
3680 | 1.5004 | 0 | 59.2857
3681 | 0 | 0 | 59.0956
3682 | 0 | 0 | 59.0017
3683 | 0 | 0 | 58.9079
3684 | 0.72946 | 0 | 58.2999
3685 | 0 | 0 | 58.1613
3686 | 0 | 0 | 58.0695
3687 | 0 | 6.3663 | 60.8663
3688 | 0 | 0 | 62.7748
3689 | 0 | 0 | 62.6722
3690 | 5.6975 | 0 | 59.261
3691 | 10.7246 | 13.7016 | 59.0334
3692 | 0 | 0 | 60.2814
3693 | 1.1249 | 0 | 59.3908
3694 | 0 | 0 | 59.2243
3695 | 0 | 0 | 59.13
3696 | 0 | 0 | 59.036
3697 | 0 | 0 | 58.9422
3698 | 0 | 0 | 58.8486
3699 | 0 | 0 | 58.7552
3700 | 0 | 0 | 58.6621
3701 | 0 | 0 | 58.5691
3702 | 10.7748 | 13.5451 | 59.299
3703 | 1.1305 | 0 | 59.7115
3704 | 1.4704 | 0 | 58.5063
3705 | 0 | 0 | 58.32
3706 | 0 | 0 | 58.2279
3707 | 0 | 0 | 58.1359
3708 | 0.71486 | 6.568 | 61.3607
3709 | 0 | 0 | 62.4444
3710 | 0 | 0 | 62.3425
3711 | 0 | 0 | 62.241
3712 | 0 | 0 | 62.1396
3713 | 0 | 0 | 62.0385
3714 | 5.609 | 6.5484 | 60.8125
3715 | 11.0708 | 12.6152 | 61.1195
3716 | 0 | 0 | 63.6394
3717 | 1.2063 | 0 | 62.6823
3718 | 0 | 0 | 62.5028
3719 | 0 | 0 | 62.4008
3720 | 0 | 0 | 62.2991
3721 | 0 | 0 | 62.1976
3722 | 0 | 0 | 62.0964
3723 | 0 | 0 | 61.9954
3724 | 0 | 0 | 61.8946
3725 | 0 | 0 | 61.7941
3726 | 10.8549 | 13.0303 | 60.5398
3727 | 1.1969 | 0 | 62.4174
3728 | 1.5566 | 0 | 61.1395
3729 | 0 | 0 | 60.9414
3730 | 0 | 0 | 60.8431
3731 | 0 | 0 | 60.745
3732 | 0.75667 | 0 | 60.1131
3733 | 0 | 0 | 59.9684
3734 | 0 | 0 | 59.8724
3735 | 0 | 0 | 59.7766
3736 | 0 | 0 | 59.6811
3737 | 0 | 0 | 59.5858
3738 | 5.4201 | 6.9902 | 59.5253
3739 | 11.0007 | 13.415 | 60.3267
3740 | 0 | 0 | 62.3523
3741 | 1.1715 | 0 | 61.4232
3742 | 0 | 0 | 61.2489
3743 | 0 | 0 | 61.1499
3744 | 0 | 0 | 61.0511
3745 | 0 | 0 | 60.9526
3746 | 0 | 0 | 60.8543
3747 | 0 | 0 | 60.7562
3748 | 0 | 0 | 60.6583
3749 | 0 | 0 | 60.5607
3750 | 10.9585 | 13.5525 | 60.295
3751 | 1.1716 | 0 | 61.5264
3752 | 1.5237 | 0 | 60.2759
3753 | 0 | 0 | 60.0819
3754 | 0 | 0 | 59.9856
3755 | 0 | 0 | 59.8896
3756 | 0.74066 | 0 | 59.2712
3757 | 0 | 0 | 59.1295
3758 | 0 | 0 | 59.0355
3759 | 0 | 0 | 58.9417
3760 | 0 | 0 | 58.8481
3761 | 0 | 0 | 58.7547
3762 | 5.5206 | 6.8616 | 59.4712
3763 | 10.9686 | 13.2922 | 60.1735
3764 | 0 | 0 | 61.2826
3765 | 1.1422 | 0 | 60.3771
3766 | 0 | 0 | 60.2072
3767 | 0 | 0 | 60.1106
3768 | 0 | 0 | 60.0143
3769 | 0 | 0 | 59.9182
3770 | 0 | 0 | 59.8223
3771 | 0 | 0 | 59.7266
3772 | 0 | 0 | 59.6312
3773 | 0 | 0 | 59.536
3774 | 10.9207 | 13.4171 | 60.1192
3775 | 1.1417 | 0 | 60.4561
3776 | 1.4848 | 0 | 59.238
3777 | 0 | 0 | 59.049
3778 | 0 | 0 | 58.9551
3779 | 0 | 0 | 58.8615
3780 | 0.72182 | 0 | 58.259
3781 | 0 | 0 | 58.1209
3782 | 0 | 6.3637 | 58.469
3783 | 0 | 0 | 62.8297
3784 | 0 | 0 | 62.727
3785 | 0 | 0 | 62.6245
3786 | 5.6423 | 0 | 59.2454
3787 | 10.6288 | 13.6949 | 59.0809
3788 | 0 | 0 | 60.3448
3789 | 1.1162 | 0 | 59.4601
3790 | 0 | 0 | 59.294
3791 | 0 | 0 | 59.1996
3792 | 0 | 0 | 59.1054
3793 | 0 | 0 | 59.0114
3794 | 0 | 0 | 58.9176
3795 | 0 | 0 | 58.8241
3796 | 0 | 0 | 58.7308
3797 | 0 | 0 | 58.6377
3798 | 10.6963 | 13.537 | 59.409
3799 | 1.1233 | 0 | 59.8389
3800 | 1.461 | 0 | 58.6404
3801 | 0 | 0 | 58.4544
3802 | 0 | 0 | 58.3619
3803 | 0 | 0 | 58.2697
3804 | 0.71026 | 6.5069 | 61.462
3805 | 0 | 0 | 62.5344
3806 | 0 | 0 | 62.4324
3807 | 0 | 0 | 62.3306
3808 | 0 | 0 | 62.2291
3809 | 0 | 0 | 62.1278
3810 | 5.5705 | 6.491 | 60.9051
3811 | 10.9938 | 12.5498 | 61.2161
3812 | 0 | 0 | 63.7225
3813 | 1.1982 | 0 | 62.7709
3814 | 0 | 0 | 62.5917
3815 | 0 | 0 | 62.4895
3816 | 0 | 0 | 62.3876
3817 | 0 | 0 | 62.2859
3818 | 0 | 0 | 62.1845
3819 | 0 | 0 | 62.0833
3820 | 0 | 0 | 61.9823
3821 | 0 | 0 | 61.8816
3822 | 10.7815 | 12.9599 | 60.6456
3823 | 1.189 | 0 | 62.5124
3824 | 1.5463 | 0 | 61.2421
3825 | 0 | 0 | 61.0443
3826 | 0 | 0 | 60.9458
3827 | 0 | 0 | 60.8475
3828 | 0.7516 | 0 | 60.219
3829 | 0 | 0 | 60.0743
3830 | 0 | 0 | 59.9781
3831 | 0 | 0 | 59.882
3832 | 0 | 0 | 59.7862
3833 | 0 | 0 | 59.6907
3834 | 5.3837 | 6.9804 | 59.6466
3835 | 10.936 | 13.3354 | 60.4626
3836 | 0 | 0 | 62.4656
3837 | 1.1642 | 0 | 61.5413
3838 | 0 | 0 | 61.3672
3839 | 0 | 0 | 61.268
3840 | 0 | 0 | 61.1689
3841 | 0 | 0 | 61.0701
3842 | 0 | 0 | 60.9715
3843 | 0 | 0 | 60.8732
3844 | 0 | 0 | 60.775
3845 | 0 | 0 | 60.6771
3846 | 10.8918 | 13.4717 | 60.4212
3847 | 1.1641 | 0 | 61.6368
3848 | 1.514 | 0 | 60.3934
3849 | 0 | 0 | 60.1997
3850 | 0 | 0 | 60.1032
3851 | 0 | 0 | 60.0069
3852 | 0.73588 | 0 | 59.3916
3853 | 0 | 0 | 59.2499
3854 | 0 | 0 | 59.1556
3855 | 0 | 0 | 59.0615
3856 | 0 | 0 | 58.9676
3857 | 0 | 0 | 58.8739
3858 | 5.486 | 6.8523 | 59.6048
3859 | 10.9049 | 13.2104 | 60.311
3860 | 0 | 0 | 61.4066
3861 | 1.1353 | 0 | 60.5057
3862 | 0 | 0 | 60.3359
3863 | 0 | 0 | 60.239
3864 | 0 | 0 | 60.1424
3865 | 0 | 0 | 60.046
3866 | 0 | 0 | 59.9498
3867 | 0 | 0 | 59.8538
3868 | 0 | 0 | 59.7581
3869 | 0 | 0 | 59.6626
3870 | 10.8546 | 13.3354 | 60.2454
3871 | 1.1345 | 0 | 60.5752
3872 | 1.4755 | 0 | 59.3638
3873 | 0 | 0 | 59.1751
3874 | 0 | 0 | 59.081
3875 | 0 | 0 | 58.987
3876 | 0.71723 | 0 | 58.3875
3877 | 0 | 0 | 58.2494
3878 | 0 | 0 | 58.1574
3879 | 0 | 0 | 58.0656
3880 | 0 | 6.3682 | 60.8633
3881 | 0 | 0 | 62.7724
3882 | 5.612 | 0 | 59.4104
3883 | 10.5739 | 13.6697 | 59.2688
3884 | 0 | 0 | 60.5376
3885 | 1.1111 | 0 | 59.6561
3886 | 0 | 0 | 59.4899
3887 | 0 | 0 | 59.395
3888 | 0 | 0 | 59.3003
3889 | 0 | 0 | 59.2059
3890 | 0 | 0 | 59.1117
3891 | 0 | 0 | 59.0177
3892 | 0 | 0 | 58.9239
3893 | 0 | 0 | 58.8304
3894 | 10.6491 | 13.5326 | 59.6266
3895 | 1.119 | 0 | 60.0667
3896 | 1.4554 | 0 | 58.8719
3897 | 0 | 0 | 58.6856
3898 | 0 | 0 | 58.5926
3899 | 0 | 0 | 58.4999
3900 | 0.70747 | 6.405 | 61.6347
3901 | 0 | 0 | 62.6879
3902 | 0 | 0 | 62.5855
3903 | 0 | 0 | 62.4833
3904 | 0 | 0 | 62.3814
3905 | 0 | 0 | 62.2798
3906 | 5.5411 | 6.4065 | 61.0463
3907 | 10.9274 | 12.4722 | 61.3373
3908 | 0 | 0 | 63.8228
3909 | 1.1907 | 0 | 62.8762
3910 | 0 | 0 | 62.6972
3911 | 0 | 0 | 62.5948
3912 | 0 | 0 | 62.4927
3913 | 0 | 0 | 62.3907
3914 | 0 | 0 | 62.289
3915 | 0 | 0 | 62.1876
3916 | 0 | 0 | 62.0864
3917 | 0 | 0 | 61.9854
3918 | 10.7146 | 12.8844 | 60.7622
3919 | 1.1816 | 0 | 62.6145
3920 | 1.5367 | 0 | 61.3511
3921 | 0 | 0 | 61.1538
3922 | 0 | 0 | 61.055
3923 | 0 | 0 | 60.9565
3924 | 0.74684 | 0 | 60.331
3925 | 0 | 0 | 60.1864
3926 | 0 | 0 | 60.0899
3927 | 0 | 0 | 59.9936
3928 | 0 | 0 | 59.8975
3929 | 0 | 0 | 59.8017
3930 | 5.3495 | 6.9705 | 59.7728
3931 | 10.4759 | 13.1908 | 59.9608
3932 | 0 | 0 | 62.8396
3933 | 1.1637 | 0 | 61.9147
3934 | 0 | 0 | 61.7398
3935 | 0 | 0 | 61.6396
3936 | 0 | 0 | 61.5397
3937 | 0 | 0 | 61.44
3938 | 0 | 0 | 61.3405
3939 | 0 | 0 | 61.2413
3940 | 0 | 0 | 61.1423
3941 | 0 | 0 | 61.0436
3942 | 10.4785 | 13.2323 | 60.0788
3943 | 1.1669 | 0 | 62.1359
3944 | 1.5176 | 0 | 60.8883
3945 | 0 | 0 | 60.6933
3946 | 0 | 0 | 60.5956
3947 | 0 | 0 | 60.4981
3948 | 0.73757 | 0 | 59.8803
3949 | 0 | 0 | 59.7374
3950 | 0 | 0 | 59.6419
3951 | 0 | 0 | 59.5467
3952 | 0 | 0 | 59.4517
3953 | 0 | 0 | 59.3569
3954 | 5.4928 | 6.7647 | 60.0315
3955 | 10.9029 | 13.0311 | 60.6381
3956 | 0 | 0 | 61.6782
3957 | 1.1323 | 0 | 60.7786
3958 | 0 | 0 | 60.6084
3959 | 0 | 0 | 60.5109
3960 | 0 | 0 | 60.4136
3961 | 0 | 0 | 60.3166
3962 | 0 | 0 | 60.2198
3963 | 0 | 0 | 60.1232
3964 | 0 | 0 | 60.0268
3965 | 0 | 0 | 59.9307
3966 | 10.8216 | 13.199 | 60.4675
3967 | 1.1295 | 0 | 60.7663
3968 | 1.469 | 0 | 59.5592
3969 | 0 | 0 | 59.3705
3970 | 0 | 0 | 59.2759
3971 | 0 | 0 | 59.1815
3972 | 0.714 | 0 | 58.5837
3973 | 0 | 0 | 58.4453
3974 | 0 | 0 | 58.3529
3975 | 0 | 0 | 58.2607
3976 | 0 | 0 | 58.1687
3977 | 0 | 0 | 58.0769
3978 | 5.3377 | 6.9703 | 58.9647
3979 | 10.6637 | 13.3829 | 59.9401
3980 | 0 | 0 | 61.1361
3981 | 1.1164 | 0 | 60.2492
3982 | 0 | 0 | 60.0812
3983 | 0 | 0 | 59.985
3984 | 0 | 0 | 59.8889
3985 | 0 | 0 | 59.7931
3986 | 0 | 0 | 59.6975
3987 | 0 | 0 | 59.6022
3988 | 0 | 0 | 59.507
3989 | 0 | 0 | 59.4121
3990 | 10.6894 | 13.3958 | 60.1205
3991 | 1.1206 | 0 | 60.5089
3992 | 1.4574 | 0 | 59.3114
3993 | 0 | 0 | 59.124
3994 | 0 | 0 | 59.0299
3995 | 0 | 0 | 58.9361
3996 | 0.70833 | 0 | 58.343
3997 | 0 | 0 | 58.2055
3998 | 0 | 0 | 58.1137
3999 | 0 | 6.3672 | 58.462
4000 | 0 | 0 | 62.8252
4001 | 0 | 0 | 62.7225
4002 | 5.5481 | 0 | 59.3977
4003 | 10.463 | 13.6611 | 59.3287
4004 | 0 | 0 | 60.6157
4005 | 1.101 | 0 | 59.741
4006 | 0 | 0 | 59.5752
4007 | 0 | 0 | 59.4802
4008 | 0 | 0 | 59.3853
4009 | 0 | 0 | 59.2907
4010 | 0 | 0 | 59.1963
4011 | 0 | 0 | 59.1021
4012 | 0 | 0 | 59.0081
4013 | 0 | 0 | 58.9144
4014 | 10.5584 | 13.5233 | 59.7585
4015 | 1.1108 | 0 | 60.2187
4016 | 1.4446 | 0 | 59.0316
4017 | 0 | 0 | 58.8456
4018 | 0 | 0 | 58.7523
4019 | 0 | 0 | 58.6591
4020 | 0.70215 | 6.3621 | 58.5107
4021 | 0 | 0 | 62.8253
4022 | 0 | 0 | 62.7226
4023 | 0 | 0 | 62.6201
4024 | 0 | 0 | 62.5179
4025 | 0 | 0 | 62.4159
4026 | 5.5001 | 0 | 59.1202
4027 | 10.3829 | 13.6869 | 59.1234
4028 | 0 | 0 | 60.4297
4029 | 1.094 | 0 | 59.5605
4030 | 0 | 0 | 59.3956
4031 | 0 | 0 | 59.3009
4032 | 0 | 0 | 59.2065
4033 | 0 | 0 | 59.1123
4034 | 0 | 0 | 59.0183
4035 | 0 | 0 | 58.9245
4036 | 0 | 0 | 58.831
4037 | 0 | 0 | 58.7376
4038 | 10.4963 | 13.5161 | 59.6146
4039 | 1.1051 | 0 | 60.0889
4040 | 1.4373 | 0 | 58.9077
4041 | 0 | 0 | 58.7225
4042 | 0 | 0 | 58.6294
4043 | 0 | 0 | 58.5365
4044 | 0.69856 | 6.3836 | 61.6651
4045 | 0 | 0 | 62.7149
4046 | 0 | 0 | 62.6124
4047 | 0 | 0 | 62.5102
4048 | 0 | 0 | 62.4082
4049 | 0 | 0 | 62.3065
4050 | 5.4758 | 6.3692 | 61.0987
4051 | 10.8076 | 12.4021 | 61.4312
4052 | 0 | 0 | 63.9093
4053 | 1.1787 | 0 | 62.971
4054 | 0 | 0 | 62.7925
4055 | 0 | 0 | 62.6899
4056 | 0 | 0 | 62.5875
4057 | 0 | 0 | 62.4854
4058 | 0 | 0 | 62.3835
4059 | 0 | 0 | 62.2818
4060 | 0 | 0 | 62.1804
4061 | 0 | 0 | 62.0792
4062 | 10.6064 | 12.7971 | 60.8888
4063 | 1.1702 | 0 | 62.7321
4064 | 1.5219 | 0 | 61.4796
4065 | 0 | 0 | 61.2828
4066 | 0 | 0 | 61.1838
4067 | 0 | 0 | 61.0849
4068 | 0.73956 | 0 | 60.4642
4069 | 0 | 0 | 60.3198
4070 | 0 | 0 | 60.223
4071 | 0 | 0 | 60.1264
4072 | 0 | 0 | 60.03
4073 | 0 | 0 | 59.9338
4074 | 5.2974 | 6.9575 | 59.9291
4075 | 10.3835 | 13.0835 | 60.1406
4076 | 0 | 0 | 62.9897
4077 | 1.1534 | 0 | 62.0717
4078 | 0 | 0 | 61.8971
4079 | 0 | 0 | 61.7965
4080 | 0 | 0 | 61.6962
4081 | 0 | 0 | 61.5962
4082 | 0 | 0 | 61.4964
4083 | 0 | 0 | 61.3968
4084 | 0 | 0 | 61.2974
4085 | 0 | 0 | 61.1983
4086 | 10.3855 | 13.1224 | 60.2497
4087 | 1.1565 | 0 | 62.2845
4088 | 1.504 | 0 | 61.0468
4089 | 0 | 0 | 60.8522
4090 | 0 | 0 | 60.7542
4091 | 0 | 0 | 60.6563
4092 | 0.73089 | 0 | 60.0429
4093 | 0 | 0 | 59.8999
4094 | 0 | 0 | 59.8041
4095 | 0 | 0 | 59.7085
4096 | 0 | 0 | 59.6131
4097 | 0 | 0 | 59.5179
4098 | 5.237 | 6.9739 | 59.5567
4099 | 10.6797 | 13.2621 | 60.5204
4100 | 0 | 0 | 62.5423
4101 | 1.1399 | 0 | 61.635
4102 | 0 | 0 | 61.4622
4103 | 0 | 0 | 61.3627
4104 | 0 | 0 | 61.2635
4105 | 0 | 0 | 61.1644
4106 | 0 | 0 | 61.0656
4107 | 0 | 0 | 60.967
4108 | 0 | 0 | 60.8687
4109 | 0 | 0 | 60.7706
4110 | 10.6739 | 13.3426 | 60.5955
4111 | 1.1422 | 0 | 61.8138
4112 | 1.4854 | 0 | 60.5914
4113 | 0 | 0 | 60.3992
4114 | 0 | 0 | 60.3022
4115 | 0 | 0 | 60.2054
4116 | 0.72186 | 0 | 59.5994
4117 | 0 | 0 | 59.4582
4118 | 0 | 0 | 59.3634
4119 | 0 | 0 | 59.2688
4120 | 0 | 0 | 59.1744
4121 | 0 | 0 | 59.0803
4122 | 5.3852 | 6.833 | 59.8582
4123 | 10.7219 | 13.0307 | 60.6024
4124 | 0 | 0 | 61.6769
4125 | 1.1161 | 0 | 60.7888
4126 | 0 | 0 | 60.6195
4127 | 0 | 0 | 60.522
4128 | 0 | 0 | 60.4247
4129 | 0 | 0 | 60.3276
4130 | 0 | 0 | 60.2308
4131 | 0 | 0 | 60.1342
4132 | 0 | 0 | 60.0378
4133 | 0 | 0 | 59.9416
4134 | 10.675 | 13.1438 | 60.5378
4135 | 1.1156 | 0 | 60.8572
4136 | 1.4508 | 0 | 59.6636
4137 | 0 | 0 | 59.4758
4138 | 0 | 0 | 59.3809
4139 | 0 | 0 | 59.2863
4140 | 0.70505 | 0 | 58.6946
4141 | 0 | 0 | 58.5565
4142 | 0 | 0 | 58.4638
4143 | 0 | 0 | 58.3713
4144 | 0 | 0 | 58.2791
4145 | 0 | 0 | 58.187
4146 | 5.2734 | 6.9581 | 59.1049
4147 | 10.5473 | 13.2775 | 60.1087
4148 | 0 | 0 | 61.294
4149 | 1.1043 | 0 | 60.4153
4150 | 0 | 0 | 60.2477
4151 | 0 | 0 | 60.151
4152 | 0 | 0 | 60.0546
4153 | 0 | 0 | 59.9584
4154 | 0 | 0 | 59.8624
4155 | 0 | 0 | 59.7666
4156 | 0 | 0 | 59.6711
4157 | 0 | 0 | 59.5758
4158 | 10.577 | 13.2809 | 60.295
4159 | 1.1088 | 0 | 60.6784
4160 | 1.442 | 0 | 59.492
4161 | 0 | 0 | 59.3051
4162 | 0 | 0 | 59.2107
4163 | 0 | 0 | 59.1164
4164 | 0.70076 | 0 | 58.5281
4165 | 0 | 0 | 58.3907
4166 | 0 | 0 | 58.2984
4167 | 0 | 0 | 58.2064
4168 | 0 | 0 | 58.1145
4169 | 0 | 6.3668 | 58.4628
4170 | 5.4968 | 0 | 59.6329
4171 | 10.3707 | 13.6245 | 59.606
4172 | 0 | 0 | 60.9024
4173 | 1.0923 | 0 | 60.0331
4174 | 0 | 0 | 59.8672
4175 | 0 | 0 | 59.7714
4176 | 0 | 0 | 59.6759
4177 | 0 | 0 | 59.5806
4178 | 0 | 0 | 59.4855
4179 | 0 | 0 | 59.3906
4180 | 0 | 0 | 59.296
4181 | 0 | 0 | 59.2015
4182 | 10.4768 | 13.4162 | 60.0431
4183 | 1.1018 | 0 | 60.4914
4184 | 1.4329 | 0 | 59.3124
4185 | 0 | 0 | 59.1265
4186 | 0 | 0 | 59.0325
4187 | 0 | 0 | 58.9387
4188 | 0.69636 | 0 | 58.3539
4189 | 0 | 0 | 58.2172
4190 | 0 | 0 | 58.1253
4191 | 0 | 0 | 58.0337
4192 | 0 | 6.3689 | 62.4631
4193 | 0 | 0 | 62.7373
4194 | 5.4634 | 0 | 59.4616
4195 | 10.3149 | 13.6396 | 59.4833
4196 | 0 | 0 | 60.7926
4197 | 1.0874 | 0 | 59.9271
4198 | 0 | 0 | 59.7617
4199 | 0 | 0 | 59.6662
4200 | 0 | 0 | 59.5709
4201 | 0 | 0 | 59.4758
4202 | 0 | 0 | 59.381
4203 | 0 | 0 | 59.2863
4204 | 0 | 0 | 59.1919
4205 | 0 | 0 | 59.0978
4206 | 10.4345 | 13.4465 | 59.9779
4207 | 1.0985 | 0 | 60.4461
4208 | 1.4286 | 0 | 59.2705
4209 | 0 | 0 | 59.085
4210 | 0 | 0 | 58.991
4211 | 0 | 0 | 58.8973
4212 | 0.69426 | 0 | 58.3142
4213 | 0 | 0 | 58.1777
4214 | 0 | 0 | 58.0859
4215 | 0 | 6.3658 | 60.0667
4216 | 0 | 0 | 62.7927
4217 | 0 | 0 | 62.69
4218 | 5.4476 | 0 | 59.4238
4219 | 10.2878 | 13.6419 | 59.4659
4220 | 0 | 0 | 60.7805
4221 | 1.085 | 0 | 59.9167
4222 | 0 | 0 | 59.7515
4223 | 0 | 0 | 59.656
4224 | 0 | 0 | 59.5607
4225 | 0 | 0 | 59.4657
4226 | 0 | 0 | 59.3709
4227 | 0 | 0 | 59.2763
4228 | 0 | 0 | 59.1819
4229 | 0 | 0 | 59.0877
4230 | 10.4129 | 13.4432 | 59.9788
4231 | 1.0965 | 0 | 60.4517
4232 | 1.426 | 0 | 59.2779
4233 | 0 | 0 | 59.0926
4234 | 0 | 0 | 58.9986
4235 | 0 | 0 | 58.9049
4236 | 0.69298 | 0 | 58.3227
4237 | 0 | 0 | 58.1862
4238 | 0 | 0 | 58.0944
4239 | 0 | 6.3691 | 59.2598
4240 | 0 | 0 | 62.8056
4241 | 0 | 0 | 62.7029
4242 | 5.4391 | 0 | 59.4415
4243 | 10.2727 | 13.6381 | 59.4918
4244 | 0 | 0 | 60.8084
4245 | 1.0836 | 0 | 59.9455
4246 | 0 | 0 | 59.7804
4247 | 0 | 0 | 59.6848
4248 | 0 | 0 | 59.5895
4249 | 0 | 0 | 59.4944
4250 | 0 | 0 | 59.3995
4251 | 0 | 0 | 59.3048
4252 | 0 | 0 | 59.2104
4253 | 0 | 0 | 59.1161
4254 | 10.3998 | 13.4264 | 60.007
4255 | 1.0951 | 0 | 60.4781
4256 | 1.4242 | 0 | 59.3057
4257 | 0 | 0 | 59.1204
4258 | 0 | 0 | 59.0264
4259 | 0 | 0 | 58.9326
4260 | 0.69207 | 0 | 58.3509
4261 | 0 | 0 | 58.2145
4262 | 0 | 0 | 58.1226
4263 | 0 | 0 | 58.0309
4264 | 0 | 6.3703 | 62.4613
4265 | 0 | 0 | 62.7356
4266 | 5.4331 | 0 | 59.4776
4267 | 10.2619 | 13.6327 | 59.5321
4268 | 0 | 0 | 60.8496
4269 | 1.0826 | 0 | 59.9874
4270 | 0 | 0 | 59.8222
4271 | 0 | 0 | 59.7265
4272 | 0 | 0 | 59.6311
4273 | 0 | 0 | 59.5359
4274 | 0 | 0 | 59.4409
4275 | 0 | 0 | 59.3461
4276 | 0 | 0 | 59.2516
4277 | 0 | 0 | 59.1572
4278 | 10.3899 | 13.4052 | 60.0441
4279 | 1.0939 | 0 | 60.5113
4280 | 1.4226 | 0 | 59.34
4281 | 0 | 0 | 59.1547
4282 | 0 | 0 | 59.0606
4283 | 0 | 0 | 58.9667
4284 | 0.69128 | 0 | 58.3855
4285 | 0 | 0 | 58.249
4286 | 0 | 0 | 58.1571
4287 | 0 | 0 | 58.0653
4288 | 0 | 6.3684 | 60.8631
4289 | 0 | 0 | 62.7722
4290 | 5.4277 | 0 | 59.5172
4291 | 10.2521 | 13.6272 | 59.5753
4292 | 0 | 0 | 60.8935
4293 | 1.0817 | 0 | 60.0317
4294 | 0 | 0 | 59.8665
4295 | 0 | 0 | 59.7707
4296 | 0 | 0 | 59.6752
4297 | 0 | 0 | 59.5799
4298 | 0 | 0 | 59.4848
4299 | 0 | 0 | 59.3899
4300 | 0 | 0 | 59.2953
4301 | 0 | 0 | 59.2008
4302 | 10.3808 | 13.383 | 60.0826
4303 | 1.0927 | 0 | 60.5454
4304 | 1.4211 | 0 | 59.3752
4305 | 0 | 0 | 59.1899
4306 | 0 | 0 | 59.0958
4307 | 0 | 0 | 59.0018
4308 | 0.69053 | 0 | 58.421
4309 | 0 | 0 | 58.2845
4310 | 0 | 0 | 58.1925
4311 | 0 | 0 | 58.1006
4312 | 0 | 6.3661 | 59.2654
4313 | 0 | 0 | 62.8094
4314 | 5.4226 | 0 | 59.5573
4315 | 10.2426 | 13.6218 | 59.6186
4316 | 0 | 0 | 60.9374
4317 | 1.0808 | 0 | 60.0762
4318 | 0 | 0 | 59.9109
4319 | 0 | 0 | 59.815
4320 | 0 | 0 | 59.7194
4321 | 0 | 0 | 59.624
4322 | 0 | 0 | 59.5288
4323 | 0 | 0 | 59.4338
4324 | 0 | 0 | 59.339
4325 | 0 | 0 | 59.2445
4326 | 10.3719 | 13.3608 | 60.1211
4327 | 1.0916 | 0 | 60.5795
4328 | 1.4196 | 0 | 59.4102
4329 | 0 | 0 | 59.225
4330 | 0 | 0 | 59.1307
4331 | 0 | 0 | 59.0367
4332 | 0.6898 | 0 | 58.4564
4333 | 0 | 0 | 58.3198
4334 | 0 | 0 | 58.2277
4335 | 0 | 0 | 58.1358
4336 | 0 | 0 | 58.0441
4337 | 0 | 6.3639 | 62.4699
4338 | 5.4176 | 0 | 59.5971
4339 | 10.2335 | 13.6164 | 59.6615
4340 | 0 | 0 | 60.9809
4341 | 1.0799 | 0 | 60.1202
4342 | 0 | 0 | 59.9549
4343 | 0 | 0 | 59.8589
4344 | 0 | 0 | 59.7632
4345 | 0 | 0 | 59.6677
4346 | 0 | 0 | 59.5724
4347 | 0 | 0 | 59.4773
4348 | 0 | 0 | 59.3824
4349 | 0 | 0 | 59.2878
4350 | 10.3633 | 13.3388 | 60.1592
4351 | 1.0905 | 0 | 60.6131
4352 | 1.4181 | 0 | 59.4449
4353 | 0 | 0 | 59.2597
4354 | 0 | 0 | 59.1653
4355 | 0 | 0 | 59.0712
4356 | 0.68908 | 0 | 58.4913
4357 | 0 | 0 | 58.3547
4358 | 0 | 0 | 58.2625
4359 | 0 | 0 | 58.1705
4360 | 0 | 0 | 58.0787
4361 | 0 | 6.3693 | 60.0606
4362 | 5.4136 | 0 | 59.6437
4363 | 10.226 | 13.6096 | 59.7092
4364 | 0 | 0 | 61.0287
4365 | 1.0792 | 0 | 60.1684
4366 | 0 | 0 | 60.003
4367 | 0 | 0 | 59.9069
4368 | 0 | 0 | 59.811
4369 | 0 | 0 | 59.7154
4370 | 0 | 0 | 59.62
4371 | 0 | 0 | 59.5248
4372 | 0 | 0 | 59.4298
4373 | 0 | 0 | 59.3351
4374 | 10.3559 | 13.3155 | 60.1999
4375 | 1.0895 | 0 | 60.6488
4376 | 1.4168 | 0 | 59.4814
4377 | 0 | 0 | 59.2962
4378 | 0 | 0 | 59.2018
4379 | 0 | 0 | 59.1076
4380 | 0.68842 | 0 | 58.528
4381 | 0 | 0 | 58.3914
4382 | 0 | 0 | 58.2991
4383 | 0 | 0 | 58.207
4384 | 0 | 0 | 58.1151
4385 | 0 | 6.3664 | 58.4635
4386 | 5.409 | 0 | 59.6843
4387 | 10.2175 | 13.6043 | 59.7523
4388 | 0 | 0 | 61.0723
4389 | 1.0783 | 0 | 60.2124
4390 | 0 | 0 | 60.047
4391 | 0 | 0 | 59.9508
4392 | 0 | 0 | 59.8548
4393 | 0 | 0 | 59.7591
4394 | 0 | 0 | 59.6636
4395 | 0 | 0 | 59.5683
4396 | 0 | 0 | 59.4732
4397 | 0 | 0 | 59.3784
4398 | 10.3479 | 13.2938 | 60.2377
4399 | 1.0884 | 0 | 60.682
4400 | 1.4154 | 0 | 59.5157
4401 | 0 | 0 | 59.3304
4402 | 0 | 0 | 59.2359
4403 | 0 | 0 | 59.1416
4404 | 0.68774 | 0 | 58.5625
4405 | 0 | 0 | 58.4258
4406 | 0 | 0 | 58.3335
4407 | 0 | 0 | 58.2413
4408 | 0 | 0 | 58.1493
4409 | 0 | 0 | 58.0576
4410 | 5.1506 | 6.9535 | 59.0445
4411 | 10.3314 | 13.2181 | 60.1678
4412 | 0 | 0 | 61.3762
4413 | 1.0841 | 0 | 60.5115
4414 | 0 | 0 | 60.3449
4415 | 0 | 0 | 60.2481
4416 | 0 | 0 | 60.1514
4417 | 0 | 0 | 60.055
4418 | 0 | 0 | 59.9588
4419 | 0 | 0 | 59.8628
4420 | 0 | 0 | 59.767
4421 | 0 | 0 | 59.6715
4422 | 10.3933 | 13.1734 | 60.4468
4423 | 1.0907 | 0 | 60.845
4424 | 1.4184 | 0 | 59.6759
4425 | 0 | 0 | 59.4901
4426 | 0 | 0 | 59.3952
4427 | 0 | 0 | 59.3006
4428 | 0.68917 | 0 | 58.72
4429 | 0 | 0 | 58.5829
4430 | 0 | 0 | 58.4902
4431 | 0 | 0 | 58.3976
4432 | 0 | 0 | 58.3053
4433 | 0 | 0 | 58.2132
4434 | 5.1601 | 6.9459 | 59.1898
4435 | 10.3454 | 13.1619 | 60.2759
4436 | 0 | 0 | 61.464
4437 | 1.0844 | 0 | 60.5987
4438 | 0 | 0 | 60.432
4439 | 0 | 0 | 60.3349
4440 | 0 | 0 | 60.238
4441 | 0 | 0 | 60.1414
4442 | 0 | 0 | 60.045
4443 | 0 | 0 | 59.9488
4444 | 0 | 0 | 59.8529
4445 | 0 | 0 | 59.7571
4446 | 10.3948 | 13.134 | 60.5127
4447 | 1.0903 | 0 | 60.8991
4448 | 1.4178 | 0 | 59.7304
4449 | 0 | 0 | 59.5445
4450 | 0 | 0 | 59.4494
4451 | 0 | 0 | 59.3547
4452 | 0.68887 | 0 | 58.7742
4453 | 0 | 0 | 58.6369
4454 | 0 | 0 | 58.5441
4455 | 0 | 0 | 58.4514
4456 | 0 | 0 | 58.359
4457 | 0 | 0 | 58.2667
4458 | 5.1577 | 6.9427 | 59.2428
4459 | 10.3401 | 13.1373 | 60.3204
4460 | 0 | 0 | 61.5017
4461 | 1.0836 | 0 | 60.637
4462 | 0 | 0 | 60.4702
4463 | 0 | 0 | 60.3731
4464 | 0 | 0 | 60.2761
4465 | 0 | 0 | 60.1794
4466 | 0 | 0 | 60.0829
4467 | 0 | 0 | 59.9866
4468 | 0 | 0 | 59.8906
4469 | 0 | 0 | 59.7948
4470 | 10.3864 | 13.1135 | 60.5454
4471 | 1.0892 | 0 | 60.9281
4472 | 1.4165 | 0 | 59.7603
4473 | 0 | 0 | 59.5744
4474 | 0 | 0 | 59.4793
4475 | 0 | 0 | 59.3844
4476 | 0.68819 | 0 | 58.8043
4477 | 0 | 0 | 58.6671
4478 | 0 | 0 | 58.5742
4479 | 0 | 0 | 58.4814
4480 | 0 | 0 | 58.3889
4481 | 0 | 0 | 58.2966
4482 | 5.1527 | 6.9406 | 59.2743
4483 | 10.3307 | 13.1203 | 60.35
4484 | 0 | 0 | 61.5278
4485 | 1.0825 | 0 | 60.6638
4486 | 0 | 0 | 60.497
4487 | 0 | 0 | 60.3997
4488 | 0 | 0 | 60.3027
4489 | 0 | 0 | 60.2059
4490 | 0 | 0 | 60.1094
4491 | 0 | 0 | 60.013
4492 | 0 | 0 | 59.9169
4493 | 0 | 0 | 59.8211
4494 | 10.376 | 13.0977 | 60.5702
4495 | 1.0881 | 0 | 60.9509
4496 | 1.4149 | 0 | 59.7842
4497 | 0 | 0 | 59.5984
4498 | 0 | 0 | 59.5032
4499 | 0 | 0 | 59.4083
4500 | 0.68744 | 0 | 58.8287
4501 | 0 | 0 | 58.6914
4502 | 0 | 0 | 58.5984
4503 | 0 | 0 | 58.5056
4504 | 0 | 0 | 58.4131
4505 | 0 | 0 | 58.3207
4506 | 5.1473 | 6.9388 | 59.3004
4507 | 10.3205 | 13.1051 | 60.3758
4508 | 0 | 0 | 61.5507
4509 | 1.0813 | 0 | 60.6875
4510 | 0 | 0 | 60.5207
4511 | 0 | 0 | 60.4234
4512 | 0 | 0 | 60.3264
4513 | 0 | 0 | 60.2295
4514 | 0 | 0 | 60.1329
4515 | 0 | 0 | 60.0365
4516 | 0 | 0 | 59.9404
4517 | 0 | 0 | 59.8444
4518 | 10.3653 | 13.0831 | 60.5929
4519 | 1.0869 | 0 | 60.9721
4520 | 1.4134 | 0 | 59.8064
4521 | 0 | 0 | 59.6206
4522 | 0 | 0 | 59.5255
4523 | 0 | 0 | 59.4305
4524 | 0.68668 | 0 | 58.8514
4525 | 0 | 0 | 58.7141
4526 | 0 | 0 | 58.621
4527 | 0 | 0 | 58.5282
4528 | 0 | 0 | 58.4356
4529 | 0 | 0 | 58.3432
4530 | 5.1418 | 6.937 | 59.325
4531 | 10.3103 | 13.0907 | 60.4003
4532 | 0 | 0 | 61.5727
4533 | 1.0802 | 0 | 60.7102
4534 | 0 | 0 | 60.5434
4535 | 0 | 0 | 60.446
4536 | 0 | 0 | 60.3489
4537 | 0 | 0 | 60.252
4538 | 0 | 0 | 60.1554
4539 | 0 | 0 | 60.0589
4540 | 0 | 0 | 59.9627
4541 | 0 | 0 | 59.8667
4542 | 10.3547 | 13.0691 | 60.6147
4543 | 1.0857 | 0 | 60.9925
4544 | 1.4119 | 0 | 59.8279
4545 | 0 | 0 | 59.6422
4546 | 0 | 0 | 59.5469
4547 | 0 | 0 | 59.4519
4548 | 0.68594 | 0 | 58.8732
4549 | 0 | 0 | 58.736
4550 | 0 | 0 | 58.6429
4551 | 0 | 0 | 58.55
4552 | 0 | 0 | 58.4573
4553 | 0 | 0 | 58.3648
4554 | 5.1364 | 6.9353 | 59.3488
4555 | 10.3003 | 13.0767 | 60.4241
4556 | 0 | 0 | 61.594
4557 | 1.0791 | 0 | 60.7322
4558 | 0 | 0 | 60.5655
4559 | 0 | 0 | 60.4681
4560 | 0 | 0 | 60.3709
4561 | 0 | 0 | 60.2739
4562 | 0 | 0 | 60.1772
4563 | 0 | 0 | 60.0807
4564 | 0 | 0 | 59.9845
4565 | 0 | 0 | 59.8884
4566 | 10.3443 | 13.0554 | 60.6359
4567 | 1.0846 | 0 | 61.0123
4568 | 1.4104 | 0 | 59.8488
4569 | 0 | 0 | 59.6631
4570 | 0 | 0 | 59.5679
4571 | 0 | 0 | 59.4728
4572 | 0.68521 | 0 | 58.8946
4573 | 0 | 0 | 58.7573
4574 | 0 | 0 | 58.6641
4575 | 0 | 0 | 58.5712
4576 | 0 | 0 | 58.4785
4577 | 0 | 0 | 58.386
4578 | 5.1311 | 6.9336 | 59.372
4579 | 10.2905 | 13.063 | 60.4473
4580 | 0 | 0 | 61.6148
4581 | 1.078 | 0 | 60.7537
4582 | 0 | 0 | 60.587
4583 | 0 | 0 | 60.4895
4584 | 0 | 0 | 60.3923
4585 | 0 | 0 | 60.2953
4586 | 0 | 0 | 60.1985
4587 | 0 | 0 | 60.102
4588 | 0 | 0 | 60.0057
4589 | 0 | 0 | 59.9096
4590 | 10.137 | 13.5979 | 60.1606
4591 | 1.0979 | 0 | 61.5965
4592 | 1.4277 | 0 | 60.4183
4593 | 0 | 0 | 60.2302
4594 | 0 | 0 | 60.1335
4595 | 0 | 0 | 60.0371
4596 | 0.69357 | 0 | 59.4516
4597 | 0 | 0 | 59.3125
4598 | 0 | 0 | 59.218
4599 | 0 | 0 | 59.1238
4600 | 0 | 0 | 59.0298
4601 | 0 | 0 | 58.936
4602 | 5.1842 | 6.8251 | 59.8264
4603 | 10.1724 | 13.4619 | 60.2631
4604 | 0 | 0 | 62.4317
4605 | 1.0968 | 0 | 61.5551
4606 | 0 | 0 | 61.3853
4607 | 0 | 0 | 61.286
4608 | 0 | 0 | 61.1869
4609 | 0 | 0 | 61.088
4610 | 0 | 0 | 60.9894
4611 | 0 | 0 | 60.891
4612 | 0 | 0 | 60.7928
4613 | 0 | 0 | 60.6949
4614 | 10.2915 | 13.2286 | 60.7024
4615 | 1.1059 | 0 | 61.9707
4616 | 1.438 | 0 | 60.7836
4617 | 0 | 0 | 60.5939
4618 | 0 | 0 | 60.4965
4619 | 0 | 0 | 60.3992
4620 | 0.69859 | 0 | 59.8092
4621 | 0 | 0 | 59.6689
4622 | 0 | 0 | 59.5736
4623 | 0 | 0 | 59.4785
4624 | 0 | 0 | 59.3837
4625 | 0 | 0 | 59.2891
4626 | 5.2153 | 6.7433 | 60.1128
4627 | 10.219 | 13.3629 | 60.4686
4628 | 0 | 0 | 62.5844
4629 | 1.0991 | 0 | 61.7059
4630 | 0 | 0 | 61.5355
4631 | 0 | 0 | 61.4359
4632 | 0 | 0 | 61.3364
4633 | 0 | 0 | 61.2372
4634 | 0 | 0 | 61.1382
4635 | 0 | 0 | 61.0395
4636 | 0 | 0 | 60.941
4637 | 0 | 0 | 60.8427
4638 | 9.9058 | 13.0952 | 60.1638
4639 | 1.113 | 0 | 62.3091
4640 | 1.4473 | 0 | 61.1142
4641 | 0 | 0 | 60.9231
4642 | 0 | 0 | 60.8248
4643 | 0 | 0 | 60.7268
4644 | 0.70306 | 0 | 60.1328
4645 | 0 | 0 | 59.9915
4646 | 0 | 0 | 59.8954
4647 | 0 | 0 | 59.7996
4648 | 0 | 0 | 59.704
4649 | 0 | 0 | 59.6086
4650 | 5.0389 | 6.9472 | 59.7504
4651 | 9.9333 | 12.9598 | 60.2254
4652 | 0 | 0 | 63.1081
4653 | 1.1107 | 0 | 62.2199
4654 | 0 | 0 | 62.0477
4655 | 0 | 0 | 61.9468
4656 | 0 | 0 | 61.8461
4657 | 0 | 0 | 61.7457
4658 | 0 | 0 | 61.6456
4659 | 0 | 0 | 61.5456
4660 | 0 | 0 | 61.4459
4661 | 0 | 0 | 61.3464
4662 | 10.007 | 12.9016 | 60.5419
4663 | 1.1184 | 0 | 62.5805
4664 | 1.4544 | 0 | 61.3794
4665 | 0 | 0 | 61.1872
4666 | 0 | 0 | 61.0884
4667 | 0 | 0 | 60.9897
4668 | 0.70648 | 0 | 60.3927
4669 | 0 | 0 | 60.2505
4670 | 0 | 0 | 60.1538
4671 | 0 | 0 | 60.0574
4672 | 0 | 0 | 59.9612
4673 | 0 | 0 | 59.8652
4674 | 5.0624 | 6.9356 | 59.9874
4675 | 9.9724 | 12.8765 | 60.4045
4676 | 0 | 0 | 63.2422
4677 | 1.1126 | 0 | 62.3524
4678 | 0 | 0 | 62.1796
4679 | 0 | 0 | 62.0784
4680 | 0 | 0 | 61.9775
4681 | 0 | 0 | 61.8768
4682 | 0 | 0 | 61.7763
4683 | 0 | 0 | 61.6761
4684 | 0 | 0 | 61.576
4685 | 0 | 0 | 61.4763
4686 | 10.0235 | 12.8472 | 60.6432
4687 | 1.1189 | 0 | 62.655
4688 | 1.4549 | 0 | 61.4532
4689 | 0 | 0 | 61.2609
4690 | 0 | 0 | 61.1618
4691 | 0 | 0 | 61.063
4692 | 0.70676 | 0 | 60.4656
4693 | 0 | 0 | 60.3232
4694 | 0 | 0 | 60.2264
4695 | 0 | 0 | 60.1298
4696 | 0 | 0 | 60.0334
4697 | 0 | 0 | 59.9372
4698 | 5.0642 | 6.9318 | 60.0565
4699 | 9.9749 | 12.8483 | 60.4613
4700 | 0 | 0 | 63.286
4701 | 1.1123 | 0 | 62.3962
4702 | 0 | 0 | 62.2234
4703 | 0 | 0 | 62.1221
4704 | 0 | 0 | 62.0211
4705 | 0 | 0 | 61.9203
4706 | 0 | 0 | 61.8197
4707 | 0 | 0 | 61.7193
4708 | 0 | 0 | 61.6192
4709 | 0 | 0 | 61.5193
4710 | 10.0206 | 12.8258 | 60.6805
4711 | 1.1182 | 0 | 62.6841
4712 | 1.4541 | 0 | 61.4829
4713 | 0 | 0 | 61.2905
4714 | 0 | 0 | 61.1914
4715 | 0 | 0 | 61.0926
4716 | 0.70634 | 0 | 60.4953
4717 | 0 | 0 | 60.3529
4718 | 0 | 0 | 60.256
4719 | 0 | 0 | 60.1593
4720 | 0 | 0 | 60.0629
4721 | 0 | 0 | 59.9667
4722 | 5.0611 | 6.9299 | 60.0868
4723 | 9.9692 | 12.8329 | 60.4898
4724 | 0 | 0 | 63.3087
4725 | 1.1115 | 0 | 62.4195
4726 | 0 | 0 | 62.2466
4727 | 0 | 0 | 62.1453
4728 | 0 | 0 | 62.0442
4729 | 0 | 0 | 61.9433
4730 | 0 | 0 | 61.8427
4731 | 0 | 0 | 61.7423
4732 | 0 | 0 | 61.6421
4733 | 0 | 0 | 61.5422
4734 | 10.0135 | 12.8123 | 60.7028
4735 | 1.1173 | 0 | 62.7025
4736 | 1.4529 | 0 | 61.5022
4737 | 0 | 0 | 61.3098
4738 | 0 | 0 | 61.2107
4739 | 0 | 0 | 61.1117
4740 | 0.70577 | 0 | 60.5148
4741 | 0 | 0 | 60.3724
4742 | 0 | 0 | 60.2755
4743 | 0 | 0 | 60.1788
4744 | 0 | 0 | 60.0823
4745 | 0 | 0 | 59.986
4746 | 5.057 | 6.9284 | 60.1078
4747 | 9.9618 | 12.8207 | 60.5113
4748 | 0 | 0 | 63.3262
4749 | 1.1106 | 0 | 62.4376
4750 | 0 | 0 | 62.2648
4751 | 0 | 0 | 62.1634
4752 | 0 | 0 | 62.0622
4753 | 0 | 0 | 61.9613
4754 | 0 | 0 | 61.8606
4755 | 0 | 0 | 61.7602
4756 | 0 | 0 | 61.66
4757 | 0 | 0 | 61.56
4758 | 10.0057 | 12.8007 | 60.7212
4759 | 1.1164 | 0 | 62.7181
4760 | 1.4517 | 0 | 61.5186
4761 | 0 | 0 | 61.3263
4762 | 0 | 0 | 61.2271
4763 | 0 | 0 | 61.1282
4764 | 0.70518 | 0 | 60.5316
4765 | 0 | 0 | 60.3892
4766 | 0 | 0 | 60.2922
4767 | 0 | 0 | 60.1955
4768 | 0 | 0 | 60.0989
4769 | 0 | 0 | 60.0026
4770 | 5.0527 | 6.927 | 60.1262
4771 | 9.9543 | 12.8095 | 60.5308
4772 | 0 | 0 | 63.3422
4773 | 1.1097 | 0 | 62.4541
4774 | 0 | 0 | 62.2814
4775 | 0 | 0 | 62.1799
4776 | 0 | 0 | 62.0787
4777 | 0 | 0 | 61.9778
4778 | 0 | 0 | 61.8771
4779 | 0 | 0 | 61.7766
4780 | 0 | 0 | 61.6763
4781 | 0 | 0 | 61.5763
4782 | 9.9979 | 12.79 | 60.7383
4783 | 1.1155 | 0 | 62.7327
4784 | 1.4506 | 0 | 61.5341
4785 | 0 | 0 | 61.3418
4786 | 0 | 0 | 61.2425
4787 | 0 | 0 | 61.1436
4788 | 0.7046 | 0 | 60.5474
4789 | 0 | 0 | 60.405
4790 | 0 | 0 | 60.308
4791 | 0 | 0 | 60.2112
4792 | 0 | 0 | 60.1146
4793 | 0 | 0 | 60.0183
4794 | 5.0486 | 6.9257 | 60.1436
4795 | 9.9468 | 12.7988 | 60.5493
4796 | 0 | 0 | 63.3574
4797 | 1.1088 | 0 | 62.4699
4798 | 0 | 0 | 62.2972
4799 | 0 | 0 | 62.1957
4800 | 0 | 0 | 62.0945
4801 | 0 | 0 | 61.9935
4802 | 0 | 0 | 61.8927
4803 | 0 | 0 | 61.7922
4804 | 0 | 0 | 61.6919
4805 | 0 | 0 | 61.5919
4806 | 9.9903 | 12.7796 | 60.7547
4807 | 1.1147 | 0 | 62.7467
4808 | 1.4494 | 0 | 61.5489
4809 | 0 | 0 | 61.3566
4810 | 0 | 0 | 61.2574
4811 | 0 | 0 | 61.1583
4812 | 0.70404 | 0 | 60.5626
4813 | 0 | 0 | 60.4201
4814 | 0 | 0 | 60.3231
4815 | 0 | 0 | 60.2262
4816 | 0 | 0 | 60.1296
4817 | 0 | 0 | 60.0333
4818 | 5.0445 | 6.9244 | 60.1604
4819 | 9.9397 | 12.7885 | 60.5672
4820 | 0 | 0 | 63.3721
4821 | 1.108 | 0 | 62.4852
4822 | 0 | 0 | 62.3124
4823 | 0 | 0 | 62.2109
4824 | 0 | 0 | 62.1096
4825 | 0 | 0 | 62.0086
4826 | 0 | 0 | 61.9078
4827 | 0 | 0 | 61.8073
4828 | 0 | 0 | 61.707
4829 | 0 | 0 | 61.6069
4830 | 9.983 | 12.7697 | 60.7705
4831 | 1.1138 | 0 | 62.7602
4832 | 1.4483 | 0 | 61.5632
4833 | 0 | 0 | 61.371
4834 | 0 | 0 | 61.2717
4835 | 0 | 0 | 61.1726
4836 | 0.70349 | 0 | 60.5772
4837 | 0 | 0 | 60.4347
4838 | 0 | 0 | 60.3376
4839 | 0 | 0 | 60.2408
4840 | 0 | 0 | 60.1441
4841 | 0 | 0 | 60.0477
4842 | 5.0406 | 6.9232 | 60.1765
4843 | 9.9327 | 12.7786 | 60.5844
4844 | 0 | 0 | 63.3862
4845 | 1.1072 | 0 | 62.4998
4846 | 0 | 0 | 62.3271
4847 | 0 | 0 | 62.2256
4848 | 0 | 0 | 62.1243
4849 | 0 | 0 | 62.0232
4850 | 0 | 0 | 61.9224
4851 | 0 | 0 | 61.8218
4852 | 0 | 0 | 61.7215
4853 | 0 | 0 | 61.6213
4854 | 9.976 | 12.7601 | 60.7857
4855 | 1.113 | 0 | 62.7732
4856 | 1.4473 | 0 | 61.5769
4857 | 0 | 0 | 61.3848
4858 | 0 | 0 | 61.2854
4859 | 0 | 0 | 61.1863
4860 | 0.70297 | 0 | 60.5912
4861 | 0 | 0 | 60.4488
4862 | 0 | 0 | 60.3517
4863 | 0 | 0 | 60.2548
4864 | 0 | 0 | 60.1581
4865 | 0 | 0 | 60.0617
4866 | 5.0369 | 6.922 | 60.1921
4867 | 9.926 | 12.769 | 60.601
4868 | 0 | 0 | 63.3999
4869 | 1.1064 | 0 | 62.514
4870 | 0 | 0 | 62.3413
4871 | 0 | 0 | 62.2397
4872 | 0 | 0 | 62.1384
4873 | 0 | 0 | 62.0373
4874 | 0 | 0 | 61.9364
4875 | 0 | 0 | 61.8358
4876 | 0 | 0 | 61.7354
4877 | 0 | 0 | 61.6353
4878 | 9.9692 | 12.7508 | 60.8004
4879 | 1.1122 | 0 | 62.7857
4880 | 1.4462 | 0 | 61.5902
4881 | 0 | 0 | 61.3981
4882 | 0 | 0 | 61.2987
4883 | 0 | 0 | 61.1996
4884 | 0.70247 | 0 | 60.6048
4885 | 0 | 0 | 60.4624
4886 | 0 | 0 | 60.3652
4887 | 0 | 0 | 60.2683
4888 | 0 | 0 | 60.1716
4889 | 0 | 0 | 60.0751
4890 | 5.0333 | 6.9208 | 60.207
4891 | 9.9196 | 12.7598 | 60.6169
4892 | 0 | 0 | 63.413
4893 | 1.1056 | 0 | 62.5276
4894 | 0 | 0 | 62.3549
4895 | 0 | 0 | 62.2533
4896 | 0 | 0 | 62.1519
4897 | 0 | 0 | 62.0508
4898 | 0 | 0 | 61.9499
4899 | 0 | 0 | 61.8493
4900 | 0 | 0 | 61.7489
4901 | 0 | 0 | 61.6487
4902 | 9.9627 | 12.7419 | 60.8145
4903 | 1.1115 | 0 | 62.7978
4904 | 1.4453 | 0 | 61.6029
4905 | 0 | 0 | 61.4108
4906 | 0 | 0 | 61.3114
4907 | 0 | 0 | 61.2123
4908 | 0.70199 | 0 | 60.6178
4909 | 0 | 0 | 60.4754
4910 | 0 | 0 | 60.3782
4911 | 0 | 0 | 60.2812
4912 | 0 | 0 | 60.1845
4913 | 0 | 0 | 60.088
4914 | 5.0298 | 6.9198 | 60.2214
4915 | 9.9134 | 12.751 | 60.6323
4916 | 0 | 0 | 63.4256
4917 | 1.1049 | 0 | 62.5407
4918 | 0 | 0 | 62.368
4919 | 0 | 0 | 62.2664
4920 | 0 | 0 | 62.165
4921 | 0 | 0 | 62.0638
4922 | 0 | 0 | 61.9629
4923 | 0 | 0 | 61.8622
4924 | 0 | 0 | 61.7618
4925 | 0 | 0 | 61.6616
4926 | 9.9565 | 12.7334 | 60.828
4927 | 1.1108 | 0 | 62.8093
4928 | 1.4443 | 0 | 61.6152
4929 | 0 | 0 | 61.4231
4930 | 0 | 0 | 61.3237
4931 | 0 | 0 | 61.2245
4932 | 0.70153 | 0 | 60.6303
4933 | 0 | 0 | 60.4879
4934 | 0 | 0 | 60.3907
4935 | 0 | 0 | 60.2937
4936 | 0 | 0 | 60.1969
4937 | 0 | 0 | 60.1004
4938 | 5.0265 | 6.9187 | 60.2352
4939 | 9.9075 | 12.7425 | 60.647
4940 | 0 | 0 | 63.4376
4941 | 1.1042 | 0 | 62.5532
4942 | 0 | 0 | 62.3805
4943 | 0 | 0 | 62.2789
4944 | 0 | 0 | 62.1774
4945 | 0 | 0 | 62.0763
4946 | 0 | 0 | 61.9753
4947 | 0 | 0 | 61.8746
4948 | 0 | 0 | 61.7741
4949 | 0 | 0 | 61.6739
4950 | 9.9506 | 12.7252 | 60.841
4951 | 1.1101 | 0 | 62.8204
4952 | 1.4434 | 0 | 61.6269
4953 | 0 | 0 | 61.4348
4954 | 0 | 0 | 61.3354
4955 | 0 | 0 | 61.2362
4956 | 0.70109 | 0 | 60.6423
4957 | 0 | 0 | 60.4998
4958 | 0 | 0 | 60.4026
4959 | 0 | 0 | 60.3056
4960 | 0 | 0 | 60.2088
4961 | 0 | 0 | 60.1122
4962 | 5.0234 | 6.9177 | 60.2484
4963 | 9.9019 | 12.7344 | 60.661
4964 | 0 | 0 | 63.4492
4965 | 1.1036 | 0 | 62.5652
4966 | 0 | 0 | 62.3925
4967 | 0 | 0 | 62.2908
4968 | 0 | 0 | 62.1894
4969 | 0 | 0 | 62.0882
4970 | 0 | 0 | 61.9872
4971 | 0 | 0 | 61.8865
4972 | 0 | 0 | 61.786
4973 | 0 | 0 | 61.6857
4974 | 9.945 | 12.7174 | 60.8534
4975 | 1.1094 | 0 | 62.8309
4976 | 1.4426 | 0 | 61.638
4977 | 0 | 0 | 61.446
4978 | 0 | 0 | 61.3465
4979 | 0 | 0 | 61.2473
4980 | 0.70067 | 0 | 60.6537
4981 | 0 | 0 | 60.5113
4982 | 0 | 0 | 60.414
4983 | 0 | 0 | 60.3169
4984 | 0 | 0 | 60.2201
4985 | 0 | 0 | 60.1235
4986 | 5.0203 | 6.9168 | 60.261
4987 | 9.8965 | 12.7267 | 60.6744
4988 | 0 | 0 | 63.4602
4989 | 1.1029 | 0 | 62.5766
4990 | 0 | 0 | 62.404
4991 | 0 | 0 | 62.3023
4992 | 0 | 0 | 62.2008
4993 | 0 | 0 | 62.0995
4994 | 0 | 0 | 61.9985
4995 | 0 | 0 | 61.8978
4996 | 0 | 0 | 61.7972
4997 | 0 | 0 | 61.697
4998 | 9.9396 | 12.71 | 60.8652
4999 | 1.1088 | 0 | 62.841
5000 | 1.4418 | 0 | 61.6487
5001 | 0 | 0 | 61.4567
5002 | 0 | 0 | 61.3572
5003 | 0 | 0 | 61.2579
5004 | 0.70027 | 0 | 60.6645
5005 | 0 | 0 | 60.5221
5006 | 0 | 0 | 60.4248
5007 | 0 | 0 | 60.3278
5008 | 0 | 0 | 60.2309
5009 | 0 | 0 | 60.1343
5010 | 5.0175 | 6.9158 | 60.273
5011 | 9.8914 | 12.7193 | 60.6872
5012 | 0 | 0 | 63.4707
5013 | 1.1023 | 0 | 62.5875
5014 | 0 | 0 | 62.4149
5015 | 0 | 0 | 62.3131
5016 | 0 | 0 | 62.2116
5017 | 0 | 0 | 62.1104
5018 | 0 | 0 | 62.0093
5019 | 0 | 0 | 61.9085
5020 | 0 | 0 | 61.808
5021 | 0 | 0 | 61.7077
5022 | 9.9345 | 12.7029 | 60.8764
5023 | 1.1082 | 0 | 62.8505
5024 | 1.441 | 0 | 61.6588
5025 | 0 | 0 | 61.4668
5026 | 0 | 0 | 61.3673
5027 | 0 | 0 | 61.268
5028 | 0.6999 | 0 | 60.6749
5029 | 0 | 0 | 60.5325
5030 | 0 | 0 | 60.4351
5031 | 0 | 0 | 60.338
5032 | 0 | 0 | 60.2412
5033 | 0 | 0 | 60.1445
5034 | 5.0148 | 6.915 | 60.2844
5035 | 9.8866 | 12.7123 | 60.6993
5036 | 0 | 0 | 63.4806
5037 | 1.1018 | 0 | 62.5978
5038 | 0 | 0 | 62.4252
5039 | 0 | 0 | 62.3234
5040 | 0 | 0 | 62.2219
5041 | 0 | 0 | 62.1206
5042 | 0 | 0 | 62.0196
5043 | 0 | 0 | 61.9188
5044 | 0 | 0 | 61.8182
5045 | 0 | 0 | 61.7178
5046 | 9.9298 | 12.6963 | 60.887
5047 | 1.1077 | 0 | 62.8596
5048 | 1.4403 | 0 | 61.6684
5049 | 0 | 0 | 61.4764
5050 | 0 | 0 | 61.3769
5051 | 0 | 0 | 61.2776
5052 | 0.69954 | 0 | 60.6847
5053 | 0 | 0 | 60.5422
5054 | 0 | 0 | 60.4449
5055 | 0 | 0 | 60.3478
5056 | 0 | 0 | 60.2509
5057 | 0 | 0 | 60.1542
5058 | 5.0122 | 6.9142 | 60.2952
5059 | 9.882 | 12.7057 | 60.7108
5060 | 0 | 0 | 63.49
5061 | 1.1012 | 0 | 62.6076
5062 | 0 | 0 | 62.435
5063 | 0 | 0 | 62.3332
5064 | 0 | 0 | 62.2316
5065 | 0 | 0 | 62.1303
5066 | 0 | 0 | 62.0293
5067 | 0 | 0 | 61.9284
5068 | 0 | 0 | 61.8278
5069 | 0 | 0 | 61.7275
5070 | 9.9253 | 12.6899 | 60.8971
5071 | 1.1071 | 0 | 62.8681
5072 | 1.4396 | 0 | 61.6774
5073 | 0 | 0 | 61.4855
5074 | 0 | 0 | 61.3859
5075 | 0 | 0 | 61.2866
5076 | 0.69921 | 0 | 60.6939
5077 | 0 | 0 | 60.5515
5078 | 0 | 0 | 60.4541
5079 | 0 | 0 | 60.357
5080 | 0 | 0 | 60.26
5081 | 0 | 0 | 60.1634
5082 | 5.0098 | 6.9134 | 60.3054
5083 | 9.8777 | 12.6995 | 60.7216
5084 | 0 | 0 | 63.4989
5085 | 1.1007 | 0 | 62.6168
5086 | 0 | 0 | 62.4442
5087 | 0 | 0 | 62.3424
5088 | 0 | 0 | 62.2408
5089 | 0 | 0 | 62.1395
5090 | 0 | 0 | 62.0384
5091 | 0 | 0 | 61.9375
5092 | 0 | 0 | 61.8369
5093 | 0 | 0 | 61.7365
5094 | 9.9211 | 12.684 | 60.9065
5095 | 1.1066 | 0 | 62.8762
5096 | 1.439 | 0 | 61.6859
5097 | 0 | 0 | 61.494
5098 | 0 | 0 | 61.3944
5099 | 0 | 0 | 61.2951
5100 | 0.69889 | 0 | 60.7026
5101 | 0 | 0 | 60.5601
5102 | 0 | 0 | 60.4628
5103 | 0 | 0 | 60.3656
5104 | 0 | 0 | 60.2687
5105 | 0 | 0 | 60.172
5106 | 5.0076 | 6.9127 | 60.3149
5107 | 9.8737 | 12.6937 | 60.7317
5108 | 0 | 0 | 63.5072
5109 | 1.1003 | 0 | 62.6254
5110 | 0 | 0 | 62.4528
5111 | 0 | 0 | 62.351
5112 | 0 | 0 | 62.2494
5113 | 0 | 0 | 62.1481
5114 | 0 | 0 | 62.0469
5115 | 0 | 0 | 61.9461
5116 | 0 | 0 | 61.8454
5117 | 0 | 0 | 61.745
5118 | 9.9172 | 12.6784 | 60.9154
5119 | 1.1062 | 0 | 62.8837
5120 | 1.4384 | 0 | 61.6939
5121 | 0 | 0 | 61.502
5122 | 0 | 0 | 61.4024
5123 | 0 | 0 | 61.303
5124 | 0.6986 | 0 | 60.7107
5125 | 0 | 0 | 60.5683
5126 | 0 | 0 | 60.4708
5127 | 0 | 0 | 60.3737
5128 | 0 | 0 | 60.2767
5129 | 0 | 0 | 60.18
5130 | 5.0055 | 6.912 | 60.3239
5131 | 9.87 | 12.6882 | 60.7412
5132 | 0 | 0 | 63.515
5133 | 1.0998 | 0 | 62.6335
5134 | 0 | 0 | 62.4609
5135 | 0 | 0 | 62.3591
5136 | 0 | 0 | 62.2575
5137 | 0 | 0 | 62.1561
5138 | 0 | 0 | 62.0549
5139 | 0 | 0 | 61.954
5140 | 0 | 0 | 61.8534
5141 | 0 | 0 | 61.753
5142 | 9.9136 | 12.6733 | 60.9236
5143 | 1.1058 | 0 | 62.8907
5144 | 1.4378 | 0 | 61.7013
5145 | 0 | 0 | 61.5094
5146 | 0 | 0 | 61.4098
5147 | 0 | 0 | 61.3104
5148 | 0.69833 | 0 | 60.7182
5149 | 0 | 0 | 60.5758
5150 | 0 | 0 | 60.4784
5151 | 0 | 0 | 60.3812
5152 | 0 | 0 | 60.2842
5153 | 0 | 0 | 60.1875
5154 | 5.0035 | 6.9114 | 60.3322
5155 | 9.8665 | 12.6831 | 60.75
5156 | 0 | 0 | 63.5223
5157 | 1.0994 | 0 | 62.641
5158 | 0 | 0 | 62.4684
5159 | 0 | 0 | 62.3666
5160 | 0 | 0 | 62.2649
5161 | 0 | 0 | 62.1635
5162 | 0 | 0 | 62.0624
5163 | 0 | 0 | 61.9615
5164 | 0 | 0 | 61.8608
5165 | 0 | 0 | 61.7603
5166 | 9.9103 | 12.6685 | 60.9313
5167 | 1.1054 | 0 | 62.8972
5168 | 1.4373 | 0 | 61.7081
5169 | 0 | 0 | 61.5163
5170 | 0 | 0 | 61.4166
5171 | 0 | 0 | 61.3172
5172 | 0.69808 | 0 | 60.7252
5173 | 0 | 0 | 60.5828
5174 | 0 | 0 | 60.4854
5175 | 0 | 0 | 60.3882
5176 | 0 | 0 | 60.2912
5177 | 0 | 0 | 60.1944
5178 | 5.0017 | 6.9093 | 60.3392
5179 | 9.8631 | 12.6788 | 60.7573
5180 | 0 | 0 | 63.5283
5181 | 1.099 | 0 | 62.6473
5182 | 0 | 0 | 62.4747
5183 | 0 | 0 | 62.3728
5184 | 0 | 0 | 62.2712
5185 | 0 | 0 | 62.1698
5186 | 0 | 0 | 62.0686
5187 | 0 | 0 | 61.9677
5188 | 0 | 0 | 61.867
5189 | 0 | 0 | 61.7665
5190 | 9.9071 | 12.6643 | 60.9379
5191 | 1.105 | 0 | 62.9028
5192 | 1.4369 | 0 | 61.7141
5193 | 0 | 0 | 61.5223
5194 | 0 | 0 | 61.4226
5195 | 0 | 0 | 61.3232
5196 | 0.69785 | 0 | 60.7314
5197 | 0 | 0 | 60.5889
5198 | 0 | 0 | 60.4915
5199 | 0 | 0 | 60.3942
5200 | 0 | 0 | 60.2972
5201 | 0 | 0 | 60.2005
5202 | 5 | 6.9059 | 60.3447
5203 | 9.8596 | 12.6752 | 60.7628
5204 | 0 | 0 | 63.5329
5205 | 1.0986 | 0 | 62.6522
5206 | 0 | 0 | 62.4796
5207 | 0 | 0 | 62.3777
5208 | 0 | 0 | 62.2761
5209 | 0 | 0 | 62.1747
5210 | 0 | 0 | 62.0735
5211 | 0 | 0 | 61.9725
5212 | 0 | 0 | 61.8718
5213 | 0 | 0 | 61.7714
5214 | 9.9041 | 12.6608 | 60.9432
5215 | 1.1047 | 0 | 62.9076
5216 | 1.4364 | 0 | 61.7191
5217 | 0 | 0 | 61.5273
5218 | 0 | 0 | 61.4276
5219 | 0 | 0 | 61.3282
5220 | 0.69763 | 0 | 60.7365
5221 | 0 | 0 | 60.5941
5222 | 0 | 0 | 60.4966
5223 | 0 | 0 | 60.3994
5224 | 0 | 0 | 60.3024
5225 | 0 | 0 | 60.2056
5226 | 4.9984 | 6.9029 | 60.3494
5227 | 9.8564 | 12.6721 | 60.7676
5228 | 0 | 0 | 63.537
5229 | 1.0983 | 0 | 62.6565
5230 | 0 | 0 | 62.484
5231 | 0 | 0 | 62.3821
5232 | 0 | 0 | 62.2804
5233 | 0 | 0 | 62.179
5234 | 0 | 0 | 62.0778
5235 | 0 | 0 | 61.9768
5236 | 0 | 0 | 61.8761
5237 | 0 | 0 | 61.7756
5238 | 9.9013 | 12.6577 | 60.948
5239 | 1.1044 | 0 | 62.9117
5240 | 1.436 | 0 | 61.7236
5241 | 0 | 0 | 61.5318
5242 | 0 | 0 | 61.4321
5243 | 0 | 0 | 61.3327
5244 | 0.69744 | 0 | 60.7411
5245 | 0 | 0 | 60.5987
5246 | 0 | 0 | 60.5012
5247 | 0 | 0 | 60.404
5248 | 0 | 0 | 60.3069
5249 | 0 | 0 | 60.2102
5250 | 4.9969 | 6.9002 | 60.3535
5251 | 9.8535 | 12.6692 | 60.772
5252 | 0 | 0 | 63.5407
5253 | 1.098 | 0 | 62.6604
5254 | 0 | 0 | 62.4878
5255 | 0 | 0 | 62.3859
5256 | 0 | 0 | 62.2843
5257 | 0 | 0 | 62.1828
5258 | 0 | 0 | 62.0816
5259 | 0 | 0 | 61.9807
5260 | 0 | 0 | 61.8799
5261 | 0 | 0 | 61.7795
5262 | 9.8989 | 12.655 | 60.9523
5263 | 1.1041 | 0 | 62.9155
5264 | 1.4357 | 0 | 61.7276
5265 | 0 | 0 | 61.5358
5266 | 0 | 0 | 61.4361
5267 | 0 | 0 | 61.3367
5268 | 0.69727 | 0 | 60.7452
5269 | 0 | 0 | 60.6028
5270 | 0 | 0 | 60.5053
5271 | 0 | 0 | 60.408
5272 | 0 | 0 | 60.311
5273 | 0 | 0 | 60.2142
5274 | 4.9957 | 6.8979 | 60.3573
5275 | 9.8509 | 12.6668 | 60.7758
5276 | 0 | 0 | 63.5439
5277 | 1.0977 | 0 | 62.6638
5278 | 0 | 0 | 62.4913
5279 | 0 | 0 | 62.3894
5280 | 0 | 0 | 62.2877
5281 | 0 | 0 | 62.1862
5282 | 0 | 0 | 62.085
5283 | 0 | 0 | 61.9841
5284 | 0 | 0 | 61.8833
5285 | 0 | 0 | 61.7828
5286 | 9.8968 | 12.6525 | 60.9561
5287 | 1.1039 | 0 | 62.9187
5288 | 1.4354 | 0 | 61.7311
5289 | 0 | 0 | 61.5393
5290 | 0 | 0 | 61.4396
5291 | 0 | 0 | 61.3402
5292 | 0.69712 | 0 | 60.7488
5293 | 0 | 0 | 60.6064
5294 | 0 | 0 | 60.5089
5295 | 0 | 0 | 60.4116
5296 | 0 | 0 | 60.3146
5297 | 0 | 0 | 60.2178
5298 | 4.9946 | 6.8958 | 60.3605
5299 | 9.8487 | 12.6646 | 60.7792
5300 | 0 | 0 | 63.5467
5301 | 1.0975 | 0 | 62.6668
5302 | 0 | 0 | 62.4943
5303 | 0 | 0 | 62.3924
5304 | 0 | 0 | 62.2907
5305 | 0 | 0 | 62.1892
5306 | 0 | 0 | 62.088
5307 | 0 | 0 | 61.987
5308 | 0 | 0 | 61.8863
5309 | 0 | 0 | 61.7858
5310 | 9.8951 | 12.6504 | 60.9593
5311 | 1.1037 | 0 | 62.9216
5312 | 1.4351 | 0 | 61.7341
5313 | 0 | 0 | 61.5423
5314 | 0 | 0 | 61.4426
5315 | 0 | 0 | 61.3432
5316 | 0.69699 | 0 | 60.7519
5317 | 0 | 0 | 60.6095
5318 | 0 | 0 | 60.512
5319 | 0 | 0 | 60.4147
5320 | 0 | 0 | 60.3176
5321 | 0 | 0 | 60.2208
5322 | 4.9936 | 6.8941 | 60.3633
5323 | 9.8468 | 12.6627 | 60.782
5324 | 0 | 0 | 63.5492
5325 | 1.0973 | 0 | 62.6693
5326 | 0 | 0 | 62.4968
5327 | 0 | 0 | 62.3949
5328 | 0 | 0 | 62.2932
5329 | 0 | 0 | 62.1918
5330 | 0 | 0 | 62.0905
5331 | 0 | 0 | 61.9896
5332 | 0 | 0 | 61.8888
5333 | 0 | 0 | 61.7883
5334 | 9.8936 | 12.6487 | 60.962
5335 | 1.1035 | 0 | 62.9239
5336 | 1.4349 | 0 | 61.7366
5337 | 0 | 0 | 61.5448
5338 | 0 | 0 | 61.4451
5339 | 0 | 0 | 61.3457
5340 | 0.69689 | 0 | 60.7545
5341 | 0 | 0 | 60.612
5342 | 0 | 0 | 60.5145
5343 | 0 | 0 | 60.4172
5344 | 0 | 0 | 60.3202
5345 | 0 | 0 | 60.2234
5346 | 4.9929 | 6.8926 | 60.3656
5347 | 9.8453 | 12.6612 | 60.7844
5348 | 0 | 0 | 63.5511
5349 | 1.0971 | 0 | 62.6715
5350 | 0 | 0 | 62.499
5351 | 0 | 0 | 62.397
5352 | 0 | 0 | 62.2953
5353 | 0 | 0 | 62.1939
5354 | 0 | 0 | 62.0926
5355 | 0 | 0 | 61.9916
5356 | 0 | 0 | 61.8909
5357 | 0 | 0 | 61.7904
5358 | 9.8925 | 12.6473 | 60.9643
5359 | 1.1034 | 0 | 62.9258
5360 | 1.4347 | 0 | 61.7386
5361 | 0 | 0 | 61.5469
5362 | 0 | 0 | 61.4472
5363 | 0 | 0 | 61.3477
5364 | 0.69681 | 0 | 60.7565
5365 | 0 | 0 | 60.6141
5366 | 0 | 0 | 60.5166
5367 | 0 | 0 | 60.4193
5368 | 0 | 0 | 60.3223
5369 | 0 | 0 | 60.2254
5370 | 4.9923 | 6.8914 | 60.3675
5371 | 9.8441 | 12.66 | 60.7863
5372 | 0 | 0 | 63.5527
5373 | 1.097 | 0 | 62.6731
5374 | 0 | 0 | 62.5006
5375 | 0 | 0 | 62.3987
5376 | 0 | 0 | 62.297
5377 | 0 | 0 | 62.1955
5378 | 0 | 0 | 62.0943
5379 | 0 | 0 | 61.9933
5380 | 0 | 0 | 61.8925
5381 | 0 | 0 | 61.792
5382 | 9.8918 | 12.6462 | 60.966
5383 | 1.1033 | 0 | 62.9273
5384 | 1.4346 | 0 | 61.7402
5385 | 0 | 0 | 61.5484
5386 | 0 | 0 | 61.4487
5387 | 0 | 0 | 61.3492
5388 | 0.69675 | 0 | 60.7581
5389 | 0 | 0 | 60.6157
5390 | 0 | 0 | 60.5182
5391 | 0 | 0 | 60.4209
5392 | 0 | 0 | 60.3238
5393 | 0 | 0 | 60.227
5394 | 4.9919 | 6.8905 | 60.3689
5395 | 9.8432 | 12.6591 | 60.7877
5396 | 0 | 0 | 63.5539
5397 | 1.0969 | 0 | 62.6743
5398 | 0 | 0 | 62.5019
5399 | 0 | 0 | 62.3999
5400 | 0 | 0 | 62.2982
5401 | 0 | 0 | 62.1967
5402 | 0 | 0 | 62.0955
5403 | 0 | 0 | 61.9945
5404 | 0 | 0 | 61.8938
5405 | 0 | 0 | 61.7932
5406 | 9.8914 | 12.6455 | 60.9672
5407 | 1.1033 | 0 | 62.9283
5408 | 1.4346 | 0 | 61.7412
5409 | 0 | 0 | 61.5495
5410 | 0 | 0 | 61.4498
5411 | 0 | 0 | 61.3503
5412 | 0.69672 | 0 | 60.7592
5413 | 0 | 0 | 60.6168
5414 | 0 | 0 | 60.5192
5415 | 0 | 0 | 60.4219
5416 | 0 | 0 | 60.3249
5417 | 0 | 0 | 60.228
5418 | 4.9916 | 6.8899 | 60.3698
5419 | 9.8427 | 12.6585 | 60.7886
5420 | 0 | 0 | 63.5546
5421 | 1.0968 | 0 | 62.6751
5422 | 0 | 0 | 62.5027
5423 | 0 | 0 | 62.4007
5424 | 0 | 0 | 62.299
5425 | 0 | 0 | 62.1975
5426 | 0 | 0 | 62.0963
5427 | 0 | 0 | 61.9953
5428 | 0 | 0 | 61.8945
5429 | 0 | 0 | 61.794
5430 | 9.8913 | 12.6451 | 60.9679
5431 | 1.1032 | 0 | 62.9288
5432 | 1.4345 | 0 | 61.7418
5433 | 0 | 0 | 61.55
5434 | 0 | 0 | 61.4503
5435 | 0 | 0 | 61.3508
5436 | 0.69671 | 0 | 60.7597
5437 | 0 | 0 | 60.6173
5438 | 0 | 0 | 60.5198
5439 | 0 | 0 | 60.4225
5440 | 0 | 0 | 60.3254
5441 | 0 | 0 | 60.2286
5442 | 4.9915 | 6.8896 | 60.3702
5443 | 9.8425 | 12.6583 | 60.789
5444 | 0 | 0 | 63.555
5445 | 1.0968 | 0 | 62.6755
5446 | 0 | 0 | 62.503
5447 | 0 | 0 | 62.401
5448 | 0 | 0 | 62.2993
5449 | 0 | 0 | 62.1979
5450 | 0 | 0 | 62.0966
5451 | 0 | 0 | 61.9956
5452 | 0 | 0 | 61.8949
5453 | 0 | 0 | 61.7944
5454 | 9.8915 | 12.645 | 60.968
5455 | 1.1033 | 0 | 62.9289
5456 | 1.4346 | 0 | 61.7418
5457 | 0 | 0 | 61.5501
5458 | 0 | 0 | 61.4504
5459 | 0 | 0 | 61.3509
5460 | 0.69672 | 0 | 60.7598
5461 | 0 | 0 | 60.6174
5462 | 0 | 0 | 60.5198
5463 | 0 | 0 | 60.4225
5464 | 0 | 0 | 60.3255
5465 | 0 | 0 | 60.2286
5466 | 4.9916 | 6.8896 | 60.3702
5467 | 9.8427 | 12.6583 | 60.7889
5468 | 0 | 0 | 63.5549
5469 | 1.0968 | 0 | 62.6754
5470 | 0 | 0 | 62.5029
5471 | 0 | 0 | 62.401
5472 | 0 | 0 | 62.2992
5473 | 0 | 0 | 62.1978
5474 | 0 | 0 | 62.0965
5475 | 0 | 0 | 61.9955
5476 | 0 | 0 | 61.8948
5477 | 0 | 0 | 61.7943
5478 | 9.8921 | 12.6453 | 60.9677
5479 | 1.1033 | 0 | 62.9286
5480 | 1.4346 | 0 | 61.7414
5481 | 0 | 0 | 61.5497
5482 | 0 | 0 | 61.4499
5483 | 0 | 0 | 61.3505
5484 | 0.69676 | 0 | 60.7593
5485 | 0 | 0 | 60.6169
5486 | 0 | 0 | 60.5194
5487 | 0 | 0 | 60.4221
5488 | 0 | 0 | 60.325
5489 | 0 | 0 | 60.2282
5490 | 4.9919 | 6.8899 | 60.3698
5491 | 9.8432 | 12.6587 | 60.7883
5492 | 0 | 0 | 63.5544
5493 | 1.0969 | 0 | 62.6748
5494 | 0 | 0 | 62.5024
5495 | 0 | 0 | 62.4004
5496 | 0 | 0 | 62.2987
5497 | 0 | 0 | 62.1972
5498 | 0 | 0 | 62.096
5499 | 0 | 0 | 61.995
5500 | 0 | 0 | 61.8942
5501 | 0 | 0 | 61.7937
5502 | 9.893 | 12.6459 | 60.9669
5503 | 1.1034 | 0 | 62.9277
5504 | 1.4348 | 0 | 61.7405
5505 | 0 | 0 | 61.5487
5506 | 0 | 0 | 61.449
5507 | 0 | 0 | 61.3496
5508 | 0.69682 | 0 | 60.7584
5509 | 0 | 0 | 60.616
5510 | 0 | 0 | 60.5184
5511 | 0 | 0 | 60.4211
5512 | 0 | 0 | 60.3241
5513 | 0 | 0 | 60.2272
5514 | 4.9923 | 6.8905 | 60.3689
5515 | 9.844 | 12.6594 | 60.7872
5516 | 0 | 0 | 63.5535
5517 | 1.0969 | 0 | 62.6739
5518 | 0 | 0 | 62.5014
5519 | 0 | 0 | 62.3994
5520 | 0 | 0 | 62.2977
5521 | 0 | 0 | 62.1963
5522 | 0 | 0 | 62.095
5523 | 0 | 0 | 61.994
5524 | 0 | 0 | 61.8933
5525 | 0 | 0 | 61.7928
5526 | 9.8943 | 12.6468 | 60.9655
5527 | 1.1035 | 0 | 62.9265
5528 | 1.4349 | 0 | 61.7391
5529 | 0 | 0 | 61.5473
5530 | 0 | 0 | 61.4476
5531 | 0 | 0 | 61.3481
5532 | 0.6969 | 0 | 60.7569
5533 | 0 | 0 | 60.6145
5534 | 0 | 0 | 60.517
5535 | 0 | 0 | 60.4197
5536 | 0 | 0 | 60.3226
5537 | 0 | 0 | 60.2258
5538 | 4.9929 | 6.8914 | 60.3675
5539 | 9.8452 | 12.6605 | 60.7857
5540 | 0 | 0 | 63.5521
5541 | 1.0971 | 0 | 62.6724
5542 | 0 | 0 | 62.4999
5543 | 0 | 0 | 62.398
5544 | 0 | 0 | 62.2963
5545 | 0 | 0 | 62.1948
5546 | 0 | 0 | 62.0936
5547 | 0 | 0 | 61.9926
5548 | 0 | 0 | 61.8919
5549 | 0 | 0 | 61.7914
5550 | 9.8958 | 12.6481 | 60.9636
5551 | 1.1037 | 0 | 62.9247
5552 | 1.4351 | 0 | 61.7372
5553 | 0 | 0 | 61.5454
5554 | 0 | 0 | 61.4457
5555 | 0 | 0 | 61.3462
5556 | 0.69701 | 0 | 60.7549
5557 | 0 | 0 | 60.6125
5558 | 0 | 0 | 60.515
5559 | 0 | 0 | 60.4177
5560 | 0 | 0 | 60.3207
5561 | 0 | 0 | 60.2238
5562 | 4.9937 | 6.8926 | 60.3656
5563 | 9.8468 | 12.6618 | 60.7836
5564 | 0 | 0 | 63.5504
5565 | 1.0972 | 0 | 62.6706
5566 | 0 | 0 | 62.4981
5567 | 0 | 0 | 62.3961
5568 | 0 | 0 | 62.2944
5569 | 0 | 0 | 62.193
5570 | 0 | 0 | 62.0918
5571 | 0 | 0 | 61.9908
5572 | 0 | 0 | 61.89
5573 | 0 | 0 | 61.7895
5574 | 9.8977 | 12.6497 | 60.9612
5575 | 1.1039 | 0 | 62.9225
5576 | 1.4354 | 0 | 61.7348
5577 | 0 | 0 | 61.543
5578 | 0 | 0 | 61.4433
5579 | 0 | 0 | 61.3439
5580 | 0.69714 | 0 | 60.7525
5581 | 0 | 0 | 60.6101
5582 | 0 | 0 | 60.5125
5583 | 0 | 0 | 60.4153
5584 | 0 | 0 | 60.3182
5585 | 0 | 0 | 60.2214
5586 | 4.9947 | 6.8941 | 60.3633
5587 | 9.8486 | 12.6635 | 60.7811
5588 | 0 | 0 | 63.5482
5589 | 1.0974 | 0 | 62.6683
5590 | 0 | 0 | 62.4958
5591 | 0 | 0 | 62.3938
5592 | 0 | 0 | 62.2921
5593 | 0 | 0 | 62.1907
5594 | 0 | 0 | 62.0895
5595 | 0 | 0 | 61.9885
5596 | 0 | 0 | 61.8878
5597 | 0 | 0 | 61.7872
5598 | 9.9 | 12.6517 | 60.9583
5599 | 1.1042 | 0 | 62.9199
5600 | 1.4357 | 0 | 61.7319
5601 | 0 | 0 | 61.5401
5602 | 0 | 0 | 61.4404
5603 | 0 | 0 | 61.341
5604 | 0.69729 | 0 | 60.7495
5605 | 0 | 0 | 60.6071
5606 | 0 | 0 | 60.5096
5607 | 0 | 0 | 60.4123
5608 | 0 | 0 | 60.3153
5609 | 0 | 0 | 60.2184
5610 | 4.9958 | 6.8959 | 60.3605
5611 | 9.8508 | 12.6655 | 60.778
5612 | 0 | 0 | 63.5456
5613 | 1.0977 | 0 | 62.6655
5614 | 0 | 0 | 62.493
5615 | 0 | 0 | 62.3911
5616 | 0 | 0 | 62.2894
5617 | 0 | 0 | 62.188
5618 | 0 | 0 | 62.0867
5619 | 0 | 0 | 61.9858
5620 | 0 | 0 | 61.885
5621 | 0 | 0 | 61.7845
5622 | 9.9025 | 12.654 | 60.9549
5623 | 1.1044 | 0 | 62.9168
5624 | 1.4361 | 0 | 61.7286
5625 | 0 | 0 | 61.5368
5626 | 0 | 0 | 61.4371
5627 | 0 | 0 | 61.3376
5628 | 0.69747 | 0 | 60.746
5629 | 0 | 0 | 60.6036
5630 | 0 | 0 | 60.5061
5631 | 0 | 0 | 60.4088
5632 | 0 | 0 | 60.3118
5633 | 0 | 0 | 60.215
5634 | 4.9971 | 6.8979 | 60.3573
5635 | 9.8534 | 12.6678 | 60.7745
5636 | 0 | 0 | 63.5426
5637 | 1.0979 | 0 | 62.6623
5638 | 0 | 0 | 62.4898
5639 | 0 | 0 | 62.3879
5640 | 0 | 0 | 62.2862
5641 | 0 | 0 | 62.1848
5642 | 0 | 0 | 62.0836
5643 | 0 | 0 | 61.9826
5644 | 0 | 0 | 61.8819
5645 | 0 | 0 | 61.7814
5646 | 9.9054 | 12.6566 | 60.951
5647 | 1.1047 | 0 | 62.9132
5648 | 1.4365 | 0 | 61.7247
5649 | 0 | 0 | 61.5329
5650 | 0 | 0 | 61.4332
5651 | 0 | 0 | 61.3338
5652 | 0.69766 | 0 | 60.742
5653 | 0 | 0 | 60.5996
5654 | 0 | 0 | 60.5021
5655 | 0 | 0 | 60.4049
5656 | 0 | 0 | 60.3079
5657 | 0 | 0 | 60.2111
5658 | 4.9985 | 6.9003 | 60.3536
5659 | 9.8562 | 12.6705 | 60.7705
5660 | 0 | 0 | 63.5392
5661 | 1.0982 | 0 | 62.6587
5662 | 0 | 0 | 62.4862
5663 | 0 | 0 | 62.3843
5664 | 0 | 0 | 62.2826
5665 | 0 | 0 | 62.1812
5666 | 0 | 0 | 62.08
5667 | 0 | 0 | 61.979
5668 | 0 | 0 | 61.8783
5669 | 0 | 0 | 61.7778
5670 | 9.9087 | 12.6596 | 60.9466
5671 | 1.1051 | 0 | 62.9092
5672 | 1.4369 | 0 | 61.7204
5673 | 0 | 0 | 61.5285
5674 | 0 | 0 | 61.4289
5675 | 0 | 0 | 61.3294
5676 | 0.69788 | 0 | 60.7376
5677 | 0 | 0 | 60.5951
5678 | 0 | 0 | 60.4977
5679 | 0 | 0 | 60.4004
5680 | 0 | 0 | 60.3034
5681 | 0 | 0 | 60.2066
5682 | 5.0002 | 6.903 | 60.3494
5683 | 9.8594 | 12.6734 | 60.766
5684 | 0 | 0 | 63.5354
5685 | 1.0986 | 0 | 62.6547
5686 | 0 | 0 | 62.4821
5687 | 0 | 0 | 62.3802
5688 | 0 | 0 | 62.2786
5689 | 0 | 0 | 62.1771
5690 | 0 | 0 | 62.076
5691 | 0 | 0 | 61.975
5692 | 0 | 0 | 61.8743
5693 | 0 | 0 | 61.7738
5694 | 9.9122 | 12.6629 | 60.9416
5695 | 1.1055 | 0 | 62.9048
5696 | 1.4374 | 0 | 61.7156
5697 | 0 | 0 | 61.5237
5698 | 0 | 0 | 61.424
5699 | 0 | 0 | 61.3246
5700 | 0.69813 | 0 | 60.7326
5701 | 0 | 0 | 60.5901
5702 | 0 | 0 | 60.4927
5703 | 0 | 0 | 60.3955
5704 | 0 | 0 | 60.2985
5705 | 0 | 0 | 60.2017
5706 | 5.0019 | 6.9059 | 60.3448
5707 | 9.863 | 12.6767 | 60.761
5708 | 0 | 0 | 63.5312
5709 | 1.099 | 0 | 62.6502
5710 | 0 | 0 | 62.4776
5711 | 0 | 0 | 62.3757
5712 | 0 | 0 | 62.2741
5713 | 0 | 0 | 62.1727
5714 | 0 | 0 | 62.0715
5715 | 0 | 0 | 61.9705
5716 | 0 | 0 | 61.8698
5717 | 0 | 0 | 61.7694
5718 | 9.9161 | 12.6665 | 60.9362
5719 | 1.1059 | 0 | 62.8999
5720 | 1.438 | 0 | 61.7103
5721 | 0 | 0 | 61.5184
5722 | 0 | 0 | 61.4187
5723 | 0 | 0 | 61.3193
5724 | 0.6984 | 0 | 60.7271
5725 | 0 | 0 | 60.5847
5726 | 0 | 0 | 60.4872
5727 | 0 | 0 | 60.39
5728 | 0 | 0 | 60.293
5729 | 0 | 0 | 60.1962
5730 | 5.0039 | 6.9092 | 60.3397
5731 | 9.8669 | 12.6803 | 60.7556
5732 | 0 | 0 | 63.5265
5733 | 1.0994 | 0 | 62.6452
5734 | 0 | 0 | 62.4727
5735 | 0 | 0 | 62.3708
5736 | 0 | 0 | 62.2692
5737 | 0 | 0 | 62.1678
5738 | 0 | 0 | 62.0666
5739 | 0 | 0 | 61.9657
5740 | 0 | 0 | 61.865
5741 | 0 | 0 | 61.7645
5742 | 9.9203 | 12.6705 | 60.9303
5743 | 1.1063 | 0 | 62.8945
5744 | 1.4386 | 0 | 61.7045
5745 | 0 | 0 | 61.5126
5746 | 0 | 0 | 61.4129
5747 | 0 | 0 | 61.3135
5748 | 0.69869 | 0 | 60.7211
5749 | 0 | 0 | 60.5787
5750 | 0 | 0 | 60.4813
5751 | 0 | 0 | 60.3841
5752 | 0 | 0 | 60.2871
5753 | 0 | 0 | 60.1903
5754 | 5.006 | 6.9115 | 60.3336
5755 | 9.8709 | 12.6845 | 60.7489
5756 | 0 | 0 | 63.5209
5757 | 1.0998 | 0 | 62.6394
5758 | 0 | 0 | 62.4668
5759 | 0 | 0 | 62.3649
5760 | 0 | 0 | 62.2633
5761 | 0 | 0 | 62.1619
5762 | 0 | 0 | 62.0607
5763 | 0 | 0 | 61.9598
5764 | 0 | 0 | 61.8592
5765 | 0 | 0 | 61.7587
5766 | 9.9247 | 12.675 | 60.9234
5767 | 1.1068 | 0 | 62.8884
5768 | 1.4392 | 0 | 61.698
5769 | 0 | 0 | 61.506
5770 | 0 | 0 | 61.4064
5771 | 0 | 0 | 61.307
5772 | 0.699 | 0 | 60.7144
5773 | 0 | 0 | 60.572
5774 | 0 | 0 | 60.4745
5775 | 0 | 0 | 60.3774
5776 | 0 | 0 | 60.2804
5777 | 0 | 0 | 60.1837
5778 | 5.0082 | 6.9121 | 60.326
5779 | 9.8748 | 12.6895 | 60.7404
5780 | 0 | 0 | 63.5139
5781 | 1.1003 | 0 | 62.632
5782 | 0 | 0 | 62.4594
5783 | 0 | 0 | 62.3576
5784 | 0 | 0 | 62.256
5785 | 0 | 0 | 62.1546
5786 | 0 | 0 | 62.0535
5787 | 0 | 0 | 61.9526
5788 | 0 | 0 | 61.8519
5789 | 0 | 0 | 61.7515
5790 | 9.9293 | 12.6802 | 60.9154
5791 | 1.1073 | 0 | 62.8814
5792 | 1.4398 | 0 | 61.6904
5793 | 0 | 0 | 61.4985
5794 | 0 | 0 | 61.3989
5795 | 0 | 0 | 61.2995
5796 | 0.69932 | 0 | 60.7067
5797 | 0 | 0 | 60.5643
5798 | 0 | 0 | 60.4669
5799 | 0 | 0 | 60.3697
5800 | 0 | 0 | 60.2727
5801 | 0 | 0 | 60.176
5802 | 5.0105 | 6.9128 | 60.3173
5803 | 9.8789 | 12.695 | 60.731
5804 | 0 | 0 | 63.5061
5805 | 1.1007 | 0 | 62.6239
5806 | 0 | 0 | 62.4513
5807 | 0 | 0 | 62.3495
5808 | 0 | 0 | 62.2479
5809 | 0 | 0 | 62.1465
5810 | 0 | 0 | 62.0454
5811 | 0 | 0 | 61.9445
5812 | 0 | 0 | 61.8439
5813 | 0 | 0 | 61.7435
5814 | 9.934 | 12.6859 | 60.9066
5815 | 1.1078 | 0 | 62.8737
5816 | 1.4405 | 0 | 61.6823
5817 | 0 | 0 | 61.4903
5818 | 0 | 0 | 61.3907
5819 | 0 | 0 | 61.2914
5820 | 0.69966 | 0 | 60.6983
5821 | 0 | 0 | 60.5559
5822 | 0 | 0 | 60.4585
5823 | 0 | 0 | 60.3614
5824 | 0 | 0 | 60.2644
5825 | 0 | 0 | 60.1677
5826 | 5.013 | 6.9135 | 60.3079
5827 | 9.8833 | 12.7009 | 60.7208
5828 | 0 | 0 | 63.4977
5829 | 1.1012 | 0 | 62.6152
5830 | 0 | 0 | 62.4426
5831 | 0 | 0 | 62.3407
5832 | 0 | 0 | 62.2392
5833 | 0 | 0 | 62.1378
5834 | 0 | 0 | 62.0368
5835 | 0 | 0 | 61.9359
5836 | 0 | 0 | 61.8353
5837 | 0 | 0 | 61.7349
5838 | 9.9391 | 12.6919 | 60.8971
5839 | 1.1084 | 0 | 62.8655
5840 | 1.4413 | 0 | 61.6736
5841 | 0 | 0 | 61.4815
5842 | 0 | 0 | 61.382
5843 | 0 | 0 | 61.2827
5844 | 0.70002 | 0 | 60.6894
5845 | 0 | 0 | 60.5469
5846 | 0 | 0 | 60.4496
5847 | 0 | 0 | 60.3525
5848 | 0 | 0 | 60.2556
5849 | 0 | 0 | 60.1589
5850 | 5.0156 | 6.9143 | 60.2979
5851 | 9.8879 | 12.7072 | 60.71
5852 | 0 | 0 | 63.4887
5853 | 1.1018 | 0 | 62.6059
5854 | 0 | 0 | 62.4332
5855 | 0 | 0 | 62.3315
5856 | 0 | 0 | 62.2299
5857 | 0 | 0 | 62.1286
5858 | 0 | 0 | 62.0275
5859 | 0 | 0 | 61.9267
5860 | 0 | 0 | 61.8261
5861 | 0 | 0 | 61.7257
5862 | 9.9444 | 12.6983 | 60.8871
5863 | 1.109 | 0 | 62.8568
5864 | 1.4421 | 0 | 61.6643
5865 | 0 | 0 | 61.4722
5866 | 0 | 0 | 61.3727
5867 | 0 | 0 | 61.2734
5868 | 0.70041 | 0 | 60.6799
5869 | 0 | 0 | 60.5374
5870 | 0 | 0 | 60.4401
5871 | 0 | 0 | 60.343
5872 | 0 | 0 | 60.2461
5873 | 0 | 0 | 60.1495
5874 | 5.0184 | 6.9151 | 60.2873
5875 | 9.8929 | 12.7139 | 60.6985
5876 | 0 | 0 | 63.4792
5877 | 1.1024 | 0 | 62.596
5878 | 0 | 0 | 62.4234
5879 | 0 | 0 | 62.3216
5880 | 0 | 0 | 62.2201
5881 | 0 | 0 | 62.1188
5882 | 0 | 0 | 62.0177
5883 | 0 | 0 | 61.9169
5884 | 0 | 0 | 61.8164
5885 | 0 | 0 | 61.716
5886 | 9.95 | 12.7051 | 60.8765
5887 | 1.1096 | 0 | 62.8476
5888 | 1.4429 | 0 | 61.6545
5889 | 0 | 0 | 61.4624
5890 | 0 | 0 | 61.3629
5891 | 0 | 0 | 61.2636
5892 | 0.70081 | 0 | 60.6699
5893 | 0 | 0 | 60.5274
5894 | 0 | 0 | 60.4301
5895 | 0 | 0 | 60.333
5896 | 0 | 0 | 60.2361
5897 | 0 | 0 | 60.1395
5898 | 5.0213 | 6.916 | 60.2761
5899 | 9.898 | 12.721 | 60.6863
5900 | 0 | 0 | 63.4692
5901 | 1.103 | 0 | 62.5856
5902 | 0 | 0 | 62.4129
5903 | 0 | 0 | 62.3112
5904 | 0 | 0 | 62.2097
5905 | 0 | 0 | 62.1084
5906 | 0 | 0 | 62.0074
5907 | 0 | 0 | 61.9066
5908 | 0 | 0 | 61.8061
5909 | 0 | 0 | 61.7058
5910 | 9.9559 | 12.7123 | 60.8653
5911 | 1.1103 | 0 | 62.8379
5912 | 1.4437 | 0 | 61.6442
5913 | 0 | 0 | 61.452
5914 | 0 | 0 | 61.3526
5915 | 0 | 0 | 61.2533
5916 | 0.70124 | 0 | 60.6593
5917 | 0 | 0 | 60.5168
5918 | 0 | 0 | 60.4195
5919 | 0 | 0 | 60.3224
5920 | 0 | 0 | 60.2256
5921 | 0 | 0 | 60.129
5922 | 5.0243 | 6.9169 | 60.2642
5923 | 9.9035 | 12.7284 | 60.6735
5924 | 0 | 0 | 63.4587
5925 | 1.1036 | 0 | 62.5746
5926 | 0 | 0 | 62.4019
5927 | 0 | 0 | 62.3002
5928 | 0 | 0 | 62.1987
5929 | 0 | 0 | 62.0975
5930 | 0 | 0 | 61.9965
5931 | 0 | 0 | 61.8958
5932 | 0 | 0 | 61.7952
5933 | 0 | 0 | 61.6949
5934 | 9.9621 | 12.7199 | 60.8535
5935 | 1.111 | 0 | 62.8277
5936 | 1.4446 | 0 | 61.6333
5937 | 0 | 0 | 61.4411
5938 | 0 | 0 | 61.3417
5939 | 0 | 0 | 61.2425
5940 | 0.70168 | 0 | 60.6481
5941 | 0 | 0 | 60.5056
5942 | 0 | 0 | 60.4084
5943 | 0 | 0 | 60.3114
5944 | 0 | 0 | 60.2145
5945 | 0 | 0 | 60.118
5946 | 5.0275 | 6.9179 | 60.2518
5947 | 9.9092 | 12.7362 | 60.66
5948 | 0 | 0 | 63.4476
5949 | 1.1042 | 0 | 62.5631
5950 | 0 | 0 | 62.3904
5951 | 0 | 0 | 62.2887
5952 | 0 | 0 | 62.1873
5953 | 0 | 0 | 62.086
5954 | 0 | 0 | 61.9851
5955 | 0 | 0 | 61.8843
5956 | 0 | 0 | 61.7838
5957 | 0 | 0 | 61.6836
5958 | 9.9685 | 12.7278 | 60.8411
5959 | 1.1117 | 0 | 62.817
5960 | 1.4456 | 0 | 61.6219
5961 | 0 | 0 | 61.4297
5962 | 0 | 0 | 61.3303
5963 | 0 | 0 | 61.2311
5964 | 0.70215 | 0 | 60.6364
5965 | 0 | 0 | 60.494
5966 | 0 | 0 | 60.3967
5967 | 0 | 0 | 60.2997
5968 | 0 | 0 | 60.2029
5969 | 0 | 0 | 60.1064
5970 | 5.0309 | 6.9189 | 60.2387
5971 | 9.9152 | 12.7444 | 60.6459
5972 | 0 | 0 | 63.4359
5973 | 1.1049 | 0 | 62.551
5974 | 0 | 0 | 62.3783
5975 | 0 | 0 | 62.2766
5976 | 0 | 0 | 62.1752
5977 | 0 | 0 | 62.074
5978 | 0 | 0 | 61.9731
5979 | 0 | 0 | 61.8724
5980 | 0 | 0 | 61.7719
5981 | 0 | 0 | 61.6717
5982 | 9.9753 | 12.7361 | 60.8281
5983 | 1.1125 | 0 | 62.8058
5984 | 1.4466 | 0 | 61.61
5985 | 0 | 0 | 61.4177
5986 | 0 | 0 | 61.3183
5987 | 0 | 0 | 61.2192
5988 | 0.70264 | 0 | 60.6242
5989 | 0 | 0 | 60.4817
5990 | 0 | 0 | 60.3845
5991 | 0 | 0 | 60.2876
5992 | 0 | 0 | 60.1908
5993 | 0 | 0 | 60.0943
5994 | 5.0344 | 6.9199 | 60.2251
5995 | 9.9214 | 12.753 | 60.6312
5996 | 0 | 0 | 63.4238
5997 | 1.1057 | 0 | 62.5384
5998 | 0 | 0 | 62.3656
5999 | 0 | 0 | 62.264
6000 | 0 | 0 | 62.1626
6001 | 0 | 0 | 62.0615
6002 | 0 | 0 | 61.9606
6003 | 0 | 0 | 61.8599
6004 | 0 | 0 | 61.7595
6005 | 0 | 0 | 61.6592
6006 | 9.9823 | 12.7447 | 60.8146
6007 | 1.1133 | 0 | 62.7941
6008 | 1.4476 | 0 | 61.5975
6009 | 0 | 0 | 61.4053
6010 | 0 | 0 | 61.3059
6011 | 0 | 0 | 61.2067
6012 | 0.70315 | 0 | 60.6115
6013 | 0 | 0 | 60.469
6014 | 0 | 0 | 60.3718
6015 | 0 | 0 | 60.2749
6016 | 0 | 0 | 60.1781
6017 | 0 | 0 | 60.0816
6018 | 5.0381 | 6.921 | 60.2109
6019 | 9.9279 | 12.7619 | 60.6158
6020 | 0 | 0 | 63.4111
6021 | 1.1064 | 0 | 62.5252
6022 | 0 | 0 | 62.3525
6023 | 0 | 0 | 62.2509
6024 | 0 | 0 | 62.1495
6025 | 0 | 0 | 62.0484
6026 | 0 | 0 | 61.9475
6027 | 0 | 0 | 61.8469
6028 | 0 | 0 | 61.7464
6029 | 0 | 0 | 61.6463
6030 | 9.9896 | 12.7537 | 60.8005
6031 | 1.1141 | 0 | 62.7819
6032 | 1.4487 | 0 | 61.5845
6033 | 0 | 0 | 61.3922
6034 | 0 | 0 | 61.2929
6035 | 0 | 0 | 61.1938
6036 | 0.70368 | 0 | 60.5982
6037 | 0 | 0 | 60.4557
6038 | 0 | 0 | 60.3586
6039 | 0 | 0 | 60.2616
6040 | 0 | 0 | 60.1649
6041 | 0 | 0 | 60.0685
6042 | 5.0419 | 6.9222 | 60.196
6043 | 9.9347 | 12.7712 | 60.5998
6044 | 0 | 0 | 63.3979
6045 | 1.1072 | 0 | 62.5115
6046 | 0 | 0 | 62.3387
6047 | 0 | 0 | 62.2372
6048 | 0 | 0 | 62.1358
6049 | 0 | 0 | 62.0348
6050 | 0 | 0 | 61.9339
6051 | 0 | 0 | 61.8333
6052 | 0 | 0 | 61.7329
6053 | 0 | 0 | 61.6328
6054 | 9.9972 | 12.7631 | 60.7858
6055 | 1.115 | 0 | 62.7692
6056 | 1.4498 | 0 | 61.5711
6057 | 0 | 0 | 61.3787
6058 | 0 | 0 | 61.2794
6059 | 0 | 0 | 61.1803
6060 | 0.70422 | 0 | 60.5844
6061 | 0 | 0 | 60.4419
6062 | 0 | 0 | 60.3448
6063 | 0 | 0 | 60.2479
6064 | 0 | 0 | 60.1512
6065 | 0 | 0 | 60.0548
6066 | 5.0458 | 6.9233 | 60.1806
6067 | 9.9417 | 12.7808 | 60.5832
6068 | 0 | 0 | 63.3842
6069 | 1.108 | 0 | 62.4973
6070 | 0 | 0 | 62.3245
6071 | 0 | 0 | 62.2229
6072 | 0 | 0 | 62.1217
6073 | 0 | 0 | 62.0206
6074 | 0 | 0 | 61.9198
6075 | 0 | 0 | 61.8192
6076 | 0 | 0 | 61.7189
6077 | 0 | 0 | 61.6187
6078 | 10.005 | 12.7728 | 60.7706
6079 | 1.1158 | 0 | 62.7561
6080 | 1.451 | 0 | 61.5571
6081 | 0 | 0 | 61.3647
6082 | 0 | 0 | 61.2654
6083 | 0 | 0 | 61.1664
6084 | 0.70479 | 0 | 60.57
6085 | 0 | 0 | 60.4276
6086 | 0 | 0 | 60.3305
6087 | 0 | 0 | 60.2336
6088 | 0 | 0 | 60.137
6089 | 0 | 0 | 60.0406
6090 | 5.0499 | 6.9246 | 60.1647
6091 | 9.949 | 12.7908 | 60.5659
6092 | 0 | 0 | 63.37
6093 | 1.1089 | 0 | 62.4825
6094 | 0 | 0 | 62.3097
6095 | 0 | 0 | 62.2082
6096 | 0 | 0 | 62.1069
6097 | 0 | 0 | 62.0059
6098 | 0 | 0 | 61.9051
6099 | 0 | 0 | 61.8046
6100 | 0 | 0 | 61.7043
6101 | 0 | 0 | 61.6042
6102 | 10.0131 | 12.7829 | 60.7548
6103 | 1.1168 | 0 | 62.7424
6104 | 1.4522 | 0 | 61.5426
6105 | 0 | 0 | 61.3502
6106 | 0 | 0 | 61.2509
6107 | 0 | 0 | 61.1519
6108 | 0.70538 | 0 | 60.5552
6109 | 0 | 0 | 60.4127
6110 | 0 | 0 | 60.3157
6111 | 0 | 0 | 60.2188
6112 | 0 | 0 | 60.1223
6113 | 0 | 0 | 60.0259
6114 | 5.0541 | 6.9258 | 60.1481
6115 | 9.9565 | 12.8012 | 60.5481
6116 | 0 | 0 | 63.3553
6117 | 1.1097 | 0 | 62.4672
6118 | 0 | 0 | 62.2944
6119 | 0 | 0 | 62.1929
6120 | 0 | 0 | 62.0917
6121 | 0 | 0 | 61.9907
6122 | 0 | 0 | 61.89
6123 | 0 | 0 | 61.7894
6124 | 0 | 0 | 61.6892
6125 | 0 | 0 | 61.5891
6126 | 10.0215 | 12.7933 | 60.7385
6127 | 1.1177 | 0 | 62.7283
6128 | 1.4534 | 0 | 61.5276
6129 | 0 | 0 | 61.3351
6130 | 0 | 0 | 61.2359
6131 | 0 | 0 | 61.1369
6132 | 0.70599 | 0 | 60.5398
6133 | 0 | 0 | 60.3973
6134 | 0 | 0 | 60.3003
6135 | 0 | 0 | 60.2035
6136 | 0 | 0 | 60.107
6137 | 0 | 0 | 60.0107
6138 | 5.0585 | 6.9272 | 60.131
6139 | 9.9643 | 12.8119 | 60.5296
6140 | 0 | 0 | 63.3401
6141 | 1.1106 | 0 | 62.4514
6142 | 0 | 0 | 62.2785
6143 | 0 | 0 | 62.1771
6144 | 0 | 0 | 62.0759
6145 | 0 | 0 | 61.975
6146 | 0 | 0 | 61.8743
6147 | 0 | 0 | 61.7738
6148 | 0 | 0 | 61.6736
6149 | 0 | 0 | 61.5736
6150 | 10.0301 | 12.8041 | 60.7216
6151 | 1.1187 | 0 | 62.7137
6152 | 1.4547 | 0 | 61.5121
6153 | 0 | 0 | 61.3196
6154 | 0 | 0 | 61.2204
6155 | 0 | 0 | 61.1215
6156 | 0.70661 | 0 | 60.524
6157 | 0 | 0 | 60.3815
6158 | 0 | 0 | 60.2845
6159 | 0 | 0 | 60.1878
6160 | 0 | 0 | 60.0912
6161 | 0 | 0 | 59.9949
6162 | 5.063 | 6.9285 | 60.1133
6163 | 9.9723 | 12.823 | 60.5105
6164 | 0 | 0 | 63.3244
6165 | 1.1116 | 0 | 62.435
6166 | 0 | 0 | 62.2622
6167 | 0 | 0 | 62.1608
6168 | 0 | 0 | 62.0596
6169 | 0 | 0 | 61.9587
6170 | 0 | 0 | 61.8581
6171 | 0 | 0 | 61.7576
6172 | 0 | 0 | 61.6574
6173 | 0 | 0 | 61.5575
6174 | 10.039 | 12.8152 | 60.7042
6175 | 1.1197 | 0 | 62.6987
6176 | 1.456 | 0 | 61.4961
6177 | 0 | 0 | 61.3035
6178 | 0 | 0 | 61.2044
6179 | 0 | 0 | 61.1055
6180 | 0.70726 | 0 | 60.5076
6181 | 0 | 0 | 60.3651
6182 | 0 | 0 | 60.2682
6183 | 0 | 0 | 60.1714
6184 | 0 | 0 | 60.075
6185 | 0 | 0 | 59.9787
6186 | 5.0676 | 6.9299 | 60.095
6187 | 9.9806 | 12.8344 | 60.4908
6188 | 0 | 0 | 63.3081
6189 | 1.1125 | 0 | 62.4182
6190 | 0 | 0 | 62.2453
6191 | 0 | 0 | 62.144
6192 | 0 | 0 | 62.0429
6193 | 0 | 0 | 61.942
6194 | 0 | 0 | 61.8414
6195 | 0 | 0 | 61.741
6196 | 0 | 0 | 61.6408
6197 | 0 | 0 | 61.5409
6198 | 10.0481 | 12.8266 | 60.6863
6199 | 1.1207 | 0 | 62.6832
6200 | 1.4573 | 0 | 61.4796
6201 | 0 | 0 | 61.287
6202 | 0 | 0 | 61.1879
6203 | 0 | 0 | 61.0891
6204 | 0.70793 | 0 | 60.4907
6205 | 0 | 0 | 60.3482
6206 | 0 | 0 | 60.2513
6207 | 0 | 0 | 60.1547
6208 | 0 | 0 | 60.0582
6209 | 0 | 0 | 59.962
6210 | 5.0724 | 6.9314 | 60.0762
6211 | 9.9891 | 12.8462 | 60.4706
6212 | 0 | 0 | 63.2914
6213 | 1.1135 | 0 | 62.4008
6214 | 0 | 0 | 62.2279
6215 | 0 | 0 | 62.1266
6216 | 0 | 0 | 62.0256
6217 | 0 | 0 | 61.9247
6218 | 0 | 0 | 61.8241
6219 | 0 | 0 | 61.7238
6220 | 0 | 0 | 61.6237
6221 | 0 | 0 | 61.5238
6222 | 10.0575 | 12.8384 | 60.6678
6223 | 1.1218 | 0 | 62.6673
6224 | 1.4587 | 0 | 61.4626
6225 | 0 | 0 | 61.27
6226 | 0 | 0 | 61.171
6227 | 0 | 0 | 61.0721
6228 | 0.70861 | 0 | 60.4733
6229 | 0 | 0 | 60.3308
6230 | 0 | 0 | 60.234
6231 | 0 | 0 | 60.1374
6232 | 0 | 0 | 60.041
6233 | 0 | 0 | 59.9448
6234 | 5.0773 | 6.9329 | 60.0569
6235 | 9.9978 | 12.8583 | 60.4497
6236 | 0 | 0 | 63.2743
6237 | 1.1145 | 0 | 62.383
6238 | 0 | 0 | 62.2101
6239 | 0 | 0 | 62.1088
6240 | 0 | 0 | 62.0078
6241 | 0 | 0 | 61.907
6242 | 0 | 0 | 61.8064
6243 | 0 | 0 | 61.7061
6244 | 0 | 0 | 61.606
6245 | 0 | 0 | 61.5062
6246 | 10.0672 | 12.8505 | 60.6488
6247 | 1.1229 | 0 | 62.6508
6248 | 1.4601 | 0 | 61.4452
6249 | 0 | 0 | 61.2525
6250 | 0 | 0 | 61.1535
6251 | 0 | 0 | 61.0547
6252 | 0.70931 | 0 | 60.4555
6253 | 0 | 0 | 60.313
6254 | 0 | 0 | 60.2162
6255 | 0 | 0 | 60.1196
6256 | 0 | 0 | 60.0232
6257 | 0 | 0 | 59.9271
6258 | 5.0824 | 6.9344 | 60.037
6259 | 10.0068 | 12.8707 | 60.4283
6260 | 0 | 0 | 63.2566
6261 | 1.1156 | 0 | 62.3646
6262 | 0 | 0 | 62.1917
6263 | 0 | 0 | 62.0905
6264 | 0 | 0 | 61.9895
6265 | 0 | 0 | 61.8887
6266 | 0 | 0 | 61.7882
6267 | 0 | 0 | 61.688
6268 | 0 | 0 | 61.5879
6269 | 0 | 0 | 61.4881
6270 | 10.0771 | 12.863 | 60.6292
6271 | 1.124 | 0 | 62.634
6272 | 1.4616 | 0 | 61.4273
6273 | 0 | 0 | 61.2346
6274 | 0 | 0 | 61.1356
6275 | 0 | 0 | 61.0368
6276 | 0.71003 | 0 | 60.4371
6277 | 0 | 0 | 60.2946
6278 | 0 | 0 | 60.1979
6279 | 0 | 0 | 60.1013
6280 | 0 | 0 | 60.005
6281 | 0 | 0 | 59.9089
6282 | 5.0875 | 6.936 | 60.0165
6283 | 10.016 | 12.8834 | 60.4062
6284 | 0 | 0 | 63.2385
6285 | 1.1166 | 0 | 62.3458
6286 | 0 | 0 | 62.1728
6287 | 0 | 0 | 62.0716
6288 | 0 | 0 | 61.9707
6289 | 0 | 0 | 61.87
6290 | 0 | 0 | 61.7695
6291 | 0 | 0 | 61.6693
6292 | 0 | 0 | 61.5693
6293 | 0 | 0 | 61.4696
6294 | 10.0873 | 12.8757 | 60.6092
6295 | 1.1252 | 0 | 62.6167
6296 | 1.4631 | 0 | 61.4089
6297 | 0 | 0 | 61.2161
6298 | 0 | 0 | 61.1172
6299 | 0 | 0 | 61.0185
6300 | 0.71077 | 0 | 60.4183
6301 | 0 | 0 | 60.2758
6302 | 0 | 0 | 60.1791
6303 | 0 | 0 | 60.0826
6304 | 0 | 0 | 59.9863
6305 | 0 | 0 | 59.8903
6306 | 5.0928 | 6.9376 | 59.9956
6307 | 10.0255 | 12.8965 | 60.3837
6308 | 0 | 0 | 63.2199
6309 | 1.1177 | 0 | 62.3265
6310 | 0 | 0 | 62.1535
6311 | 0 | 0 | 62.0523
6312 | 0 | 0 | 61.9514
6313 | 0 | 0 | 61.8508
6314 | 0 | 0 | 61.7504
6315 | 0 | 0 | 61.6502
6316 | 0 | 0 | 61.5502
6317 | 0 | 0 | 61.4505
6318 | 10.0977 | 12.8888 | 60.5886
6319 | 1.1263 | 0 | 62.599
6320 | 1.4646 | 0 | 61.3901
6321 | 0 | 0 | 61.1972
6322 | 0 | 0 | 61.0983
6323 | 0 | 0 | 60.9997
6324 | 0.71153 | 0 | 60.399
6325 | 0 | 0 | 60.2565
6326 | 0 | 0 | 60.1598
6327 | 0 | 0 | 60.0634
6328 | 0 | 0 | 59.9672
6329 | 0 | 0 | 59.8712
6330 | 5.0983 | 6.9392 | 59.9741
6331 | 10.0352 | 12.91 | 60.3605
6332 | 0 | 0 | 63.2008
6333 | 1.1189 | 0 | 62.3067
6334 | 0 | 0 | 62.1336
6335 | 0 | 0 | 62.0326
6336 | 0 | 0 | 61.9317
6337 | 0 | 0 | 61.8311
6338 | 0 | 0 | 61.7307
6339 | 0 | 0 | 61.6306
6340 | 0 | 0 | 61.5307
6341 | 0 | 0 | 61.431
6342 | 10.1083 | 12.9023 | 60.5676
6343 | 1.1275 | 0 | 62.5808
6344 | 1.4662 | 0 | 61.3708
6345 | 0 | 0 | 61.1779
6346 | 0 | 0 | 61.079
6347 | 0 | 0 | 60.9804
6348 | 0.7123 | 0 | 60.3793
6349 | 0 | 0 | 60.2368
6350 | 0 | 0 | 60.1401
6351 | 0 | 0 | 60.0437
6352 | 0 | 0 | 59.9475
6353 | 0 | 0 | 59.8516
6354 | 5.1038 | 6.9409 | 59.9521
6355 | 10.0451 | 12.9237 | 60.3368
6356 | 0 | 0 | 63.1813
6357 | 1.12 | 0 | 62.2864
6358 | 0 | 0 | 62.1133
6359 | 0 | 0 | 62.0123
6360 | 0 | 0 | 61.9115
6361 | 0 | 0 | 61.8109
6362 | 0 | 0 | 61.7106
6363 | 0 | 0 | 61.6105
6364 | 0 | 0 | 61.5107
6365 | 0 | 0 | 61.4111
6366 | 10.1192 | 12.916 | 60.546
6367 | 1.1288 | 0 | 62.5622
6368 | 1.4678 | 0 | 61.351
6369 | 0 | 0 | 61.1581
6370 | 0 | 0 | 61.0593
6371 | 0 | 0 | 60.9607
6372 | 0.7131 | 0 | 60.359
6373 | 0 | 0 | 60.2165
6374 | 0 | 0 | 60.1199
6375 | 0 | 0 | 60.0236
6376 | 0 | 0 | 59.9275
6377 | 0 | 0 | 59.8316
6378 | 5.1095 | 6.9426 | 59.9296
6379 | 10.0552 | 12.9377 | 60.3126
6380 | 0 | 0 | 63.1613
6381 | 1.1212 | 0 | 62.2656
6382 | 0 | 0 | 62.0926
6383 | 0 | 0 | 61.9916
6384 | 0 | 0 | 61.8908
6385 | 0 | 0 | 61.7903
6386 | 0 | 0 | 61.69
6387 | 0 | 0 | 61.59
6388 | 0 | 0 | 61.4902
6389 | 0 | 0 | 61.3906
6390 | 10.1303 | 12.93 | 60.524
6391 | 1.13 | 0 | 62.5432
6392 | 1.4695 | 0 | 61.3308
6393 | 0 | 0 | 61.1378
6394 | 0 | 0 | 61.0391
6395 | 0 | 0 | 60.9406
6396 | 0.7139 | 0 | 60.3384
6397 | 0 | 0 | 60.1958
6398 | 0 | 0 | 60.0993
6399 | 0 | 0 | 60.003
6400 | 0 | 0 | 59.9069
6401 | 0 | 0 | 59.8111
6402 | 5.1154 | 6.9444 | 59.9066
6403 | 10.0656 | 12.9521 | 60.2878
6404 | 0 | 0 | 63.1409
6405 | 1.1224 | 0 | 62.2444
6406 | 0 | 0 | 62.0713
6407 | 0 | 0 | 61.9704
6408 | 0 | 0 | 61.8697
6409 | 0 | 0 | 61.7692
6410 | 0 | 0 | 61.669
6411 | 0 | 0 | 61.569
6412 | 0 | 0 | 61.4693
6413 | 0 | 0 | 61.3697
6414 | 10.1417 | 12.9444 | 60.5014
6415 | 1.1313 | 0 | 62.5238
6416 | 1.4711 | 0 | 61.3102
6417 | 0 | 0 | 61.1171
6418 | 0 | 0 | 61.0184
6419 | 0 | 0 | 60.92
6420 | 0.71473 | 0 | 60.3172
6421 | 0 | 0 | 60.1747
6422 | 0 | 0 | 60.0782
6423 | 0 | 0 | 59.982
6424 | 0 | 0 | 59.8859
6425 | 0 | 0 | 59.7901
6426 | 5.1213 | 6.9462 | 59.883
6427 | 10.0761 | 12.9668 | 60.2625
6428 | 0 | 0 | 63.1201
6429 | 1.1236 | 0 | 62.2228
6430 | 0 | 0 | 62.0496
6431 | 0 | 0 | 61.9487
6432 | 0 | 0 | 61.8481
6433 | 0 | 0 | 61.7477
6434 | 0 | 0 | 61.6475
6435 | 0 | 0 | 61.5476
6436 | 0 | 0 | 61.4479
6437 | 0 | 0 | 61.3484
6438 | 10.1532 | 12.959 | 60.4784
6439 | 1.1326 | 0 | 62.504
6440 | 1.4729 | 0 | 61.2891
6441 | 0 | 0 | 61.096
6442 | 0 | 0 | 60.9974
6443 | 0 | 0 | 60.8989
6444 | 0.71557 | 0 | 60.2957
6445 | 0 | 0 | 60.1531
6446 | 0 | 0 | 60.0567
6447 | 0 | 0 | 59.9605
6448 | 0 | 0 | 59.8645
6449 | 0 | 0 | 59.7688
6450 | 5.1273 | 6.9481 | 59.859
6451 | 10.0869 | 12.9818 | 60.2366
6452 | 0 | 0 | 63.0988
6453 | 1.1249 | 0 | 62.2006
6454 | 0 | 0 | 62.0275
6455 | 0 | 0 | 61.9267
6456 | 0 | 0 | 61.8261
6457 | 0 | 0 | 61.7257
6458 | 0 | 0 | 61.6256
6459 | 0 | 0 | 61.5257
6460 | 0 | 0 | 61.426
6461 | 0 | 0 | 61.3266
6462 | 10.165 | 12.9739 | 60.455
6463 | 1.134 | 0 | 62.4837
6464 | 1.4746 | 0 | 61.2676
6465 | 0 | 0 | 61.0744
6466 | 0 | 0 | 60.9759
6467 | 0 | 0 | 60.8775
6468 | 0.71643 | 0 | 60.2737
6469 | 0 | 0 | 60.1311
6470 | 0 | 0 | 60.0348
6471 | 0 | 0 | 59.9386
6472 | 0 | 0 | 59.8427
6473 | 0 | 0 | 59.747
6474 | 5.1335 | 6.9499 | 59.8346
6475 | 10.0979 | 12.997 | 60.2103
6476 | 0 | 0 | 63.0771
6477 | 1.1262 | 0 | 62.1781
6478 | 0 | 0 | 62.0049
6479 | 0 | 0 | 61.9041
6480 | 0 | 0 | 61.8036
6481 | 0 | 0 | 61.7033
6482 | 0 | 0 | 61.6032
6483 | 0 | 0 | 61.5034
6484 | 0 | 0 | 61.4038
6485 | 0 | 0 | 61.3044
6486 | 10.1771 | 12.9892 | 60.431
6487 | 1.1353 | 0 | 62.4631
6488 | 1.4764 | 0 | 61.2457
6489 | 0 | 0 | 61.0525
6490 | 0 | 0 | 60.9539
6491 | 0 | 0 | 60.8556
6492 | 0.71731 | 0 | 60.2512
6493 | 0 | 0 | 60.1087
6494 | 0 | 0 | 60.0124
6495 | 0 | 0 | 59.9163
6496 | 0 | 0 | 59.8204
6497 | 0 | 0 | 59.7247
6498 | 5.1398 | 6.9519 | 59.8096
6499 | 10.1091 | 13.0126 | 60.1834
6500 | 0 | 0 | 63.0549
6501 | 1.1275 | 0 | 62.1551
6502 | 0 | 0 | 61.9819
6503 | 0 | 0 | 61.8812
6504 | 0 | 0 | 61.7807
6505 | 0 | 0 | 61.6804
6506 | 0 | 0 | 61.5804
6507 | 0 | 0 | 61.4806
6508 | 0 | 0 | 61.3811
6509 | 0 | 0 | 61.2818
6510 | 10.1893 | 13.0047 | 60.4066
6511 | 1.1367 | 0 | 62.4421
6512 | 1.4782 | 0 | 61.2234
6513 | 0 | 0 | 61.0301
6514 | 0 | 0 | 60.9316
6515 | 0 | 0 | 60.8333
6516 | 0.7182 | 0 | 60.2284
6517 | 0 | 0 | 60.0858
6518 | 0 | 0 | 59.9896
6519 | 0 | 0 | 59.8935
6520 | 0 | 0 | 59.7977
6521 | 0 | 0 | 59.7021
6522 | 5.1462 | 6.9538 | 59.7841
6523 | 10.1206 | 13.0285 | 60.156
6524 | 0 | 0 | 63.0324
6525 | 1.1288 | 0 | 62.1317
6526 | 0 | 0 | 61.9584
6527 | 0 | 0 | 61.8578
6528 | 0 | 0 | 61.7573
6529 | 0 | 0 | 61.6571
6530 | 0 | 0 | 61.5572
6531 | 0 | 0 | 61.4575
6532 | 0 | 0 | 61.358
6533 | 0 | 0 | 61.2587
6534 | 10.2017 | 13.0205 | 60.3818
6535 | 1.1381 | 0 | 62.4207
6536 | 1.48 | 0 | 61.2007
6537 | 0 | 0 | 61.0073
6538 | 0 | 0 | 60.9088
6539 | 0 | 0 | 60.8106
6540 | 0.71911 | 0 | 60.2051
6541 | 0 | 0 | 60.0626
6542 | 0 | 0 | 59.9663
6543 | 0 | 0 | 59.8703
6544 | 0 | 0 | 59.7746
6545 | 0 | 0 | 59.679
6546 | 5.1527 | 6.9558 | 59.7582
6547 | 10.1322 | 13.0446 | 60.1282
6548 | 0 | 0 | 63.0095
6549 | 1.1301 | 0 | 62.1078
6550 | 0 | 0 | 61.9346
6551 | 0 | 0 | 61.834
6552 | 0 | 0 | 61.7336
6553 | 0 | 0 | 61.6334
6554 | 0 | 0 | 61.5335
6555 | 0 | 0 | 61.4339
6556 | 0 | 0 | 61.3344
6557 | 0 | 0 | 61.2352
6558 | 10.2144 | 13.0366 | 60.3565
6559 | 1.1396 | 0 | 62.3989
6560 | 1.4819 | 0 | 61.1775
6561 | 0 | 0 | 60.9841
6562 | 0 | 0 | 60.8857
6563 | 0 | 0 | 60.7875
6564 | 0.72003 | 0 | 60.1814
6565 | 0 | 0 | 60.0389
6566 | 0 | 0 | 59.9427
6567 | 0 | 0 | 59.8468
6568 | 0 | 0 | 59.7511
6569 | 0 | 0 | 59.6556
6570 | 5.1594 | 6.9578 | 59.7319
6571 | 10.144 | 13.061 | 60.0998
6572 | 0 | 0 | 62.9861
6573 | 1.1315 | 0 | 62.0836
6574 | 0 | 0 | 61.9103
6575 | 0 | 0 | 61.8097
6576 | 0 | 0 | 61.7094
6577 | 0 | 0 | 61.6093
6578 | 0 | 0 | 61.5095
6579 | 0 | 0 | 61.4099
6580 | 0 | 0 | 61.3105
6581 | 0 | 0 | 61.2113
6582 | 10.2273 | 13.053 | 60.3308
6583 | 1.141 | 0 | 62.3768
6584 | 1.4838 | 0 | 61.154
6585 | 0 | 0 | 60.9605
6586 | 0 | 0 | 60.8622
6587 | 0 | 0 | 60.7641
6588 | 0.72097 | 0 | 60.1573
6589 | 0 | 0 | 60.0148
6590 | 0 | 0 | 59.9187
6591 | 0 | 0 | 59.8228
6592 | 0 | 0 | 59.7271
6593 | 0 | 0 | 59.6317
6594 | 5.1661 | 6.9599 | 59.7051
6595 | 10.156 | 13.0777 | 60.071
6596 | 0 | 0 | 62.9624
6597 | 1.1329 | 0 | 62.0589
6598 | 0 | 0 | 61.8856
6599 | 0 | 0 | 61.7851
6600 | 0 | 0 | 61.6848
6601 | 0 | 0 | 61.5848
6602 | 0 | 0 | 61.485
6603 | 0 | 0 | 61.3855
6604 | 0 | 0 | 61.2861
6605 | 0 | 0 | 61.187
6606 | 10.2403 | 13.0696 | 60.3047
6607 | 1.1425 | 0 | 62.3542
6608 | 1.4858 | 0 | 61.1301
6609 | 0 | 0 | 60.9365
6610 | 0 | 0 | 60.8382
6611 | 0 | 0 | 60.7402
6612 | 0.72192 | 0 | 60.1328
6613 | 0 | 0 | 59.9903
6614 | 0 | 0 | 59.8943
6615 | 0 | 0 | 59.7984
6616 | 0 | 0 | 59.7028
6617 | 0 | 0 | 59.6074
6618 | 5.173 | 6.962 | 59.6779
6619 | 10.1682 | 13.0947 | 60.0417
6620 | 0 | 0 | 62.9382
6621 | 1.1343 | 0 | 62.0339
6622 | 0 | 0 | 61.8605
6623 | 0 | 0 | 61.7601
6624 | 0 | 0 | 61.6599
6625 | 0 | 0 | 61.5599
6626 | 0 | 0 | 61.4602
6627 | 0 | 0 | 61.3607
6628 | 0 | 0 | 61.2614
6629 | 0 | 0 | 61.1624
6630 | 10.2536 | 13.0865 | 60.2781
6631 | 1.144 | 0 | 62.3314
6632 | 1.4877 | 0 | 61.1058
6633 | 0 | 0 | 60.9121
6634 | 0 | 0 | 60.8139
6635 | 0 | 0 | 60.7159
6636 | 0.72289 | 0 | 60.108
6637 | 0 | 0 | 59.9654
6638 | 0 | 0 | 59.8694
6639 | 0 | 0 | 59.7737
6640 | 0 | 0 | 59.6781
6641 | 0 | 0 | 59.5828
6642 | 5.1799 | 6.9641 | 59.6502
6643 | 10.1806 | 13.1119 | 60.0119
6644 | 0 | 0 | 62.9137
6645 | 1.1358 | 0 | 62.0084
6646 | 0 | 0 | 61.835
6647 | 0 | 0 | 61.7346
6648 | 0 | 0 | 61.6345
6649 | 0 | 0 | 61.5346
6650 | 0 | 0 | 61.4349
6651 | 0 | 0 | 61.3355
6652 | 0 | 0 | 61.2363
6653 | 0 | 0 | 61.1373
6654 | 10.2671 | 13.1036 | 60.2511
6655 | 1.1455 | 0 | 62.3081
6656 | 1.4897 | 0 | 61.0811
6657 | 0 | 0 | 60.8874
6658 | 0 | 0 | 60.7892
6659 | 0 | 0 | 60.6913
6660 | 0.72387 | 0 | 60.0827
6661 | 0 | 0 | 59.9402
6662 | 0 | 0 | 59.8442
6663 | 0 | 0 | 59.7485
6664 | 0 | 0 | 59.653
6665 | 0 | 0 | 59.5578
6666 | 5.187 | 6.9662 | 59.6221
6667 | 10.1932 | 13.1294 | 59.9817
6668 | 0 | 0 | 62.8889
6669 | 1.1372 | 0 | 61.9826
6670 | 0 | 0 | 61.8091
6671 | 0 | 0 | 61.7088
6672 | 0 | 0 | 61.6087
6673 | 0 | 0 | 61.5089
6674 | 0 | 0 | 61.4093
6675 | 0 | 0 | 61.3099
6676 | 0 | 0 | 61.2107
6677 | 0 | 0 | 61.1118
6678 | 10.2807 | 13.121 | 60.2238
6679 | 1.1471 | 0 | 62.2846
6680 | 1.4917 | 0 | 61.0561
6681 | 0 | 0 | 60.8623
6682 | 0 | 0 | 60.7642
6683 | 0 | 0 | 60.6663
6684 | 0.72487 | 0 | 60.0571
6685 | 0 | 0 | 59.9145
6686 | 0 | 0 | 59.8187
6687 | 0 | 0 | 59.723
6688 | 0 | 0 | 59.6276
6689 | 0 | 0 | 59.5324
6690 | 5.1941 | 6.9684 | 59.5936
6691 | 10.2059 | 13.1472 | 59.9511
6692 | 0 | 0 | 62.8636
6693 | 1.1387 | 0 | 61.9564
6694 | 0 | 0 | 61.7829
6695 | 0 | 0 | 61.6826
6696 | 0 | 0 | 61.5826
6697 | 0 | 0 | 61.4828
6698 | 0 | 0 | 61.3833
6699 | 0 | 0 | 61.284
6700 | 0 | 0 | 61.1849
6701 | 0 | 0 | 61.086
6702 | 10.2946 | 13.1387 | 60.196
6703 | 1.1487 | 0 | 62.2606
6704 | 1.4938 | 0 | 61.0307
6705 | 0 | 0 | 60.8368
6706 | 0 | 0 | 60.7388
6707 | 0 | 0 | 60.641
6708 | 0.72588 | 0 | 60.0311
6709 | 0 | 0 | 59.8886
6710 | 0 | 0 | 59.7927
6711 | 0 | 0 | 59.6971
6712 | 0 | 0 | 59.6018
6713 | 0 | 0 | 59.5066
6714 | 5.2014 | 6.9706 | 59.5647
6715 | 10.6173 | 13.2316 | 60.5597
6716 | 0 | 0 | 62.5804
6717 | 1.1338 | 0 | 61.6774
6718 | 0 | 0 | 61.5049
6719 | 0 | 0 | 61.4053
6720 | 0 | 0 | 61.3059
6721 | 0 | 0 | 61.2068
6722 | 0 | 0 | 61.1079
6723 | 0 | 0 | 61.0092
6724 | 0 | 0 | 60.9108
6725 | 0 | 0 | 60.8126
6726 | 10.2523 | 13.2476 | 59.9846
6727 | 1.1469 | 0 | 62.1057
6728 | 1.4915 | 0 | 60.8779
6729 | 0 | 0 | 60.6846
6730 | 0 | 0 | 60.5869
6731 | 0 | 0 | 60.4894
6732 | 0.7248 | 0 | 59.8807
6733 | 0 | 0 | 59.7386
6734 | 0 | 0 | 59.6431
6735 | 0 | 0 | 59.5479
6736 | 0 | 0 | 59.4529
6737 | 0 | 0 | 59.3581
6738 | 5.4013 | 6.7463 | 60.0752
6739 | 10.5435 | 13.5257 | 60.2661
6740 | 0 | 0 | 62.3881
6741 | 1.1311 | 0 | 61.4874
6742 | 0 | 0 | 61.3155
6743 | 0 | 0 | 61.2164
6744 | 0 | 0 | 61.1175
6745 | 0 | 0 | 61.0188
6746 | 0 | 0 | 60.9203
6747 | 0 | 0 | 60.8221
6748 | 0 | 0 | 60.7241
6749 | 0 | 0 | 60.6263
6750 | 10.6368 | 13.3957 | 60.4921
6751 | 1.1399 | 0 | 61.7411
6752 | 1.4824 | 0 | 60.5212
6753 | 0 | 0 | 60.3293
6754 | 0 | 0 | 60.2325
6755 | 0 | 0 | 60.1358
6756 | 0.72036 | 0 | 59.5311
6757 | 0 | 0 | 59.3901
6758 | 0 | 0 | 59.2955
6759 | 0 | 0 | 59.201
6760 | 0 | 0 | 59.1068
6761 | 0 | 0 | 59.0129
6762 | 5.3748 | 6.8359 | 59.7986
6763 | 10.7048 | 13.0492 | 60.5638
6764 | 0 | 0 | 61.6474
6765 | 1.1148 | 0 | 60.7603
6766 | 0 | 0 | 60.5912
6767 | 0 | 0 | 60.4937
6768 | 0 | 0 | 60.3965
6769 | 0 | 0 | 60.2995
6770 | 0 | 0 | 60.2027
6771 | 0 | 0 | 60.1062
6772 | 0 | 0 | 60.0098
6773 | 0 | 0 | 59.9137
6774 | 10.7056 | 13.1668 | 60.5029
6775 | 1.1187 | 0 | 60.8215
6776 | 1.4548 | 0 | 59.625
6777 | 0 | 0 | 59.4369
6778 | 0 | 0 | 59.3422
6779 | 0 | 0 | 59.2477
6780 | 0.70704 | 0 | 58.6546
6781 | 0 | 0 | 58.5165
6782 | 0 | 0 | 58.4239
6783 | 0 | 0 | 58.3315
6784 | 0 | 0 | 58.2394
6785 | 0 | 0 | 58.1474
6786 | 5.2878 | 6.9617 | 59.0592
6787 | 10.5735 | 13.3073 | 60.0595
6788 | 0 | 0 | 61.2491
6789 | 1.1071 | 0 | 60.3685
6790 | 0 | 0 | 60.2008
6791 | 0 | 0 | 60.1043
6792 | 0 | 0 | 60.0079
6793 | 0 | 0 | 59.9118
6794 | 0 | 0 | 59.816
6795 | 0 | 0 | 59.7203
6796 | 0 | 0 | 59.6249
6797 | 0 | 0 | 59.5297
6798 | 10.645 | 13.3253 | 60.2303
6799 | 1.1156 | 0 | 60.6096
6800 | 1.4508 | 0 | 59.4167
6801 | 0 | 0 | 59.2294
6802 | 0 | 0 | 59.1352
6803 | 0 | 0 | 59.0411
6804 | 0.7051 | 0 | 58.45
6805 | 0 | 0 | 58.3125
6806 | 0 | 0 | 58.2204
6807 | 0 | 0 | 58.1285
6808 | 0 | 0 | 58.0368
6809 | 0 | 6.3674 | 62.4651
6810 | 5.5266 | 0 | 59.5293
6811 | 10.4239 | 13.6417 | 59.4757
6812 | 0 | 0 | 60.7659
6813 | 1.0973 | 0 | 59.8935
6814 | 0 | 0 | 59.7276
6815 | 0 | 0 | 59.6322
6816 | 0 | 0 | 59.5369
6817 | 0 | 0 | 59.442
6818 | 0 | 0 | 59.3472
6819 | 0 | 0 | 59.2526
6820 | 0 | 0 | 59.1583
6821 | 0 | 0 | 59.0642
6822 | 10.566 | 13.5062 | 59.8958
6823 | 1.1112 | 0 | 60.3486
6824 | 1.4452 | 0 | 59.1607
6825 | 0 | 0 | 58.9744
6826 | 0 | 0 | 58.8808
6827 | 0 | 0 | 58.7873
6828 | 0.70239 | 0 | 58.1987
6829 | 0 | 0 | 58.062
6830 | 0 | 6.37 | 60.8605
6831 | 0 | 0 | 62.7701
6832 | 0 | 0 | 62.6676
6833 | 0 | 0 | 62.5652
6834 | 5.5044 | 0 | 59.2665
6835 | 10.3885 | 13.6696 | 59.255
6836 | 0 | 0 | 60.557
6837 | 1.0944 | 0 | 59.6872
6838 | 0 | 0 | 59.522
6839 | 0 | 0 | 59.427
6840 | 0 | 0 | 59.3323
6841 | 0 | 0 | 59.2378
6842 | 0 | 0 | 59.1435
6843 | 0 | 0 | 59.0494
6844 | 0 | 0 | 58.9556
6845 | 0 | 0 | 58.862
6846 | 10.5413 | 13.5202 | 59.7145
6847 | 1.1092 | 0 | 60.1783
6848 | 1.4426 | 0 | 58.9929
6849 | 0 | 0 | 58.8071
6850 | 0 | 0 | 58.7139
6851 | 0 | 0 | 58.6208
6852 | 0.70116 | 6.3633 | 60.1051
6853 | 0 | 0 | 62.7851
6854 | 0 | 0 | 62.6824
6855 | 0 | 0 | 62.5801
6856 | 0 | 0 | 62.4779
6857 | 0 | 0 | 62.3761
6858 | 5.4927 | 0 | 59.0847
6859 | 10.7443 | 13.7213 | 59.7069
6860 | 0 | 0 | 60.1427
6861 | 1.0863 | 0 | 59.2796
6862 | 0 | 0 | 59.1159
6863 | 0 | 0 | 59.0219
6864 | 0 | 0 | 58.9281
6865 | 0 | 0 | 58.8345
6866 | 0 | 0 | 58.7412
6867 | 0 | 0 | 58.6481
6868 | 0 | 0 | 58.5552
6869 | 0 | 0 | 58.4625
6870 | 10.4709 | 13.5124 | 59.3529
6871 | 1.1028 | 0 | 59.8331
6872 | 1.4343 | 0 | 58.6549
6873 | 0 | 0 | 58.4705
6874 | 0 | 0 | 58.378
6875 | 0 | 0 | 58.2857
6876 | 0.69713 | 6.492 | 61.4786
6877 | 0 | 0 | 62.549
6878 | 0 | 0 | 62.447
6879 | 0 | 0 | 62.3451
6880 | 0 | 0 | 62.2436
6881 | 0 | 0 | 62.1422
6882 | 5.4759 | 6.4486 | 60.9607
6883 | 10.8221 | 12.456 | 61.3387
6884 | 0 | 0 | 63.8372
6885 | 1.181 | 0 | 62.8975
6886 | 0 | 0 | 62.7191
6887 | 0 | 0 | 62.6166
6888 | 0 | 0 | 62.5144
6889 | 0 | 0 | 62.4124
6890 | 0 | 0 | 62.3107
6891 | 0 | 0 | 62.2092
6892 | 0 | 0 | 62.1079
6893 | 0 | 0 | 62.0069
6894 | 10.6705 | 12.8565 | 60.7997
6895 | 1.1771 | 0 | 62.6516
6896 | 1.5308 | 0 | 61.3925
6897 | 0 | 0 | 61.1955
6898 | 0 | 0 | 61.0966
6899 | 0 | 0 | 60.9979
6900 | 0.74396 | 0 | 60.3744
6901 | 0 | 0 | 60.2298
6902 | 0 | 0 | 60.1332
6903 | 0 | 0 | 60.0368
6904 | 0 | 0 | 59.9407
6905 | 0 | 0 | 59.8447
6906 | 5.329 | 6.9659 | 59.8256
6907 | 10.4396 | 13.1523 | 60.0243
6908 | 0 | 0 | 62.893
6909 | 1.1597 | 0 | 61.9708
6910 | 0 | 0 | 61.796
6911 | 0 | 0 | 61.6957
6912 | 0 | 0 | 61.5956
6913 | 0 | 0 | 61.4958
6914 | 0 | 0 | 61.3962
6915 | 0 | 0 | 61.2969
6916 | 0 | 0 | 61.1978
6917 | 0 | 0 | 61.0989
6918 | 10.486 | 13.2092 | 60.1217
6919 | 1.1672 | 0 | 62.1672
6920 | 1.5179 | 0 | 60.9193
6921 | 0 | 0 | 60.7242
6922 | 0 | 0 | 60.6264
6923 | 0 | 0 | 60.5289
6924 | 0.73772 | 0 | 59.9109
6925 | 0 | 0 | 59.7679
6926 | 0 | 0 | 59.6723
6927 | 0 | 0 | 59.577
6928 | 0 | 0 | 59.482
6929 | 0 | 0 | 59.3871
6930 | 5.4931 | 6.7502 | 60.053
6931 | 10.7039 | 13.5736 | 60.1524
6932 | 0 | 0 | 62.2629
6933 | 1.1464 | 0 | 61.3519
6934 | 0 | 0 | 61.1794
6935 | 0 | 0 | 61.0805
6936 | 0 | 0 | 60.9819
6937 | 0 | 0 | 60.8835
6938 | 0 | 0 | 60.7854
6939 | 0 | 0 | 60.6875
6940 | 0 | 0 | 60.5898
6941 | 0 | 0 | 60.4923
6942 | 10.7773 | 13.5121 | 60.3174
6943 | 1.1546 | 0 | 61.5786
6944 | 1.5016 | 0 | 60.3447
6945 | 0 | 0 | 60.152
6946 | 0 | 0 | 60.0556
6947 | 0 | 0 | 59.9594
6948 | 0.72981 | 0 | 59.3484
6949 | 0 | 0 | 59.2073
6950 | 0 | 0 | 59.113
6951 | 0 | 0 | 59.019
6952 | 0 | 0 | 58.9253
6953 | 0 | 0 | 58.8317
6954 | 5.4429 | 6.8513 | 59.5872
6955 | 10.8292 | 13.188 | 60.3346
6956 | 0 | 0 | 61.4379
6957 | 1.1281 | 0 | 60.5419
6958 | 0 | 0 | 60.3725
6959 | 0 | 0 | 60.2755
6960 | 0 | 0 | 60.1788
6961 | 0 | 0 | 60.0823
6962 | 0 | 0 | 59.986
6963 | 0 | 0 | 59.89
6964 | 0 | 0 | 59.7942
6965 | 0 | 0 | 59.6986
6966 | 10.8342 | 13.3112 | 60.2816
6967 | 1.1323 | 0 | 60.6097
6968 | 1.4727 | 0 | 59.4003
6969 | 0 | 0 | 59.2117
6970 | 0 | 0 | 59.1174
6971 | 0 | 0 | 59.0234
6972 | 0.71582 | 0 | 58.4248
6973 | 0 | 0 | 58.2867
6974 | 0 | 0 | 58.1946
6975 | 0 | 0 | 58.1028
6976 | 0 | 6.365 | 59.2673
6977 | 0 | 0 | 62.8108
6978 | 5.6021 | 0 | 59.4543
6979 | 10.5563 | 13.6631 | 59.321
6980 | 0 | 0 | 60.5917
6981 | 1.1094 | 0 | 59.7112
6982 | 0 | 0 | 59.545
6983 | 0 | 0 | 59.45
6984 | 0 | 0 | 59.3552
6985 | 0 | 0 | 59.2606
6986 | 0 | 0 | 59.1663
6987 | 0 | 0 | 59.0722
6988 | 0 | 0 | 58.9783
6989 | 0 | 0 | 58.8846
6990 | 10.6789 | 13.5348 | 59.6644
6991 | 1.1218 | 0 | 60.0975
6992 | 1.4589 | 0 | 58.8999
6993 | 0 | 0 | 58.7134
6994 | 0 | 0 | 58.6203
6995 | 0 | 0 | 58.5275
6996 | 0.70919 | 6.394 | 61.6547
6997 | 0 | 0 | 62.7057
6998 | 0 | 0 | 62.6032
6999 | 0 | 0 | 62.501
7000 | 0 | 0 | 62.3991
7001 | 0 | 0 | 62.2974
7002 | 5.5523 | 6.4021 | 61.0559
7003 | 10.9461 | 12.4769 | 61.3337
7004 | 0 | 0 | 63.8177
7005 | 1.1925 | 0 | 62.8699
7006 | 0 | 0 | 62.6908
7007 | 0 | 0 | 62.5884
7008 | 0 | 0 | 62.4862
7009 | 0 | 0 | 62.3843
7010 | 0 | 0 | 62.2827
7011 | 0 | 0 | 62.1812
7012 | 0 | 0 | 62.08
7013 | 0 | 0 | 61.9791
7014 | 10.7756 | 12.9115 | 60.7297
7015 | 1.1876 | 0 | 62.5779
7016 | 1.5445 | 0 | 61.3088
7017 | 0 | 0 | 61.1111
7018 | 0 | 0 | 61.0124
7019 | 0 | 0 | 60.9139
7020 | 0.75066 | 0 | 60.2859
7021 | 0 | 0 | 60.1411
7022 | 0 | 0 | 60.0447
7023 | 0 | 0 | 59.9485
7024 | 0 | 0 | 59.8526
7025 | 0 | 0 | 59.7568
7026 | 5.3769 | 6.976 | 59.7146
7027 | 10.5242 | 13.2369 | 59.8867
7028 | 0 | 0 | 62.7765
7029 | 1.1689 | 0 | 61.8481
7030 | 0 | 0 | 61.673
7031 | 0 | 0 | 61.573
7032 | 0 | 0 | 61.4732
7033 | 0 | 0 | 61.3737
7034 | 0 | 0 | 61.2744
7035 | 0 | 0 | 61.1753
7036 | 0 | 0 | 61.0765
7037 | 0 | 0 | 60.9779
7038 | 10.5709 | 13.2999 | 59.9827
7039 | 1.1765 | 0 | 62.0445
7040 | 1.5301 | 0 | 60.7878
7041 | 0 | 0 | 60.5922
7042 | 0 | 0 | 60.4947
7043 | 0 | 0 | 60.3975
7044 | 0.74369 | 0 | 59.7757
7045 | 0 | 0 | 59.6326
7046 | 0 | 0 | 59.5374
7047 | 0 | 0 | 59.4424
7048 | 0 | 0 | 59.3476
7049 | 0 | 0 | 59.2531
7050 | 5.5394 | 6.8237 | 59.9354
7051 | 10.9915 | 13.1048 | 60.5274
7052 | 0 | 0 | 61.5731
7053 | 1.1413 | 0 | 60.6674
7054 | 0 | 0 | 60.4968
7055 | 0 | 0 | 60.3996
7056 | 0 | 0 | 60.3026
7057 | 0 | 0 | 60.2058
7058 | 0 | 0 | 60.1092
7059 | 0 | 0 | 60.0129
7060 | 0 | 0 | 59.9168
7061 | 0 | 0 | 59.8209
7062 | 10.9523 | 13.2945 | 60.3268
7063 | 1.1427 | 0 | 60.6206
7064 | 1.4862 | 0 | 59.401
7065 | 0 | 0 | 59.2115
7066 | 0 | 0 | 59.1173
7067 | 0 | 0 | 59.0233
7068 | 0.72244 | 0 | 58.42
7069 | 0 | 0 | 58.2814
7070 | 0 | 0 | 58.1894
7071 | 0 | 0 | 58.0976
7072 | 0 | 6.3676 | 59.2626
7073 | 0 | 0 | 62.8075
7074 | 5.6494 | 0 | 59.4237
7075 | 10.6388 | 13.6742 | 59.2392
7076 | 0 | 0 | 60.4974
7077 | 1.117 | 0 | 59.6118
7078 | 0 | 0 | 59.4453
7079 | 0 | 0 | 59.3505
7080 | 0 | 0 | 59.2559
7081 | 0 | 0 | 59.1616
7082 | 0 | 0 | 59.0675
7083 | 0 | 0 | 58.9736
7084 | 0 | 0 | 58.8799
7085 | 0 | 0 | 58.7865
7086 | 10.7485 | 13.5418 | 59.5295
7087 | 1.1281 | 0 | 59.9473
7088 | 1.4672 | 0 | 58.7439
7089 | 0 | 0 | 58.5572
7090 | 0 | 0 | 58.4645
7091 | 0 | 0 | 58.372
7092 | 0.71327 | 6.4642 | 61.5373
7093 | 0 | 0 | 62.6014
7094 | 0 | 0 | 62.4992
7095 | 0 | 0 | 62.3972
7096 | 0 | 0 | 62.2955
7097 | 0 | 0 | 62.1941
7098 | 5.5879 | 6.4654 | 60.9528
7099 | 11.0193 | 12.5443 | 61.2325
7100 | 0 | 0 | 63.7317
7101 | 1.2003 | 0 | 62.7785
7102 | 0 | 0 | 62.5992
7103 | 0 | 0 | 62.497
7104 | 0 | 0 | 62.395
7105 | 0 | 0 | 62.2933
7106 | 0 | 0 | 62.1919
7107 | 0 | 0 | 62.0907
7108 | 0 | 0 | 61.9897
7109 | 0 | 0 | 61.8889
7110 | 10.8475 | 12.9826 | 60.6223
7111 | 1.1954 | 0 | 62.4819
7112 | 1.5546 | 0 | 61.2054
7113 | 0 | 0 | 61.0072
7114 | 0 | 0 | 60.9088
7115 | 0 | 0 | 60.8106
7116 | 0.75566 | 0 | 60.1793
7117 | 0 | 0 | 60.0344
7118 | 0 | 0 | 59.9383
7119 | 0 | 0 | 59.8424
7120 | 0 | 0 | 59.7467
7121 | 0 | 0 | 59.6512
7122 | 5.4127 | 6.9858 | 59.5928
7123 | 10.9873 | 13.3805 | 60.3905
7124 | 0 | 0 | 62.4034
7125 | 1.1697 | 0 | 61.4755
7126 | 0 | 0 | 61.3012
7127 | 0 | 0 | 61.2021
7128 | 0 | 0 | 61.1032
7129 | 0 | 0 | 61.0045
7130 | 0 | 0 | 60.9061
7131 | 0 | 0 | 60.8079
7132 | 0 | 0 | 60.7099
7133 | 0 | 0 | 60.6122
7134 | 10.9883 | 13.5398 | 60.3243
7135 | 1.174 | 0 | 61.5432
7136 | 1.5269 | 0 | 60.2903
7137 | 0 | 0 | 60.0961
7138 | 0 | 0 | 59.9998
7139 | 0 | 0 | 59.9037
7140 | 0.74222 | 0 | 59.2842
7141 | 0 | 0 | 59.1424
7142 | 0 | 0 | 59.0483
7143 | 0 | 0 | 58.9544
7144 | 0 | 0 | 58.8608
7145 | 0 | 0 | 58.7674
7146 | 5.5316 | 6.8618 | 59.4775
7147 | 10.988 | 13.2972 | 60.169
7148 | 0 | 0 | 61.2759
7149 | 1.144 | 0 | 60.3691
7150 | 0 | 0 | 60.199
7151 | 0 | 0 | 60.1025
7152 | 0 | 0 | 60.0062
7153 | 0 | 0 | 59.9101
7154 | 0 | 0 | 59.8142
7155 | 0 | 0 | 59.7186
7156 | 0 | 0 | 59.6232
7157 | 0 | 0 | 59.528
7158 | 10.9849 | 13.4423 | 60.0855
7159 | 1.1478 | 0 | 60.4138
7160 | 1.4928 | 0 | 59.1898
7161 | 0 | 0 | 59.0004
7162 | 0 | 0 | 58.9066
7163 | 0 | 0 | 58.8131
7164 | 0.72575 | 0 | 58.208
7165 | 0 | 0 | 58.0697
7166 | 0 | 6.3662 | 60.8665
7167 | 0 | 0 | 62.775
7168 | 0 | 0 | 62.6724
7169 | 0 | 0 | 62.57
7170 | 5.6699 | 0 | 59.1752
7171 | 10.6777 | 13.7076 | 58.9841
7172 | 0 | 0 | 60.2418
7173 | 1.1208 | 0 | 59.3542
7174 | 0 | 0 | 59.188
7175 | 0 | 0 | 59.0939
7176 | 0 | 0 | 58.9999
7177 | 0 | 0 | 58.9062
7178 | 0 | 0 | 58.8127
7179 | 0 | 0 | 58.7194
7180 | 0 | 0 | 58.6263
7181 | 0 | 0 | 58.5334
7182 | 10.7849 | 13.5447 | 59.2572
7183 | 1.1314 | 0 | 59.6673
7184 | 1.4716 | 0 | 58.4614
7185 | 0 | 0 | 58.2751
7186 | 0 | 0 | 58.183
7187 | 0 | 0 | 58.0912
7188 | 0.71545 | 6.5878 | 61.3271
7189 | 0 | 0 | 62.4145
7190 | 0 | 0 | 62.3128
7191 | 0 | 0 | 62.2113
7192 | 0 | 0 | 62.11
7193 | 0 | 0 | 62.009
7194 | 5.615 | 6.565 | 60.7849
7195 | 11.0843 | 12.6306 | 61.0955
7196 | 0 | 0 | 63.6195
7197 | 1.2078 | 0 | 62.6613
7198 | 0 | 0 | 62.4818
7199 | 0 | 0 | 62.3799
7200 | 0 | 0 | 62.2782
7201 | 0 | 0 | 62.1768
7202 | 0 | 0 | 62.0756
7203 | 0 | 0 | 61.9747
7204 | 0 | 0 | 61.874
7205 | 0 | 0 | 61.7735
7206 | 10.9162 | 13.0643 | 60.4952
7207 | 1.203 | 0 | 62.3714
7208 | 1.5646 | 0 | 61.0876
7209 | 0 | 0 | 60.8891
7210 | 0 | 0 | 60.791
7211 | 0 | 0 | 60.693
7212 | 0.7606 | 0 | 60.0585
7213 | 0 | 0 | 59.9137
7214 | 0 | 0 | 59.8178
7215 | 0 | 0 | 59.7221
7216 | 0 | 0 | 59.6267
7217 | 0 | 0 | 59.5315
7218 | 5.4482 | 6.9963 | 59.4575
7219 | 11.0505 | 13.4369 | 60.2343
7220 | 0 | 0 | 62.2599
7221 | 1.1764 | 0 | 61.3276
7222 | 0 | 0 | 61.1532
7223 | 0 | 0 | 61.0544
7224 | 0 | 0 | 60.9559
7225 | 0 | 0 | 60.8576
7226 | 0 | 0 | 60.7595
7227 | 0 | 0 | 60.6616
7228 | 0 | 0 | 60.564
7229 | 0 | 0 | 60.4666
7230 | 11.0511 | 13.5778 | 60.1573
7231 | 1.1803 | 0 | 61.3748
7232 | 1.5351 | 0 | 60.1161
7233 | 0 | 0 | 59.9218
7234 | 0 | 0 | 59.8259
7235 | 0 | 0 | 59.7303
7236 | 0.74627 | 0 | 59.1083
7237 | 0 | 0 | 58.9666
7238 | 0 | 0 | 58.873
7239 | 0 | 0 | 58.7796
7240 | 0 | 0 | 58.6863
7241 | 0 | 0 | 58.5933
7242 | 5.561 | 6.8693 | 59.2911
7243 | 11.0433 | 13.3987 | 59.9934
7244 | 0 | 0 | 61.1215
7245 | 1.1506 | 0 | 60.2105
7246 | 0 | 0 | 60.0405
7247 | 0 | 0 | 59.9443
7248 | 0 | 0 | 59.8484
7249 | 0 | 0 | 59.7526
7250 | 0 | 0 | 59.6571
7251 | 0 | 0 | 59.5619
7252 | 0 | 0 | 59.4668
7253 | 0 | 0 | 59.372
7254 | 11.0489 | 13.537 | 59.9374
7255 | 1.1549 | 0 | 60.277
7256 | 1.5022 | 0 | 59.0463
7257 | 0 | 0 | 58.8566
7258 | 0 | 0 | 58.7632
7259 | 0 | 0 | 58.67
7260 | 0.73035 | 6.3704 | 58.5023
7261 | 0 | 0 | 62.8209
7262 | 0 | 0 | 62.7182
7263 | 0 | 0 | 62.6158
7264 | 0 | 0 | 62.5136
7265 | 0 | 0 | 62.4116
7266 | 5.7012 | 6.4026 | 61.0835
7267 | 11.2043 | 12.5794 | 61.218
7268 | 0 | 0 | 63.6972
7269 | 1.2176 | 0 | 62.732
7270 | 0 | 0 | 62.5516
7271 | 0 | 0 | 62.4495
7272 | 0 | 0 | 62.3477
7273 | 0 | 0 | 62.2461
7274 | 0 | 0 | 62.1448
7275 | 0 | 0 | 62.0437
7276 | 0 | 0 | 61.9428
7277 | 0 | 0 | 61.8422
7278 | 11.0044 | 13.0673 | 60.5134
7279 | 1.211 | 0 | 62.3686
7280 | 1.575 | 0 | 61.077
7281 | 0 | 0 | 60.8778
7282 | 0 | 0 | 60.7797
7283 | 0 | 0 | 60.6818
7284 | 0.76569 | 0 | 60.0437
7285 | 0 | 0 | 59.8986
7286 | 0 | 0 | 59.8028
7287 | 0 | 0 | 59.7071
7288 | 0 | 0 | 59.6118
7289 | 0 | 0 | 59.5166
7290 | 5.4845 | 7.001 | 59.4237
7291 | 11.1143 | 13.4433 | 60.161
7292 | 0 | 0 | 62.1768
7293 | 1.1822 | 0 | 61.2406
7294 | 0 | 0 | 61.0661
7295 | 0 | 0 | 60.9675
7296 | 0 | 0 | 60.8691
7297 | 0 | 0 | 60.771
7298 | 0 | 0 | 60.6731
7299 | 0 | 0 | 60.5755
7300 | 0 | 0 | 60.4781
7301 | 0 | 0 | 60.3809
7302 | 11.3045 | 13.0835 | 60.5682
7303 | 1.1718 | 0 | 60.7251
7304 | 1.524 | 0 | 59.4766
7305 | 0 | 0 | 59.2845
7306 | 0 | 0 | 59.1901
7307 | 0 | 0 | 59.0959
7308 | 0.74099 | 0 | 58.4793
7309 | 0 | 0 | 58.3395
7310 | 0 | 0 | 58.2473
7311 | 0 | 0 | 58.1553
7312 | 0 | 0 | 58.0636
7313 | 0 | 6.3692 | 60.8617
7314 | 5.7821 | 0 | 59.4128
7315 | 10.8699 | 13.6967 | 59.08
7316 | 0 | 0 | 60.3012
7317 | 1.138 | 0 | 59.4013
7318 | 0 | 0 | 59.2339
7319 | 0 | 0 | 59.1397
7320 | 0 | 0 | 59.0456
7321 | 0 | 0 | 58.9518
7322 | 0 | 0 | 58.8582
7323 | 0 | 0 | 58.7648
7324 | 0 | 0 | 58.6716
7325 | 0 | 0 | 58.5786
7326 | 10.9414 | 13.5614 | 59.2197
7327 | 1.1456 | 0 | 59.5948
7328 | 1.4901 | 0 | 58.3751
7329 | 0 | 0 | 58.1878
7330 | 0 | 0 | 58.096
7331 | 0 | 6.3383 | 59.2552
7332 | 0.80611 | 0 | 62.214
7333 | 0 | 0 | 62.0612
7334 | 0 | 0 | 61.9602
7335 | 0 | 0 | 61.8596
7336 | 0 | 0 | 61.7591
7337 | 0 | 0 | 61.6589
7338 | 5.6491 | 6.747 | 60.4753
7339 | 11.1762 | 12.7775 | 60.8573
7340 | 0 | 0 | 63.427
7341 | 1.2188 | 0 | 62.4617
7342 | 0 | 0 | 62.2819
7343 | 0 | 0 | 62.1804
7344 | 0 | 0 | 62.0792
7345 | 0 | 0 | 61.9783
7346 | 0 | 0 | 61.8776
7347 | 0 | 0 | 61.7771
7348 | 0 | 0 | 61.6769
7349 | 0 | 0 | 61.5768
7350 | 11.0177 | 13.1972 | 60.2855
7351 | 1.2146 | 0 | 62.1915
7352 | 1.5798 | 0 | 60.8968
7353 | 0 | 0 | 60.6978
7354 | 0 | 0 | 60.6
7355 | 0 | 0 | 60.5026
7356 | 0.76804 | 0 | 59.8633
7357 | 0 | 0 | 59.7184
7358 | 0 | 0 | 59.623
7359 | 0 | 0 | 59.5278
7360 | 0 | 0 | 59.4328
7361 | 0 | 0 | 59.3381
7362 | 5.7117 | 6.8163 | 59.9156
7363 | 11.2944 | 13.2335 | 60.3582
7364 | 0 | 0 | 61.3859
7365 | 1.1704 | 0 | 60.4602
7366 | 0 | 0 | 60.2882
7367 | 0 | 0 | 60.1915
7368 | 0 | 0 | 60.0949
7369 | 0 | 0 | 59.9987
7370 | 0 | 0 | 59.9026
7371 | 0 | 0 | 59.8067
7372 | 0 | 0 | 59.7111
7373 | 0 | 0 | 59.6157
7374 | 11.2247 | 13.4834 | 60.0525
7375 | 1.1699 | 0 | 60.3329
7376 | 1.5217 | 0 | 59.0873
7377 | 0 | 0 | 58.8963
7378 | 0 | 0 | 58.8028
7379 | 0 | 0 | 58.7095
7380 | 0.73992 | 0 | 58.0947
7381 | 0 | 6.3697 | 61.6616
7382 | 0 | 0 | 62.7534
7383 | 0 | 0 | 62.6508
7384 | 0 | 0 | 62.5485
7385 | 0 | 0 | 62.4465
7386 | 5.7694 | 6.4112 | 61.0814
7387 | 11.3243 | 12.6322 | 61.155
7388 | 0 | 0 | 63.6343
7389 | 1.2293 | 0 | 62.6609
7390 | 0 | 0 | 62.4799
7391 | 0 | 0 | 62.3781
7392 | 0 | 0 | 62.2764
7393 | 0 | 0 | 62.175
7394 | 0 | 0 | 62.0738
7395 | 0 | 0 | 61.9729
7396 | 0 | 0 | 61.8722
7397 | 0 | 0 | 61.7717
7398 | 11.1114 | 13.1431 | 60.4069
7399 | 1.222 | 0 | 62.2666
7400 | 1.5894 | 0 | 60.9644
7401 | 0 | 0 | 60.7647
7402 | 0 | 0 | 60.6668
7403 | 0 | 0 | 60.5691
7404 | 0.77275 | 0 | 59.9264
7405 | 0 | 0 | 59.7811
7406 | 0 | 0 | 59.6855
7407 | 0 | 0 | 59.5902
7408 | 0 | 0 | 59.495
7409 | 0 | 0 | 59.4001
7410 | 5.7438 | 6.7927 | 59.945
7411 | 11.3486 | 13.2435 | 60.3503
7412 | 0 | 0 | 61.3709
7413 | 1.1754 | 0 | 60.4417
7414 | 0 | 0 | 60.2694
7415 | 0 | 0 | 60.1727
7416 | 0 | 0 | 60.0763
7417 | 0 | 0 | 59.98
7418 | 0 | 0 | 59.884
7419 | 0 | 0 | 59.7882
7420 | 0 | 0 | 59.6926
7421 | 0 | 0 | 59.5972
7422 | 11.271 | 13.5078 | 60.0187
7423 | 1.1744 | 0 | 60.2945
7424 | 1.5276 | 0 | 59.0446
7425 | 0 | 0 | 58.8533
7426 | 0 | 0 | 58.7599
7427 | 0 | 0 | 58.6668
7428 | 0.74281 | 6.3693 | 59.307
7429 | 0 | 0 | 62.8053
7430 | 0 | 0 | 62.7026
7431 | 0 | 0 | 62.6002
7432 | 0 | 0 | 62.498
7433 | 0 | 0 | 62.3961
7434 | 5.7893 | 6.443 | 61.0299
7435 | 11.3645 | 12.6674 | 61.1026
7436 | 0 | 0 | 63.5894
7437 | 1.2336 | 0 | 62.6131
7438 | 0 | 0 | 62.432
7439 | 0 | 0 | 62.3302
7440 | 0 | 0 | 62.2287
7441 | 0 | 0 | 62.1274
7442 | 0 | 0 | 62.0263
7443 | 0 | 0 | 61.9255
7444 | 0 | 0 | 61.8249
7445 | 0 | 0 | 61.7245
7446 | 11.1504 | 13.1808 | 60.3501
7447 | 1.2262 | 0 | 62.2157
7448 | 1.5949 | 0 | 60.9095
7449 | 0 | 0 | 60.7095
7450 | 0 | 0 | 60.6118
7451 | 0 | 0 | 60.5142
7452 | 0.77545 | 0 | 59.8697
7453 | 0 | 0 | 59.7244
7454 | 0 | 0 | 59.6289
7455 | 0 | 0 | 59.5337
7456 | 0 | 0 | 59.4387
7457 | 0 | 0 | 59.344
7458 | 5.7646 | 6.8238 | 59.8951
7459 | 11.3886 | 13.2793 | 60.2958
7460 | 0 | 0 | 61.3196
7461 | 1.1796 | 0 | 60.3876
7462 | 0 | 0 | 60.2153
7463 | 0 | 0 | 60.1187
7464 | 0 | 0 | 60.0224
7465 | 0 | 0 | 59.9262
7466 | 0 | 0 | 59.8303
7467 | 0 | 0 | 59.7347
7468 | 0 | 0 | 59.6392
7469 | 0 | 0 | 59.544
7470 | 11.3101 | 13.5461 | 59.9608
7471 | 1.1785 | 0 | 60.2379
7472 | 1.5329 | 0 | 58.9841
7473 | 0 | 0 | 58.7927
7474 | 0 | 0 | 58.6994
7475 | 0 | 0 | 58.6064
7476 | 0.74543 | 6.3773 | 61.6981
7477 | 0 | 0 | 62.7436
7478 | 0 | 0 | 62.6411
7479 | 0 | 0 | 62.5388
7480 | 0 | 0 | 62.4368
7481 | 0 | 0 | 62.335
7482 | 5.8081 | 6.4795 | 60.97
7483 | 11.4036 | 12.7051 | 61.0456
7484 | 0 | 0 | 63.5412
7485 | 1.2378 | 0 | 62.562
7486 | 0 | 0 | 62.3808
7487 | 0 | 0 | 62.2791
7488 | 0 | 0 | 62.1777
7489 | 0 | 0 | 62.0765
7490 | 0 | 0 | 61.9756
7491 | 0 | 0 | 61.8749
7492 | 0 | 0 | 61.7744
7493 | 0 | 0 | 61.6741
7494 | 11.1889 | 13.2199 | 60.2908
7495 | 1.2304 | 0 | 62.1629
7496 | 1.6003 | 0 | 60.8528
7497 | 0 | 0 | 60.6525
7498 | 0 | 0 | 60.5549
7499 | 0 | 0 | 60.4576
7500 | 0.77813 | 0 | 59.8113
7501 | 0 | 0 | 59.6659
7502 | 0 | 0 | 59.5706
7503 | 0 | 0 | 59.4755
7504 | 0 | 0 | 59.3807
7505 | 0 | 0 | 59.2861
7506 | 5.7853 | 6.8557 | 59.8439
7507 | 11.4286 | 13.3155 | 60.2404
7508 | 0 | 0 | 61.2677
7509 | 1.1837 | 0 | 60.3329
7510 | 0 | 0 | 60.1605
7511 | 0 | 0 | 60.064
7512 | 0 | 0 | 59.9678
7513 | 0 | 0 | 59.8718
7514 | 0 | 0 | 59.776
7515 | 0 | 0 | 59.6805
7516 | 0 | 0 | 59.5851
7517 | 0 | 0 | 59.49
7518 | 11.3492 | 13.5846 | 59.9024
7519 | 1.1826 | 0 | 60.1809
7520 | 1.5382 | 0 | 58.9232
7521 | 0 | 0 | 58.7316
7522 | 0 | 0 | 58.6385
7523 | 0 | 0 | 58.5456
7524 | 0.74805 | 6.4077 | 61.6532
7525 | 0 | 0 | 62.7043
7526 | 0 | 0 | 62.6019
7527 | 0 | 0 | 62.4997
7528 | 0 | 0 | 62.3978
7529 | 0 | 0 | 62.2961
7530 | 5.8296 | 6.5064 | 60.9274
7531 | 11.4457 | 12.7381 | 60.9977
7532 | 0 | 0 | 63.4995
7533 | 1.2422 | 0 | 62.5173
7534 | 0 | 0 | 62.3359
7535 | 0 | 0 | 62.2344
7536 | 0 | 0 | 62.133
7537 | 0 | 0 | 62.032
7538 | 0 | 0 | 61.9311
7539 | 0 | 0 | 61.8305
7540 | 0 | 0 | 61.7301
7541 | 0 | 0 | 61.63
7542 | 11.229 | 13.2566 | 60.2361
7543 | 1.2347 | 0 | 62.1134
7544 | 1.6059 | 0 | 60.7991
7545 | 0 | 0 | 60.5987
7546 | 0 | 0 | 60.5012
7547 | 0 | 0 | 60.4039
7548 | 0.78088 | 0 | 59.7558
7549 | 0 | 0 | 59.6104
7550 | 0 | 0 | 59.5153
7551 | 0 | 0 | 59.4203
7552 | 0 | 0 | 59.3256
7553 | 0 | 0 | 59.2311
7554 | 5.8052 | 6.8614 | 59.7809
7555 | 11.4651 | 13.3566 | 60.1726
7556 | 0 | 0 | 61.2058
7557 | 1.1876 | 0 | 60.2684
7558 | 0 | 0 | 60.0959
7559 | 0 | 0 | 59.9996
7560 | 0 | 0 | 59.9035
7561 | 0 | 0 | 59.8076
7562 | 0 | 0 | 59.712
7563 | 0 | 0 | 59.6166
7564 | 0 | 0 | 59.5214
7565 | 0 | 0 | 59.4265
7566 | 11.3854 | 13.5957 | 59.8236
7567 | 1.186 | 0 | 60.0959
7568 | 1.5426 | 0 | 58.8352
7569 | 0 | 0 | 58.6434
7570 | 0 | 0 | 58.5505
7571 | 0 | 0 | 58.4579
7572 | 0.75024 | 6.4494 | 61.5883
7573 | 0 | 0 | 62.6471
7574 | 0 | 0 | 62.5448
7575 | 0 | 0 | 62.4428
7576 | 0 | 0 | 62.341
7577 | 0 | 0 | 62.2394
7578 | 5.849 | 6.541 | 60.8709
7579 | 11.4857 | 12.7749 | 60.9423
7580 | 0 | 0 | 63.4524
7581 | 1.2465 | 0 | 62.4673
7582 | 0 | 0 | 62.2858
7583 | 0 | 0 | 62.1843
7584 | 0 | 0 | 62.0831
7585 | 0 | 0 | 61.9822
7586 | 0 | 0 | 61.8815
7587 | 0 | 0 | 61.781
7588 | 0 | 0 | 61.6807
7589 | 0 | 0 | 61.5807
7590 | 11.268 | 13.2954 | 60.1775
7591 | 1.2389 | 0 | 62.061
7592 | 1.6114 | 0 | 60.7428
7593 | 0 | 0 | 60.5421
7594 | 0 | 0 | 60.4448
7595 | 0 | 0 | 60.3476
7596 | 0.78359 | 0 | 59.6978
7597 | 0 | 0 | 59.5523
7598 | 0 | 0 | 59.4573
7599 | 0 | 0 | 59.3625
7600 | 0 | 0 | 59.2679
7601 | 0 | 0 | 59.1735
7602 | 5.8248 | 6.8662 | 59.7148
7603 | 11.5009 | 13.3988 | 60.1025
7604 | 0 | 0 | 61.142
7605 | 1.1915 | 0 | 60.2021
7606 | 0 | 0 | 60.0295
7607 | 0 | 0 | 59.9333
7608 | 0 | 0 | 59.8374
7609 | 0 | 0 | 59.7417
7610 | 0 | 0 | 59.6462
7611 | 0 | 0 | 59.551
7612 | 0 | 0 | 59.456
7613 | 0 | 0 | 59.3612
7614 | 11.4211 | 13.6024 | 59.7413
7615 | 1.1893 | 0 | 60.0062
7616 | 1.5469 | 0 | 58.7425
7617 | 0 | 0 | 58.5507
7618 | 0 | 0 | 58.4581
7619 | 0 | 0 | 58.3656
7620 | 0.75235 | 6.4908 | 61.5187
7621 | 0 | 0 | 62.5853
7622 | 0 | 0 | 62.4832
7623 | 0 | 0 | 62.3813
7624 | 0 | 0 | 62.2796
7625 | 0 | 0 | 62.1782
7626 | 5.868 | 6.5777 | 60.8108
7627 | 11.5251 | 12.8128 | 60.885
7628 | 0 | 0 | 63.4039
7629 | 1.2508 | 0 | 62.416
7630 | 0 | 0 | 62.2342
7631 | 0 | 0 | 62.1329
7632 | 0 | 0 | 62.0318
7633 | 0 | 0 | 61.931
7634 | 0 | 0 | 61.8304
7635 | 0 | 0 | 61.73
7636 | 0 | 0 | 61.6299
7637 | 0 | 0 | 61.53
7638 | 11.3067 | 13.3347 | 60.1179
7639 | 1.2431 | 0 | 62.008
7640 | 1.6169 | 0 | 60.6857
7641 | 0 | 0 | 60.4848
7642 | 0 | 0 | 60.3876
7643 | 0 | 0 | 60.2906
7644 | 0.78629 | 0 | 59.639
7645 | 0 | 0 | 59.4935
7646 | 0 | 0 | 59.3986
7647 | 0 | 0 | 59.304
7648 | 0 | 0 | 59.2095
7649 | 0 | 0 | 59.1153
7650 | 5.8443 | 6.8709 | 59.6481
7651 | 11.5367 | 13.4412 | 60.0319
7652 | 0 | 0 | 61.0779
7653 | 1.1953 | 0 | 60.1354
7654 | 0 | 0 | 59.9627
7655 | 0 | 0 | 59.8667
7656 | 0 | 0 | 59.7709
7657 | 0 | 0 | 59.6754
7658 | 0 | 0 | 59.5801
7659 | 0 | 0 | 59.485
7660 | 0 | 0 | 59.3901
7661 | 0 | 0 | 59.2955
7662 | 11.4568 | 13.609 | 59.6587
7663 | 1.1925 | 0 | 59.9163
7664 | 1.5512 | 0 | 58.6496
7665 | 0 | 0 | 58.4578
7666 | 0 | 0 | 58.3653
7667 | 0 | 0 | 58.2731
7668 | 0.75446 | 6.5324 | 61.449
7669 | 0 | 0 | 62.5233
7670 | 0 | 0 | 62.4213
7671 | 0 | 0 | 62.3196
7672 | 0 | 0 | 62.2181
7673 | 0 | 0 | 62.1168
7674 | 5.8869 | 6.6145 | 60.7506
7675 | 11.5646 | 12.8508 | 60.8275
7676 | 0 | 0 | 63.3553
7677 | 1.255 | 0 | 62.3645
7678 | 0 | 0 | 62.1826
7679 | 0 | 0 | 62.0814
7680 | 0 | 0 | 61.9805
7681 | 0 | 0 | 61.8798
7682 | 0 | 0 | 61.7793
7683 | 0 | 0 | 61.679
7684 | 0 | 0 | 61.579
7685 | 0 | 0 | 61.4792
7686 | 11.3454 | 13.374 | 60.0582
7687 | 1.2473 | 0 | 61.9549
7688 | 1.6224 | 0 | 60.6286
7689 | 0 | 0 | 60.4275
7690 | 0 | 0 | 60.3304
7691 | 0 | 0 | 60.2336
7692 | 0.78899 | 0 | 59.5802
7693 | 0 | 0 | 59.4347
7694 | 0 | 0 | 59.3399
7695 | 0 | 0 | 59.2454
7696 | 0 | 0 | 59.1511
7697 | 0 | 0 | 59.057
7698 | 5.8638 | 6.8757 | 59.5814
7699 | 11.5725 | 13.4836 | 59.9614
7700 | 0 | 0 | 61.0138
7701 | 1.1992 | 0 | 60.0688
7702 | 0 | 0 | 59.8959
7703 | 0 | 0 | 59.8001
7704 | 0 | 0 | 59.7045
7705 | 0 | 0 | 59.6091
7706 | 0 | 0 | 59.5139
7707 | 0 | 0 | 59.419
7708 | 0 | 0 | 59.3243
7709 | 0 | 0 | 59.2298
7710 | 11.4924 | 13.6157 | 59.5761
7711 | 1.1958 | 0 | 59.8264
7712 | 1.5555 | 0 | 58.5567
7713 | 0 | 0 | 58.3648
7714 | 0 | 0 | 58.2726
7715 | 0 | 0 | 58.1806
7716 | 0.75657 | 6.574 | 61.3793
7717 | 0 | 0 | 62.4614
7718 | 0 | 0 | 62.3595
7719 | 0 | 0 | 62.2579
7720 | 0 | 0 | 62.1565
7721 | 0 | 0 | 62.0554
7722 | 5.9058 | 6.6512 | 60.6903
7723 | 11.6039 | 12.8887 | 60.7702
7724 | 0 | 0 | 63.3067
7725 | 1.2593 | 0 | 62.3131
7726 | 0 | 0 | 62.1311
7727 | 0 | 0 | 62.03
7728 | 0 | 0 | 61.9292
7729 | 0 | 0 | 61.8286
7730 | 0 | 0 | 61.7282
7731 | 0 | 0 | 61.6281
7732 | 0 | 0 | 61.5282
7733 | 0 | 0 | 61.4285
7734 | 11.384 | 13.4132 | 59.9986
7735 | 1.2515 | 0 | 61.9018
7736 | 1.6279 | 0 | 60.5716
7737 | 0 | 0 | 60.3703
7738 | 0 | 0 | 60.2733
7739 | 0 | 0 | 60.1766
7740 | 0.79169 | 0 | 59.5215
7741 | 0 | 0 | 59.3759
7742 | 0 | 0 | 59.2813
7743 | 0 | 0 | 59.1869
7744 | 0 | 0 | 59.0928
7745 | 0 | 0 | 58.9988
7746 | 5.8833 | 6.8804 | 59.5148
7747 | 11.6076 | 13.5111 | 59.8844
7748 | 0 | 0 | 60.9387
7749 | 1.2028 | 0 | 59.9913
7750 | 0 | 0 | 59.8185
7751 | 0 | 0 | 59.7228
7752 | 0 | 0 | 59.6274
7753 | 0 | 0 | 59.5322
7754 | 0 | 0 | 59.4372
7755 | 0 | 0 | 59.3425
7756 | 0 | 0 | 59.2479
7757 | 0 | 0 | 59.1536
7758 | 11.5255 | 13.6231 | 59.4848
7759 | 1.1988 | 0 | 59.7286
7760 | 1.5594 | 0 | 58.4562
7761 | 0 | 0 | 58.2643
7762 | 0 | 0 | 58.1723
7763 | 0 | 0 | 58.0805
7764 | 0.75854 | 6.6187 | 61.3039
7765 | 0 | 0 | 62.3944
7766 | 0 | 0 | 62.2927
7767 | 0 | 0 | 62.1913
7768 | 0 | 0 | 62.0901
7769 | 0 | 0 | 61.9891
7770 | 5.924 | 6.6901 | 60.6262
7771 | 11.6426 | 12.9276 | 60.7108
7772 | 0 | 0 | 63.2568
7773 | 1.2635 | 0 | 62.2603
7774 | 0 | 0 | 62.0781
7775 | 0 | 0 | 61.9772
7776 | 0 | 0 | 61.8765
7777 | 0 | 0 | 61.776
7778 | 0 | 0 | 61.6758
7779 | 0 | 0 | 61.5758
7780 | 0 | 0 | 61.476
7781 | 0 | 0 | 61.3764
7782 | 11.4222 | 13.4529 | 59.938
7783 | 1.2557 | 0 | 61.8482
7784 | 1.6333 | 0 | 60.514
7785 | 0 | 0 | 60.3124
7786 | 0 | 0 | 60.2156
7787 | 0 | 0 | 60.1191
7788 | 0.79436 | 0 | 59.4622
7789 | 0 | 0 | 59.3166
7790 | 0 | 0 | 59.2221
7791 | 0 | 0 | 59.1279
7792 | 0 | 0 | 59.0338
7793 | 0 | 0 | 58.94
7794 | 5.9026 | 6.8852 | 59.4477
7795 | 11.6418 | 13.5144 | 59.7965
7796 | 0 | 0 | 60.8455
7797 | 1.2059 | 0 | 59.8962
7798 | 0 | 0 | 59.7233
7799 | 0 | 0 | 59.6279
7800 | 0 | 0 | 59.5327
7801 | 0 | 0 | 59.4377
7802 | 0 | 0 | 59.343
7803 | 0 | 0 | 59.2484
7804 | 0 | 0 | 59.1541
7805 | 0 | 0 | 59.06
7806 | 11.5542 | 13.6269 | 59.3767
7807 | 1.2014 | 0 | 59.6144
7808 | 1.5629 | 0 | 58.3398
7809 | 0 | 0 | 58.1479
7810 | 0 | 0 | 58.0562
7811 | 0 | 6.3418 | 61.6543
7812 | 0.84175 | 0 | 62.1462
7813 | 0 | 0 | 61.9913
7814 | 0 | 0 | 61.8905
7815 | 0 | 0 | 61.79
7816 | 0 | 0 | 61.6897
7817 | 0 | 0 | 61.5897
7818 | 5.9022 | 6.8421 | 60.2902
7819 | 11.6322 | 13.0443 | 60.4921
7820 | 0 | 0 | 63.0909
7821 | 1.2647 | 0 | 62.094
7822 | 0 | 0 | 61.9121
7823 | 0 | 0 | 61.8116
7824 | 0 | 0 | 61.7112
7825 | 0 | 0 | 61.6112
7826 | 0 | 0 | 61.5113
7827 | 0 | 0 | 61.4117
7828 | 0 | 0 | 61.3123
7829 | 0 | 0 | 61.2131
7830 | 11.4349 | 13.5347 | 59.7957
7831 | 1.2584 | 0 | 61.7367
7832 | 1.6368 | 0 | 60.4002
7833 | 0 | 0 | 60.1987
7834 | 0 | 0 | 60.1022
7835 | 0 | 0 | 60.0059
7836 | 0.79609 | 0 | 59.348
7837 | 0 | 0 | 59.2026
7838 | 0 | 0 | 59.1084
7839 | 0 | 0 | 59.0144
7840 | 0 | 0 | 58.9207
7841 | 0 | 0 | 58.8271
7842 | 5.9154 | 6.8925 | 59.3317
7843 | 11.6648 | 13.5164 | 59.6672
7844 | 0 | 0 | 60.7127
7845 | 1.208 | 0 | 59.7623
7846 | 0 | 0 | 59.5896
7847 | 0 | 0 | 59.4945
7848 | 0 | 0 | 59.3996
7849 | 0 | 0 | 59.305
7850 | 0 | 0 | 59.2105
7851 | 0 | 0 | 59.1163
7852 | 0 | 0 | 59.0223
7853 | 0 | 0 | 58.9285
7854 | 11.5739 | 13.6299 | 59.2356
7855 | 1.2032 | 0 | 59.4694
7856 | 1.5652 | 0 | 58.1933
7857 | 0 | 6.3392 | 59.2527
7858 | 0 | 0 | 62.7815
7859 | 0 | 0 | 62.6789
7860 | 0.84261 | 0 | 61.9813
7861 | 0 | 0 | 61.8267
7862 | 0 | 0 | 61.7263
7863 | 0 | 0 | 61.6262
7864 | 0 | 0 | 61.5263
7865 | 0 | 0 | 61.4266
7866 | 5.9087 | 6.8617 | 60.1302
7867 | 11.6469 | 13.1165 | 60.355
7868 | 0 | 0 | 62.9831
7869 | 1.2675 | 0 | 61.9845
7870 | 0 | 0 | 61.8028
7871 | 0 | 0 | 61.7025
7872 | 0 | 0 | 61.6024
7873 | 0 | 0 | 61.5026
7874 | 0 | 0 | 61.403
7875 | 0 | 0 | 61.3036
7876 | 0 | 0 | 61.2045
7877 | 0 | 0 | 61.1056
7878 | 11.8682 | 13.6308 | 60.3373
7879 | 1.2545 | 0 | 61.3708
7880 | 1.6318 | 0 | 60.0391
7881 | 0 | 0 | 59.8388
7882 | 0 | 0 | 59.7431
7883 | 0 | 0 | 59.6476
7884 | 0.79372 | 0 | 58.9924
7885 | 0 | 0 | 58.848
7886 | 0 | 0 | 58.7546
7887 | 0 | 0 | 58.6614
7888 | 0 | 0 | 58.5685
7889 | 0 | 0 | 58.4758
7890 | 5.8998 | 6.9051 | 58.9976
7891 | 11.6387 | 13.512 | 59.3519
7892 | 0 | 0 | 60.4019
7893 | 1.2056 | 0 | 59.454
7894 | 0 | 0 | 59.2822
7895 | 0 | 0 | 59.1878
7896 | 0 | 0 | 59.0936
7897 | 0 | 0 | 58.9997
7898 | 0 | 0 | 58.906
7899 | 0 | 0 | 58.8124
7900 | 0 | 0 | 58.7192
7901 | 0 | 0 | 58.6261
7902 | 11.5539 | 13.6268 | 58.9439
7903 | 1.2014 | 0 | 59.1826
7904 | 1.5629 | 6.3963 | 61.6303
7905 | 0 | 0 | 62.6274
7906 | 0 | 0 | 62.5251
7907 | 0 | 0 | 62.4231
7908 | 0.84192 | 0 | 61.7267
7909 | 0 | 0 | 61.5727
7910 | 0 | 0 | 61.473
7911 | 0 | 0 | 61.3734
7912 | 0 | 0 | 61.2741
7913 | 0 | 0 | 61.1751
7914 | 5.9043 | 6.8852 | 59.8895
7915 | 11.6437 | 13.2149 | 60.1598
7916 | 0 | 0 | 62.8324
7917 | 1.2691 | 0 | 61.8331
7918 | 0 | 0 | 61.6516
7919 | 0 | 0 | 61.5517
7920 | 0 | 0 | 61.452
7921 | 0 | 0 | 61.3525
7922 | 0 | 0 | 61.2532
7923 | 0 | 0 | 61.1542
7924 | 0 | 0 | 61.0554
7925 | 0 | 0 | 60.9569
7926 | 11.8842 | 13.64 | 60.185
7927 | 1.256 | 0 | 61.2165
7928 | 1.6338 | 0 | 59.8837
7929 | 0 | 0 | 59.6837
7930 | 0 | 0 | 59.5883
7931 | 0 | 0 | 59.4932
7932 | 0.79473 | 0 | 58.8377
7933 | 0 | 0 | 58.6936
7934 | 0 | 0 | 58.6006
7935 | 0 | 0 | 58.5078
7936 | 0 | 0 | 58.4152
7937 | 0 | 0 | 58.3228
7938 | 5.9072 | 6.9058 | 58.8411
7939 | 11.6519 | 13.5133 | 59.1875
7940 | 0 | 0 | 60.2356
7941 | 1.2068 | 0 | 59.2873
7942 | 0 | 0 | 59.1159
7943 | 0 | 0 | 59.0219
7944 | 0 | 0 | 58.9281
7945 | 0 | 0 | 58.8345
7946 | 0 | 0 | 58.7412
7947 | 0 | 0 | 58.648
7948 | 0 | 0 | 58.5551
7949 | 0 | 0 | 58.4625
7950 | 11.5654 | 18.9887 | 60.521
7951 | 1.3058 | 0 | 63.0576
7952 | 1.6984 | 0 | 61.6707
7953 | 0 | 0 | 61.4623
7954 | 0 | 0 | 61.3628
7955 | 0 | 0 | 61.2635
7956 | 0.82609 | 0 | 60.5813
7957 | 0 | 0 | 60.431
7958 | 0 | 0 | 60.3339
7959 | 0 | 0 | 60.2371
7960 | 0 | 0 | 60.1404
7961 | 0 | 0 | 60.044
7962 | 5.9123 | 7.0195 | 59.7093
7963 | 12.0636 | 13.0651 | 60.5185
7964 | 0 | 0 | 61.3707
7965 | 1.2378 | 0 | 60.3975
7966 | 0 | 0 | 60.2214
7967 | 0 | 0 | 60.1248
7968 | 0 | 0 | 60.0284
7969 | 0 | 0 | 59.9323
7970 | 0 | 0 | 59.8364
7971 | 0 | 0 | 59.7407
7972 | 0 | 0 | 59.6452
7973 | 0 | 0 | 59.55
7974 | 11.8379 | 13.6319 | 59.7007
7975 | 1.2271 | 0 | 59.8701
7976 | 1.5962 | 0 | 58.5696
7977 | 0 | 0 | 58.375
7978 | 0 | 0 | 58.2828
7979 | 0 | 0 | 58.1907
7980 | 0.77656 | 6.5817 | 61.3798
7981 | 0 | 0 | 62.4621
7982 | 0 | 0 | 62.3602
7983 | 0 | 0 | 62.2586
7984 | 0 | 0 | 62.1572
7985 | 0 | 0 | 62.0561
7986 | 6.0485 | 6.7042 | 60.6254
7987 | 11.8609 | 13.0226 | 60.5981
7988 | 0 | 0 | 63.1436
7989 | 1.2848 | 0 | 62.1323
7990 | 0 | 0 | 61.9491
7991 | 0 | 0 | 61.8484
7992 | 0 | 0 | 61.748
7993 | 0 | 0 | 61.6478
7994 | 0 | 0 | 61.5479
7995 | 0 | 0 | 61.4482
7996 | 0 | 0 | 61.3487
7997 | 0 | 0 | 61.2495
7998 | 11.6152 | 13.5896 | 59.746
7999 | 1.2756 | 0 | 61.6643
8000 | 1.6592 | 0 | 60.3111
8001 | 0 | 0 | 60.1084
8002 | 0 | 0 | 60.012
8003 | 0 | 0 | 59.9159
8004 | 0.8071 | 0 | 59.2506
8005 | 0 | 0 | 59.1047
8006 | 0 | 0 | 59.0107
8007 | 0 | 0 | 58.917
8008 | 0 | 0 | 58.8234
8009 | 0 | 0 | 58.7301
8010 | 5.9943 | 6.9041 | 59.1959
8011 | 11.8033 | 13.5305 | 59.4456
8012 | 0 | 0 | 60.4692
8013 | 1.2206 | 0 | 59.5106
8014 | 0 | 0 | 59.3377
8015 | 0 | 0 | 59.2432
8016 | 0 | 0 | 59.1489
8017 | 0 | 0 | 59.0548
8018 | 0 | 0 | 58.9609
8019 | 0 | 0 | 58.8673
8020 | 0 | 0 | 58.7739
8021 | 0 | 0 | 58.6807
8022 | 11.6889 | 13.6412 | 58.9271
8023 | 1.2137 | 0 | 59.1357
8024 | 1.5789 | 6.4244 | 61.5876
8025 | 0 | 0 | 62.589
8026 | 0 | 0 | 62.4868
8027 | 0 | 0 | 62.3849
8028 | 0.85015 | 0 | 61.6828
8029 | 0 | 0 | 61.5284
8030 | 0 | 0 | 61.4287
8031 | 0 | 0 | 61.3293
8032 | 0 | 0 | 61.2301
8033 | 0 | 0 | 61.1312
8034 | 6.077 | 6.7989 | 60.5972
8035 | 11.7131 | 13.4081 | 59.9533
8036 | 0 | 0 | 62.6865
8037 | 1.2787 | 0 | 61.6808
8038 | 0 | 0 | 61.4991
8039 | 0 | 0 | 61.3995
8040 | 0 | 0 | 61.3001
8041 | 0 | 0 | 61.201
8042 | 0 | 0 | 61.1021
8043 | 0 | 0 | 61.0034
8044 | 0 | 0 | 60.905
8045 | 0 | 0 | 60.8068
8046 | 12.1736 | 13.1831 | 60.533
8047 | 1.2512 | 0 | 60.5016
8048 | 1.6276 | 0 | 59.1756
8049 | 0 | 0 | 58.9776
8050 | 0 | 0 | 58.8839
8051 | 0 | 0 | 58.7905
8052 | 0.79183 | 0 | 58.1388
8053 | 0 | 6.3647 | 60.0686
8054 | 0 | 0 | 62.794
8055 | 0 | 0 | 62.6914
8056 | 0 | 0 | 62.589
8057 | 0 | 0 | 62.4869
8058 | 6.1381 | 6.5295 | 60.9459
8059 | 11.9848 | 12.9655 | 60.7321
8060 | 0 | 0 | 63.2296
8061 | 1.2949 | 0 | 62.211
8062 | 0 | 0 | 62.027
8063 | 0 | 0 | 61.9261
8064 | 0 | 0 | 61.8255
8065 | 0 | 0 | 61.7252
8066 | 0 | 0 | 61.6251
8067 | 0 | 0 | 61.5252
8068 | 0 | 0 | 61.4255
8069 | 0 | 0 | 61.3261
8070 | 11.7047 | 13.5894 | 59.7704
8071 | 1.2836 | 0 | 61.6659
8072 | 1.6697 | 0 | 60.3048
8073 | 0 | 0 | 60.1014
8074 | 0 | 0 | 60.0051
8075 | 0 | 0 | 59.909
8076 | 0.81223 | 0 | 59.2401
8077 | 0 | 0 | 59.0939
8078 | 0 | 0 | 58.9999
8079 | 0 | 0 | 58.9062
8080 | 0 | 0 | 58.8127
8081 | 0 | 0 | 58.7194
8082 | 6.0309 | 6.9076 | 59.1659
8083 | 11.8674 | 13.5373 | 59.3755
8084 | 0 | 0 | 60.3891
8085 | 1.2264 | 0 | 59.4265
8086 | 0 | 0 | 59.2535
8087 | 0 | 0 | 59.1591
8088 | 0 | 0 | 59.065
8089 | 0 | 0 | 58.9712
8090 | 0 | 0 | 58.8775
8091 | 0 | 0 | 58.7841
8092 | 0 | 0 | 58.6908
8093 | 0 | 0 | 58.5978
8094 | 11.7419 | 19.0027 | 60.5615
8095 | 1.3218 | 0 | 63.0563
8096 | 1.7193 | 0 | 61.6538
8097 | 0 | 0 | 61.444
8098 | 0 | 0 | 61.3446
8099 | 0 | 0 | 61.2453
8100 | 0.8363 | 0 | 60.5559
8101 | 0 | 0 | 60.4051
8102 | 0 | 0 | 60.3081
8103 | 0 | 0 | 60.2113
8104 | 0 | 0 | 60.1147
8105 | 0 | 0 | 60.0183
8106 | 5.985 | 7.0288 | 59.6456
8107 | 12.1936 | 13.1412 | 60.4038
8108 | 0 | 0 | 61.2552
8109 | 1.2507 | 0 | 60.2732
8110 | 0 | 0 | 60.0966
8111 | 0 | 0 | 60.0003
8112 | 0 | 0 | 59.9042
8113 | 0 | 0 | 59.8083
8114 | 0 | 0 | 59.7127
8115 | 0 | 0 | 59.6173
8116 | 0 | 0 | 59.5221
8117 | 0 | 0 | 59.4272
8118 | 11.9546 | 13.6491 | 59.5195
8119 | 1.2377 | 0 | 59.6639
8120 | 1.6102 | 0 | 58.3534
8121 | 0 | 0 | 58.1585
8122 | 0 | 0 | 58.0668
8123 | 0 | 6.3501 | 60.8562
8124 | 0.86508 | 0 | 62.1485
8125 | 0 | 0 | 61.9921
8126 | 0 | 0 | 61.8913
8127 | 0 | 0 | 61.7908
8128 | 0 | 0 | 61.6905
8129 | 0 | 0 | 61.5905
8130 | 6.0678 | 6.8573 | 60.1997
8131 | 11.9221 | 13.2092 | 60.2641
8132 | 0 | 0 | 62.8797
8133 | 1.2939 | 0 | 61.8628
8134 | 0 | 0 | 61.6796
8135 | 0 | 0 | 61.5796
8136 | 0 | 0 | 61.4798
8137 | 0 | 0 | 61.3803
8138 | 0 | 0 | 61.2809
8139 | 0 | 0 | 61.1819
8140 | 0 | 0 | 61.083
8141 | 0 | 0 | 60.9844
8142 | 12.1071 | 13.6604 | 60.0914
8143 | 1.2763 | 0 | 61.0738
8144 | 1.6603 | 0 | 59.7215
8145 | 0 | 0 | 59.5202
8146 | 0 | 0 | 59.4252
8147 | 0 | 0 | 59.3305
8148 | 0.80774 | 0 | 58.6662
8149 | 0 | 0 | 58.5216
8150 | 0 | 0 | 58.429
8151 | 0 | 0 | 58.3366
8152 | 0 | 0 | 58.2445
8153 | 0 | 0 | 58.1525
8154 | 6.0003 | 6.9152 | 58.6225
8155 | 11.815 | 18.8796 | 60.6102
8156 | 0 | 0 | 64.0023
8157 | 1.3245 | 0 | 62.9606
8158 | 0 | 0 | 62.7729
8159 | 0 | 0 | 62.6703
8160 | 0 | 0 | 62.568
8161 | 0 | 0 | 62.4659
8162 | 0 | 0 | 62.364
8163 | 0 | 0 | 62.2624
8164 | 0 | 0 | 62.161
8165 | 0 | 0 | 62.0599
8166 | 11.9657 | 13.3495 | 60.2685
8167 | 1.3025 | 0 | 61.998
8168 | 1.6943 | 0 | 60.6173
8169 | 0 | 0 | 60.4117
8170 | 0 | 0 | 60.3146
8171 | 0 | 0 | 60.2178
8172 | 0.82424 | 0 | 59.5396
8173 | 0 | 0 | 59.3919
8174 | 0 | 0 | 59.2973
8175 | 0 | 0 | 59.2028
8176 | 0 | 0 | 59.1086
8177 | 0 | 0 | 59.0146
8178 | 6.1151 | 6.8979 | 59.4058
8179 | 12.0134 | 13.5539 | 59.521
8180 | 0 | 0 | 60.5112
8181 | 1.2397 | 0 | 59.5389
8182 | 0 | 0 | 59.3647
8183 | 0 | 0 | 59.2701
8184 | 0 | 0 | 59.1758
8185 | 0 | 0 | 59.0816
8186 | 0 | 0 | 58.9877
8187 | 0 | 0 | 58.894
8188 | 0 | 0 | 58.8005
8189 | 0 | 0 | 58.7073
8190 | 11.8611 | 19.0044 | 60.6042
8191 | 1.3324 | 0 | 63.0675
8192 | 1.7332 | 0 | 61.6544
8193 | 0 | 0 | 61.4438
8194 | 0 | 0 | 61.3443
8195 | 0 | 0 | 61.2451
8196 | 0.84311 | 0 | 60.5509
8197 | 0 | 0 | 60.3996
8198 | 0 | 0 | 60.3026
8199 | 0 | 0 | 60.2058
8200 | 0 | 0 | 60.1093
8201 | 0 | 0 | 60.0129
8202 | 6.0334 | 7.0344 | 59.6146
8203 | 12.28 | 13.187 | 60.3365
8204 | 0 | 0 | 61.1858
8205 | 1.2591 | 0 | 60.198
8206 | 0 | 0 | 60.021
8207 | 0 | 0 | 59.9249
8208 | 0 | 0 | 59.829
8209 | 0 | 0 | 59.7333
8210 | 0 | 0 | 59.6379
8211 | 0 | 0 | 59.5427
8212 | 0 | 0 | 59.4477
8213 | 0 | 0 | 59.3529
8214 | 12.0312 | 13.66 | 59.4066
8215 | 1.2447 | 0 | 59.5346
8216 | 1.6193 | 0 | 58.2176
8217 | 0 | 6.3438 | 58.4608
8218 | 0 | 0 | 62.8076
8219 | 0 | 0 | 62.705
8220 | 0.86921 | 0 | 61.9886
8221 | 0 | 0 | 61.8322
8222 | 0 | 0 | 61.7318
8223 | 0 | 0 | 61.6317
8224 | 0 | 0 | 61.5318
8225 | 0 | 0 | 61.4321
8226 | 6.0975 | 6.8789 | 60.0316
8227 | 11.9775 | 13.3025 | 60.0989
8228 | 0 | 0 | 62.7453
8229 | 1.3006 | 0 | 61.7239
8230 | 0 | 0 | 61.5407
8231 | 0 | 0 | 61.441
8232 | 0 | 0 | 61.3415
8233 | 0 | 0 | 61.2423
8234 | 0 | 0 | 61.1433
8235 | 0 | 0 | 61.0446
8236 | 0 | 0 | 60.946
8237 | 0 | 0 | 60.8477
8238 | 12.3716 | 13.2306 | 60.4806
8239 | 1.2697 | 0 | 60.4137
8240 | 1.6517 | 0 | 59.0697
8241 | 0 | 0 | 58.8705
8242 | 0 | 0 | 58.7771
8243 | 0 | 0 | 58.6839
8244 | 0.80366 | 6.3689 | 60.9137
8245 | 0 | 0 | 62.7715
8246 | 0 | 0 | 62.6689
8247 | 0 | 0 | 62.5666
8248 | 0 | 0 | 62.4645
8249 | 0 | 0 | 62.3626
8250 | 6.2211 | 6.6205 | 60.8035
8251 | 12.1451 | 13.0843 | 60.5618
8252 | 0 | 0 | 63.0801
8253 | 1.3115 | 0 | 62.0502
8254 | 0 | 0 | 61.8655
8255 | 0 | 0 | 61.765
8256 | 0 | 0 | 61.6648
8257 | 0 | 0 | 61.5648
8258 | 0 | 0 | 61.4651
8259 | 0 | 0 | 61.3655
8260 | 0 | 0 | 61.2663
8261 | 0 | 0 | 61.1672
8262 | 12.2634 | 13.6664 | 60.1838
8263 | 1.2905 | 0 | 61.1302
8264 | 1.6787 | 0 | 59.7638
8265 | 0 | 0 | 59.5611
8266 | 0 | 0 | 59.4661
8267 | 0 | 0 | 59.3713
8268 | 0.81678 | 0 | 58.7005
8269 | 0 | 0 | 58.5553
8270 | 0 | 0 | 58.4626
8271 | 0 | 0 | 58.3701
8272 | 0 | 0 | 58.2779
8273 | 0 | 0 | 58.1858
8274 | 6.0647 | 6.9223 | 58.6224
8275 | 11.928 | 18.9308 | 60.5524
8276 | 0 | 0 | 63.9439
8277 | 1.3356 | 0 | 62.8946
8278 | 0 | 0 | 62.7063
8279 | 0 | 0 | 62.6039
8280 | 0 | 0 | 62.5017
8281 | 0 | 0 | 62.3998
8282 | 0 | 0 | 62.2981
8283 | 0 | 0 | 62.1966
8284 | 0 | 0 | 62.0954
8285 | 0 | 0 | 61.9944
8286 | 12.0649 | 13.4199 | 60.1697
8287 | 1.3127 | 0 | 61.9034
8288 | 1.7076 | 0 | 60.5129
8289 | 0 | 0 | 60.3066
8290 | 0 | 0 | 60.2098
8291 | 0 | 0 | 60.1133
8292 | 0.83079 | 0 | 59.4307
8293 | 0 | 0 | 59.2829
8294 | 0 | 0 | 59.1885
8295 | 0 | 0 | 59.0943
8296 | 0 | 0 | 59.0003
8297 | 0 | 0 | 58.9066
8298 | 6.1623 | 6.9076 | 59.2763
8299 | 12.0965 | 13.5622 | 59.3405
8300 | 0 | 0 | 60.3177
8301 | 1.2473 | 0 | 59.3406
8302 | 0 | 0 | 59.1664
8303 | 0 | 0 | 59.0723
8304 | 0 | 0 | 58.9784
8305 | 0 | 0 | 58.8847
8306 | 0 | 0 | 58.7912
8307 | 0 | 0 | 58.698
8308 | 0 | 0 | 58.605
8309 | 0 | 0 | 58.5122
8310 | 11.9298 | 19.1173 | 60.4074
8311 | 1.3407 | 0 | 62.9011
8312 | 1.744 | 0 | 61.4803
8313 | 0 | 0 | 61.2694
8314 | 0 | 0 | 61.1704
8315 | 0 | 0 | 61.0716
8316 | 0.84844 | 0 | 60.3741
8317 | 0 | 0 | 60.2229
8318 | 0 | 0 | 60.1263
8319 | 0 | 0 | 60.0299
8320 | 0 | 0 | 59.9338
8321 | 0 | 0 | 59.8378
8322 | 6.0718 | 7.0483 | 59.4239
8323 | 12.3523 | 13.2947 | 60.1508
8324 | 0 | 0 | 61.0202
8325 | 1.2673 | 0 | 60.0271
8326 | 0 | 0 | 59.85
8327 | 0 | 0 | 59.7543
8328 | 0 | 0 | 59.6588
8329 | 0 | 0 | 59.5635
8330 | 0 | 0 | 59.4685
8331 | 0 | 0 | 59.3736
8332 | 0 | 0 | 59.279
8333 | 0 | 0 | 59.1846
8334 | 12.1059 | 13.6755 | 59.2039
8335 | 1.2516 | 0 | 59.3168
8336 | 1.6283 | 6.3688 | 61.6989
8337 | 0 | 0 | 62.6865
8338 | 0 | 0 | 62.5842
8339 | 0 | 0 | 62.482
8340 | 0.87364 | 0 | 61.7631
8341 | 0 | 0 | 61.6069
8342 | 0 | 0 | 61.5071
8343 | 0 | 0 | 61.4075
8344 | 0 | 0 | 61.3081
8345 | 0 | 0 | 61.209
8346 | 6.2437 | 6.8143 | 60.5847
8347 | 12.0048 | 13.5365 | 59.7889
8348 | 0 | 0 | 62.5219
8349 | 1.3072 | 0 | 61.4965
8350 | 0 | 0 | 61.3133
8351 | 0 | 0 | 61.2142
8352 | 0 | 0 | 61.1153
8353 | 0 | 0 | 61.0166
8354 | 0 | 0 | 60.9181
8355 | 0 | 0 | 60.8199
8356 | 0 | 0 | 60.7219
8357 | 0 | 0 | 60.6241
8358 | 12.4365 | 13.3569 | 60.2795
8359 | 1.2774 | 0 | 60.2329
8360 | 1.6617 | 0 | 58.8818
8361 | 0 | 0 | 58.6824
8362 | 0 | 0 | 58.5894
8363 | 0 | 0 | 58.4966
8364 | 0.80862 | 6.4541 | 61.5885
8365 | 0 | 0 | 62.6445
8366 | 0 | 0 | 62.5422
8367 | 0 | 0 | 62.4402
8368 | 0 | 0 | 62.3384
8369 | 0 | 0 | 62.2368
8370 | 6.2642 | 6.6974 | 60.678
8371 | 12.2337 | 13.166 | 60.439
8372 | 0 | 0 | 62.9757
8373 | 1.321 | 0 | 61.9393
8374 | 0 | 0 | 61.7542
8375 | 0 | 0 | 61.654
8376 | 0 | 0 | 61.5541
8377 | 0 | 0 | 61.4544
8378 | 0 | 0 | 61.3549
8379 | 0 | 0 | 61.2556
8380 | 0 | 0 | 61.1566
8381 | 0 | 0 | 61.0578
8382 | 12.5505 | 13.1926 | 60.5674
8383 | 1.2852 | 0 | 60.4452
8384 | 1.6719 | 0 | 59.0859
8385 | 0 | 0 | 58.8853
8386 | 0 | 0 | 58.7919
8387 | 0 | 0 | 58.6986
8388 | 0.81356 | 6.3655 | 60.9198
8389 | 0 | 0 | 62.776
8390 | 0 | 0 | 62.6734
8391 | 0 | 0 | 62.571
8392 | 0 | 0 | 62.4689
8393 | 0 | 0 | 62.367
8394 | 6.2911 | 6.6445 | 60.775
8395 | 12.2708 | 13.1486 | 60.4797
8396 | 0 | 0 | 63.0018
8397 | 1.324 | 0 | 61.9633
8398 | 0 | 0 | 61.778
8399 | 0 | 0 | 61.6777
8400 | 0 | 0 | 61.5777
8401 | 0 | 0 | 61.478
8402 | 0 | 0 | 61.3784
8403 | 0 | 0 | 61.2791
8404 | 0 | 0 | 61.18
8405 | 0 | 0 | 61.0812
8406 | 12.5771 | 13.1907 | 60.5742
8407 | 1.2876 | 0 | 60.4449
8408 | 1.675 | 0 | 59.0832
8409 | 0 | 0 | 58.8825
8410 | 0 | 0 | 58.789
8411 | 0 | 0 | 58.6958
8412 | 0.81507 | 6.3674 | 60.9168
8413 | 0 | 0 | 62.7735
8414 | 0 | 0 | 62.6709
8415 | 0 | 0 | 62.5685
8416 | 0 | 0 | 62.4664
8417 | 0 | 0 | 62.3646
8418 | 6.302 | 6.6498 | 60.7679
8419 | 12.2907 | 13.1597 | 60.4651
8420 | 0 | 0 | 62.9883
8421 | 1.326 | 0 | 61.9484
8422 | 0 | 0 | 61.763
8423 | 0 | 0 | 61.6628
8424 | 0 | 0 | 61.5628
8425 | 0 | 0 | 61.463
8426 | 0 | 0 | 61.3635
8427 | 0 | 0 | 61.2643
8428 | 0 | 0 | 61.1652
8429 | 0 | 0 | 61.0664
8430 | 12.5954 | 13.2037 | 60.555
8431 | 1.2894 | 0 | 60.4248
8432 | 1.6774 | 0 | 59.0615
8433 | 0 | 0 | 58.8606
8434 | 0 | 0 | 58.7672
8435 | 0 | 0 | 58.674
8436 | 0.81625 | 6.371 | 61.712
8437 | 0 | 0 | 62.7517
8438 | 0 | 0 | 62.6492
8439 | 0 | 0 | 62.5469
8440 | 0 | 0 | 62.4448
8441 | 0 | 0 | 62.343
8442 | 6.3105 | 6.6634 | 60.7459
8443 | 12.3078 | 13.1747 | 60.4428
8444 | 0 | 0 | 62.9691
8445 | 1.3278 | 0 | 61.928
8446 | 0 | 0 | 61.7425
8447 | 0 | 0 | 61.6423
8448 | 0 | 0 | 61.5424
8449 | 0 | 0 | 61.4427
8450 | 0 | 0 | 61.3433
8451 | 0 | 0 | 61.244
8452 | 0 | 0 | 61.145
8453 | 0 | 0 | 61.0463
8454 | 12.6122 | 13.2188 | 60.5322
8455 | 1.2911 | 0 | 60.4022
8456 | 1.6796 | 0 | 59.0372
8457 | 0 | 0 | 58.8362
8458 | 0 | 0 | 58.7429
8459 | 0 | 0 | 58.6497
8460 | 0.81736 | 6.3832 | 61.694
8461 | 0 | 0 | 62.736
8462 | 0 | 0 | 62.6335
8463 | 0 | 0 | 62.5313
8464 | 0 | 0 | 62.4292
8465 | 0 | 0 | 62.3275
8466 | 6.3196 | 6.6743 | 60.7287
8467 | 12.3255 | 13.1883 | 60.423
8468 | 0 | 0 | 62.9519
8469 | 1.3296 | 0 | 61.9095
8470 | 0 | 0 | 61.724
8471 | 0 | 0 | 61.6238
8472 | 0 | 0 | 61.524
8473 | 0 | 0 | 61.4243
8474 | 0 | 0 | 61.3249
8475 | 0 | 0 | 61.2257
8476 | 0 | 0 | 61.1268
8477 | 0 | 0 | 61.028
8478 | 12.6293 | 13.233 | 60.5108
8479 | 1.2929 | 0 | 60.3807
8480 | 1.6819 | 0 | 59.014
8481 | 0 | 0 | 58.8129
8482 | 0 | 0 | 58.7196
8483 | 0 | 0 | 58.6266
8484 | 0.81848 | 6.3948 | 61.6769
8485 | 0 | 0 | 62.721
8486 | 0 | 0 | 62.6185
8487 | 0 | 0 | 62.5163
8488 | 0 | 0 | 62.4143
8489 | 0 | 0 | 62.3126
8490 | 6.3286 | 6.6849 | 60.7121
8491 | 12.3431 | 13.2017 | 60.4037
8492 | 0 | 0 | 62.935
8493 | 1.3315 | 0 | 61.8914
8494 | 0 | 0 | 61.7058
8495 | 0 | 0 | 61.6057
8496 | 0 | 0 | 61.5059
8497 | 0 | 0 | 61.4062
8498 | 0 | 0 | 61.3069
8499 | 0 | 0 | 61.2077
8500 | 0 | 0 | 61.1088
8501 | 0 | 0 | 61.0101
8502 | 12.6461 | 13.247 | 60.4897
8503 | 1.2946 | 0 | 60.3595
8504 | 1.6841 | 0 | 58.9912
8505 | 0 | 0 | 58.79
8506 | 0 | 0 | 58.6968
8507 | 0 | 0 | 58.6038
8508 | 0.81959 | 6.4063 | 61.66
8509 | 0 | 0 | 62.7062
8510 | 0 | 0 | 62.6038
8511 | 0 | 0 | 62.5016
8512 | 0 | 0 | 62.3996
8513 | 0 | 0 | 62.2979
8514 | 6.3375 | 6.6953 | 60.6957
8515 | 12.3605 | 13.2149 | 60.3847
8516 | 0 | 0 | 62.9184
8517 | 1.3333 | 0 | 61.8735
8518 | 0 | 0 | 61.6878
8519 | 0 | 0 | 61.5878
8520 | 0 | 0 | 61.488
8521 | 0 | 0 | 61.3884
8522 | 0 | 0 | 61.2891
8523 | 0 | 0 | 61.19
8524 | 0 | 0 | 61.0911
8525 | 0 | 0 | 60.9925
8526 | 12.6628 | 13.2609 | 60.4689
8527 | 1.2963 | 0 | 60.3385
8528 | 1.6864 | 0 | 58.9686
8529 | 0 | 0 | 58.7674
8530 | 0 | 0 | 58.6742
8531 | 0 | 0 | 58.5812
8532 | 0.82068 | 6.4176 | 61.6433
8533 | 0 | 0 | 62.6916
8534 | 0 | 0 | 62.5892
8535 | 0 | 0 | 62.487
8536 | 0 | 0 | 62.3851
8537 | 0 | 0 | 62.2835
8538 | 6.3464 | 6.7056 | 60.6794
8539 | 12.3776 | 13.2279 | 60.3659
8540 | 0 | 0 | 62.9019
8541 | 1.335 | 0 | 61.8559
8542 | 0 | 0 | 61.6701
8543 | 0 | 0 | 61.5701
8544 | 0 | 0 | 61.4703
8545 | 0 | 0 | 61.3708
8546 | 0 | 0 | 61.2715
8547 | 0 | 0 | 61.1725
8548 | 0 | 0 | 61.0736
8549 | 0 | 0 | 60.975
8550 | 12.6792 | 13.2745 | 60.4484
8551 | 1.298 | 0 | 60.3179
8552 | 1.6886 | 0 | 58.9463
8553 | 0 | 0 | 58.745
8554 | 0 | 0 | 58.6519
8555 | 0 | 0 | 58.559
8556 | 0.82175 | 6.4288 | 61.6268
8557 | 0 | 0 | 62.6772
8558 | 0 | 0 | 62.5748
8559 | 0 | 0 | 62.4727
8560 | 0 | 0 | 62.3708
8561 | 0 | 0 | 62.2692
8562 | 6.3551 | 6.7157 | 60.6634
8563 | 12.3945 | 13.2408 | 60.3473
8564 | 0 | 0 | 62.8857
8565 | 1.3368 | 0 | 61.8384
8566 | 0 | 0 | 61.6526
8567 | 0 | 0 | 61.5526
8568 | 0 | 0 | 61.4529
8569 | 0 | 0 | 61.3534
8570 | 0 | 0 | 61.2542
8571 | 0 | 0 | 61.1552
8572 | 0 | 0 | 61.0564
8573 | 0 | 0 | 60.9578
8574 | 12.6954 | 13.288 | 60.4281
8575 | 1.2996 | 0 | 60.2975
8576 | 1.6907 | 0 | 58.9244
8577 | 0 | 0 | 58.723
8578 | 0 | 0 | 58.6299
8579 | 0 | 0 | 58.537
8580 | 0.82282 | 6.4398 | 61.6106
8581 | 0 | 0 | 62.6629
8582 | 0 | 0 | 62.5606
8583 | 0 | 0 | 62.4585
8584 | 0 | 0 | 62.3567
8585 | 0 | 0 | 62.2551
8586 | 6.3637 | 6.7257 | 60.6477
8587 | 12.4112 | 13.2535 | 60.329
8588 | 0 | 0 | 62.8697
8589 | 1.3385 | 0 | 61.8212
8590 | 0 | 0 | 61.6353
8591 | 0 | 0 | 61.5354
8592 | 0 | 0 | 61.4357
8593 | 0 | 0 | 61.3363
8594 | 0 | 0 | 61.2371
8595 | 0 | 0 | 61.1381
8596 | 0 | 0 | 61.0394
8597 | 0 | 0 | 60.9408
8598 | 12.7114 | 13.3013 | 60.4082
8599 | 1.3013 | 0 | 60.2773
8600 | 1.6928 | 0 | 58.9027
8601 | 0 | 0 | 58.7012
8602 | 0 | 0 | 58.6082
8603 | 0 | 0 | 58.5154
8604 | 0.82386 | 6.4507 | 61.5945
8605 | 0 | 0 | 62.6489
8606 | 0 | 0 | 62.5466
8607 | 0 | 0 | 62.4445
8608 | 0 | 0 | 62.3427
8609 | 0 | 0 | 62.2412
8610 | 6.3721 | 6.7356 | 60.6321
8611 | 12.4277 | 13.266 | 60.311
8612 | 0 | 0 | 62.8539
8613 | 1.3403 | 0 | 61.8043
8614 | 0 | 0 | 61.6183
8615 | 0 | 0 | 61.5184
8616 | 0 | 0 | 61.4188
8617 | 0 | 0 | 61.3194
8618 | 0 | 0 | 61.2202
8619 | 0 | 0 | 61.1213
8620 | 0 | 0 | 61.0226
8621 | 0 | 0 | 60.9241
8622 | 12.7271 | 13.3144 | 60.3885
8623 | 1.3029 | 0 | 60.2575
8624 | 1.6949 | 0 | 58.8814
8625 | 0 | 0 | 58.6798
8626 | 0 | 0 | 58.5868
8627 | 0 | 0 | 58.494
8628 | 0.8249 | 6.4614 | 61.5787
8629 | 0 | 0 | 62.635
8630 | 0 | 0 | 62.5328
8631 | 0 | 0 | 62.4308
8632 | 0 | 0 | 62.329
8633 | 0 | 0 | 62.2274
8634 | 6.3805 | 6.7454 | 60.6167
8635 | 12.4439 | 13.2784 | 60.2932
8636 | 0 | 0 | 62.8383
8637 | 1.3419 | 0 | 61.7876
8638 | 0 | 0 | 61.6015
8639 | 0 | 0 | 61.5017
8640 | 0 | 0 | 61.4021
8641 | 0 | 0 | 61.3027
8642 | 0 | 0 | 61.2036
8643 | 0 | 0 | 61.1047
8644 | 0 | 0 | 61.006
8645 | 0 | 0 | 60.9076
8646 | 12.7426 | 13.3274 | 60.369
8647 | 1.3044 | 0 | 60.238
8648 | 1.697 | 0 | 58.8603
8649 | 0 | 0 | 58.6587
8650 | 0 | 0 | 58.5657
8651 | 0 | 0 | 58.473
8652 | 0.82591 | 6.472 | 61.5631
8653 | 0 | 0 | 62.6214
8654 | 0 | 0 | 62.5192
8655 | 0 | 0 | 62.4172
8656 | 0 | 0 | 62.3154
8657 | 0 | 0 | 62.2139
8658 | 6.3887 | 6.755 | 60.6016
8659 | 12.4599 | 13.2905 | 60.2756
8660 | 0 | 0 | 62.823
8661 | 1.3436 | 0 | 61.7711
8662 | 0 | 0 | 61.585
8663 | 0 | 0 | 61.4852
8664 | 0 | 0 | 61.3856
8665 | 0 | 0 | 61.2863
8666 | 0 | 0 | 61.1872
8667 | 0 | 0 | 61.0883
8668 | 0 | 0 | 60.9897
8669 | 0 | 0 | 60.8913
8670 | 12.7579 | 13.3401 | 60.3499
8671 | 1.306 | 0 | 60.2187
8672 | 1.699 | 0 | 58.8396
8673 | 0 | 0 | 58.6379
8674 | 0 | 0 | 58.545
8675 | 0 | 0 | 58.4523
8676 | 0.82691 | 6.4824 | 61.5478
8677 | 0 | 0 | 62.608
8678 | 0 | 0 | 62.5058
8679 | 0 | 0 | 62.4038
8680 | 0 | 0 | 62.3021
8681 | 0 | 0 | 62.2006
8682 | 6.3968 | 6.7644 | 60.5867
8683 | 12.4756 | 13.3025 | 60.2584
8684 | 0 | 0 | 62.8079
8685 | 1.3452 | 0 | 61.7549
8686 | 0 | 0 | 61.5687
8687 | 0 | 0 | 61.4689
8688 | 0 | 0 | 61.3694
8689 | 0 | 0 | 61.2701
8690 | 0 | 0 | 61.1711
8691 | 0 | 0 | 61.0722
8692 | 0 | 0 | 60.9736
8693 | 0 | 0 | 60.8753
8694 | 12.7729 | 13.3526 | 60.3311
8695 | 1.3075 | 0 | 60.1998
8696 | 1.701 | 0 | 58.8192
8697 | 0 | 0 | 58.6174
8698 | 0 | 0 | 58.5245
8699 | 0 | 0 | 58.4319
8700 | 0.8279 | 6.4926 | 61.5327
8701 | 0 | 0 | 62.5948
8702 | 0 | 0 | 62.4926
8703 | 0 | 0 | 62.3907
8704 | 0 | 0 | 62.289
8705 | 0 | 0 | 62.1875
8706 | 6.4047 | 6.7737 | 60.5721
8707 | 12.4911 | 13.3143 | 60.2414
8708 | 0 | 0 | 62.793
8709 | 1.3469 | 0 | 61.7389
8710 | 0 | 0 | 61.5527
8711 | 0 | 0 | 61.4529
8712 | 0 | 0 | 61.3535
8713 | 0 | 0 | 61.2542
8714 | 0 | 0 | 61.1552
8715 | 0 | 0 | 61.0564
8716 | 0 | 0 | 60.9578
8717 | 0 | 0 | 60.8595
8718 | 12.7877 | 13.3649 | 60.3126
8719 | 1.3091 | 0 | 60.1811
8720 | 1.703 | 0 | 58.7991
8721 | 0 | 0 | 58.5972
8722 | 0 | 0 | 58.5044
8723 | 0 | 0 | 58.4119
8724 | 0.82887 | 6.5027 | 61.5178
8725 | 0 | 0 | 62.5817
8726 | 0 | 0 | 62.4796
8727 | 0 | 0 | 62.3777
8728 | 0 | 0 | 62.2761
8729 | 0 | 0 | 62.1746
8730 | 6.4126 | 6.7829 | 60.5577
8731 | 12.5064 | 13.3259 | 60.2246
8732 | 0 | 0 | 62.7784
8733 | 1.3484 | 0 | 61.7232
8734 | 0 | 0 | 61.5369
8735 | 0 | 0 | 61.4372
8736 | 0 | 0 | 61.3378
8737 | 0 | 0 | 61.2385
8738 | 0 | 0 | 61.1396
8739 | 0 | 0 | 61.0408
8740 | 0 | 0 | 60.9423
8741 | 0 | 0 | 60.844
8742 | 12.8022 | 13.3771 | 60.2944
8743 | 1.3105 | 0 | 60.1628
8744 | 1.7049 | 0 | 58.7794
8745 | 0 | 0 | 58.5774
8746 | 0 | 0 | 58.4847
8747 | 0 | 0 | 58.3922
8748 | 0.82982 | 6.5126 | 61.5032
8749 | 0 | 0 | 62.569
8750 | 0 | 0 | 62.4669
8751 | 0 | 0 | 62.365
8752 | 0 | 0 | 62.2634
8753 | 0 | 0 | 62.162
8754 | 6.4203 | 6.7919 | 60.5435
8755 | 12.5213 | 13.3372 | 60.2082
8756 | 0 | 0 | 62.764
8757 | 1.35 | 0 | 61.7077
8758 | 0 | 0 | 61.5213
8759 | 0 | 0 | 61.4217

## Comparison + Tolerances
hour | CogenS | EnergyPlus | difference
0 | 0.12485 | 0
1 | 0.12485 | 0
2 | 0.12485 | 0
3 | 0.12485 | 0
4 | 0.12485 | 0
5 | 0.12485 | 0
6 | 12.6506 | 13.6671
7 | 1.4142 | 0
8 | 1.8023 | 6.4214
9 | 0.12485 | 0
10 | 0.12485 | 0
11 | 0.12485 | 0
12 | 1.0233 | 0
13 | 0.12485 | 0
14 | 0.12485 | 0
15 | 0.12485 | 0
16 | 0.12485 | 0
17 | 0.12485 | 0
18 | 6.5454 | 6.844
19 | 13.046 | 13.1124
20 | 0.12485 | 0
21 | 1.4402 | 0
22 | 0.12485 | 0
23 | 0.12485 | 0
24 | 0.12485 | 0
25 | 0.12485 | 0
26 | 0.12485 | 0
27 | 0.12485 | 0
28 | 0.12485 | 0
29 | 0.12485 | 0
30 | 12.6582 | 13.7037
31 | 1.4152 | 0
32 | 1.8037 | 6.4365
33 | 0.12485 | 0
34 | 0.12485 | 0
35 | 0.12485 | 0
36 | 1.0242 | 0
37 | 0.12485 | 0
38 | 0.12485 | 0
39 | 0.12485 | 0
40 | 0.12485 | 0
41 | 0.12485 | 0
42 | 6.5516 | 6.8458
43 | 13.0575 | 13.1275
44 | 0.12485 | 0
45 | 1.4415 | 0
46 | 0.12485 | 0
47 | 0.12485 | 0
48 | 0.12485 | 0
49 | 0.12485 | 0
50 | 0.12485 | 0
51 | 0.12485 | 0
52 | 0.12485 | 0
53 | 0.12485 | 0
54 | 12.6696 | 13.706
55 | 1.4163 | 0
56 | 1.805 | 6.4508
57 | 0.12485 | 0
58 | 0.12485 | 0
59 | 0.12485 | 0
60 | 1.025 | 0
61 | 0.12485 | 0
62 | 0.12485 | 0
63 | 0.12485 | 0
64 | 0.12485 | 0
65 | 0.12485 | 0
66 | 6.5577 | 6.8475
67 | 13.0689 | 13.1421
68 | 0.12485 | 0
69 | 1.4427 | 0
70 | 0.12485 | 0
71 | 0.12485 | 0
72 | 0.12485 | 0
73 | 0.12485 | 0
74 | 0.12485 | 0
75 | 0.12485 | 0
76 | 0.12485 | 0
77 | 0.12485 | 0
78 | 12.6808 | 13.7082
79 | 1.4173 | 0
80 | 1.8064 | 6.4647
81 | 0.12485 | 0
82 | 0.12485 | 0
83 | 0.12485 | 0
84 | 1.0259 | 0
85 | 0.12485 | 0
86 | 0.12485 | 0
87 | 0.12485 | 0
88 | 0.12485 | 0
89 | 0.12485 | 0
90 | 6.5637 | 6.8492
91 | 13.0801 | 13.1564
92 | 0.12485 | 0
93 | 1.444 | 0
94 | 0.12485 | 0
95 | 0.12485 | 0
96 | 0.12485 | 0
97 | 0.12485 | 0
98 | 0.12485 | 0
99 | 0.12485 | 0
100 | 0.12485 | 0
101 | 0.12485 | 0
102 | 12.6918 | 13.7103
103 | 1.4183 | 0
104 | 1.8077 | 6.4783
105 | 0.12485 | 0
106 | 0.12485 | 0
107 | 0.12485 | 0
108 | 1.0267 | 0
109 | 0.12485 | 0
110 | 0.12485 | 0
111 | 0.12485 | 0
112 | 0.12485 | 0
113 | 0.12485 | 0
114 | 6.5697 | 6.8508
115 | 13.0911 | 13.1703
116 | 0.12485 | 0
117 | 1.4452 | 0
118 | 0.12485 | 0
119 | 0.12485 | 0
120 | 0.12485 | 0
121 | 0.12485 | 0
122 | 0.12485 | 0
123 | 0.12485 | 0
124 | 0.12485 | 0
125 | 0.12485 | 0
126 | 12.7026 | 13.7125
127 | 1.4193 | 0
128 | 1.809 | 6.4916
129 | 0.12485 | 0
130 | 0.12485 | 0
131 | 0.12485 | 0
132 | 1.0275 | 0
133 | 0.12485 | 0
134 | 0.12485 | 0
135 | 0.12485 | 0
136 | 0.12485 | 0
137 | 0.12485 | 0
138 | 6.5755 | 6.8524
139 | 13.1018 | 13.184
140 | 0.12485 | 0
141 | 1.4463 | 0
142 | 0.12485 | 0
143 | 0.12485 | 0
144 | 0.12485 | 0
145 | 0.12485 | 0
146 | 0.12485 | 0
147 | 0.12485 | 0
148 | 0.12485 | 0
149 | 0.12485 | 0
150 | 12.7131 | 13.7145
151 | 1.4203 | 0
152 | 1.8103 | 6.5046
153 | 0.12485 | 0
154 | 0.12485 | 0
155 | 0.12485 | 0
156 | 1.0283 | 0
157 | 0.12485 | 0
158 | 0.12485 | 0
159 | 0.12485 | 0
160 | 0.12485 | 0
161 | 0.12485 | 0
162 | 6.5811 | 6.854
163 | 13.1123 | 13.1973
164 | 0.12485 | 0
165 | 1.4475 | 0
166 | 0.12485 | 0
167 | 0.12485 | 0
168 | 0.12485 | 0
169 | 0.12485 | 0
170 | 0.12485 | 0
171 | 0.12485 | 0
172 | 0.12485 | 0
173 | 0.12485 | 0
174 | 12.7234 | 13.7166
175 | 1.4212 | 0
176 | 1.8115 | 6.5173
177 | 0.12485 | 0
178 | 0.12485 | 0
179 | 0.12485 | 0
180 | 1.0291 | 0
181 | 0.12485 | 0
182 | 0.12485 | 0
183 | 0.12485 | 0
184 | 0.12485 | 0
185 | 0.12485 | 0
186 | 6.5867 | 6.8555
187 | 13.1226 | 13.2104
188 | 0.12485 | 0
189 | 1.4486 | 0
190 | 0.12485 | 0
191 | 0.12485 | 0
192 | 0.12485 | 0
193 | 0.12485 | 0
194 | 0.12485 | 0
195 | 0.12485 | 0
196 | 0.12485 | 0
197 | 0.12485 | 0
198 | 12.7335 | 13.7185
199 | 1.4221 | 0
200 | 1.8127 | 6.5297
201 | 0.12485 | 0
202 | 0.12485 | 0
203 | 0.12485 | 0
204 | 1.0298 | 0
205 | 0.12485 | 0
206 | 0.12485 | 0
207 | 0.12485 | 0
208 | 0.12485 | 0
209 | 0.12485 | 0
210 | 6.5921 | 6.857
211 | 13.1327 | 13.2231
212 | 0.12485 | 0
213 | 1.4497 | 0
214 | 0.12485 | 0
215 | 0.12485 | 0
216 | 0.12485 | 0
217 | 0.12485 | 0
218 | 0.12485 | 0
219 | 0.12485 | 0
220 | 0.12485 | 0
221 | 0.12485 | 0
222 | 12.7433 | 19.0693
223 | 1.5262 | 0
224 | 1.9478 | 0
225 | 0.12485 | 0
226 | 0.12485 | 0
227 | 0.12485 | 0
228 | 1.012 | 0
229 | 0.12485 | 0
230 | 0.12485 | 0
231 | 0.12485 | 0
232 | 0.12485 | 0
233 | 0.12485 | 0
234 | 6.4718 | 7.077
235 | 12.9635 | 13.4335
236 | 0.12485 | 0
237 | 1.4378 | 0
238 | 0.12485 | 0
239 | 0.12485 | 0
240 | 0.12485 | 0
241 | 0.12485 | 0
242 | 0.12485 | 0
243 | 0.12485 | 0
244 | 0.12485 | 0
245 | 0.12485 | 0
246 | 12.6403 | 19.265
247 | 1.5205 | 0
248 | 1.9405 | 0
249 | 0.12485 | 0
250 | 0.12485 | 0
251 | 0.12485 | 0
252 | 1.0084 | 0
253 | 0.12485 | 0
254 | 0.12485 | 0
255 | 0.12485 | 0
256 | 0.12485 | 0
257 | 0.12485 | 0
258 | 6.6578 | 6.8512
259 | 12.8624 | 13.6298
260 | 0.12485 | 0
261 | 1.4305 | 0
262 | 0.12485 | 0
263 | 0.12485 | 0
264 | 0.12485 | 0
265 | 0.12485 | 0
266 | 0.12485 | 0
267 | 0.12485 | 0
268 | 0.12485 | 0
269 | 0.12485 | 0
270 | 12.5753 | 19.3856
271 | 1.517 | 0
272 | 1.936 | 0
273 | 0.12485 | 0
274 | 0.12485 | 0
275 | 0.12485 | 0
276 | 1.0063 | 0
277 | 0.12485 | 0
278 | 0.12485 | 0
279 | 0.12485 | 0
280 | 0.12485 | 0
281 | 0.12485 | 0
282 | 6.6455 | 6.9087
283 | 12.8462 | 13.6303
284 | 0.12485 | 0
285 | 1.4291 | 0
286 | 0.12485 | 0
287 | 0.12485 | 0
288 | 0.12485 | 0
289 | 0.12485 | 0
290 | 0.12485 | 0
291 | 0.12485 | 0
292 | 0.12485 | 0
293 | 0.12485 | 0
294 | 12.5624 | 19.4294
295 | 1.5167 | 0
296 | 1.9356 | 0
297 | 0.12485 | 0
298 | 0.12485 | 0
299 | 0.12485 | 0
300 | 1.0061 | 0
301 | 0.12485 | 0
302 | 0.12485 | 0
303 | 0.12485 | 0
304 | 0.12485 | 0
305 | 0.12485 | 0
306 | 6.6446 | 6.9123
307 | 12.8448 | 13.6299
308 | 0.12485 | 0
309 | 1.4289 | 0
310 | 0.12485 | 0
311 | 0.12485 | 0
312 | 0.12485 | 0
313 | 0.12485 | 0
314 | 0.12485 | 0
315 | 0.12485 | 0
316 | 0.12485 | 0
317 | 0.12485 | 0
318 | 12.5612 | 19.4554
319 | 1.5171 | 0
320 | 1.9361 | 0
321 | 0.12485 | 0
322 | 0.12485 | 0
323 | 0.12485 | 0
324 | 1.0063 | 0
325 | 0.12485 | 0
326 | 0.12485 | 0
327 | 0.12485 | 0
328 | 0.12485 | 0
329 | 0.12485 | 0
330 | 6.6466 | 6.9146
331 | 12.8486 | 13.6301
332 | 0.12485 | 0
333 | 1.4293 | 0
334 | 0.12485 | 0
335 | 0.12485 | 0
336 | 0.12485 | 0
337 | 0.12485 | 0
338 | 0.12485 | 0
339 | 0.12485 | 0
340 | 0.12485 | 0
341 | 0.12485 | 0
342 | 12.5642 | 19.4745
343 | 1.5178 | 0
344 | 1.9369 | 0
345 | 0.12485 | 0
346 | 0.12485 | 0
347 | 0.12485 | 0
348 | 1.0068 | 0
349 | 0.12485 | 0
350 | 0.12485 | 0
351 | 0.12485 | 0
352 | 0.12485 | 0
353 | 0.12485 | 0
354 | 6.6496 | 6.9165
355 | 12.854 | 13.6306
356 | 0.12485 | 0
357 | 1.4298 | 0
358 | 0.12485 | 0
359 | 0.12485 | 0
360 | 0.12485 | 0
361 | 0.12485 | 0
362 | 0.12485 | 0
363 | 0.12485 | 0
364 | 0.12485 | 0
365 | 0.12485 | 0
366 | 12.5685 | 19.491
367 | 1.5185 | 0
368 | 1.9378 | 0
369 | 0.12485 | 0
370 | 0.12485 | 0
371 | 0.12485 | 0
372 | 1.0072 | 0
373 | 0.12485 | 0
374 | 0.12485 | 0
375 | 0.12485 | 0
376 | 0.12485 | 0
377 | 0.12485 | 0
378 | 6.653 | 6.9182
379 | 12.86 | 13.6311
380 | 0.12485 | 0
381 | 1.4303 | 0
382 | 0.12485 | 0
383 | 0.12485 | 0
384 | 0.12485 | 0
385 | 0.12485 | 0
386 | 0.12485 | 0
387 | 0.12485 | 0
388 | 0.12485 | 0
389 | 0.12485 | 0
390 | 12.5732 | 19.5061
391 | 1.5192 | 0
392 | 1.9388 | 0
393 | 0.12485 | 0
394 | 0.12485 | 0
395 | 0.12485 | 0
396 | 1.0077 | 0
397 | 0.12485 | 0
398 | 0.12485 | 0
399 | 0.12485 | 0
400 | 0.12485 | 0
401 | 0.12485 | 0
402 | 6.6563 | 6.9197
403 | 12.866 | 13.6316
404 | 0.12485 | 0
405 | 1.4309 | 0
406 | 0.12485 | 0
407 | 0.12485 | 0
408 | 0.12485 | 0
409 | 0.12485 | 0
410 | 0.12485 | 0
411 | 0.12485 | 0
412 | 0.12485 | 0
413 | 0.12485 | 0
414 | 12.578 | 19.5205
415 | 1.5199 | 0
416 | 1.9397 | 0
417 | 0.12485 | 0
418 | 0.12485 | 0
419 | 0.12485 | 0
420 | 1.0081 | 0
421 | 0.12485 | 0
422 | 0.12485 | 0
423 | 0.12485 | 0
424 | 0.12485 | 0
425 | 0.12485 | 0
426 | 6.6597 | 6.9212
427 | 12.872 | 18.985
428 | 0.12485 | 0
429 | 1.5344 | 0
430 | 0.12485 | 0
431 | 0.12485 | 0
432 | 0.12485 | 0
433 | 0.12485 | 0
434 | 0.12485 | 0
435 | 0.12485 | 0
436 | 0.12485 | 0
437 | 0.12485 | 0
438 | 12.8448 | 13.6744
439 | 1.5011 | 0
440 | 1.9153 | 0
441 | 0.12485 | 0
442 | 0.12485 | 0
443 | 0.12485 | 0
444 | 0.99631 | 0
445 | 0.12485 | 0
446 | 0.12485 | 0
447 | 0.12485 | 0
448 | 0.12485 | 0
449 | 0.12485 | 0
450 | 6.5788 | 6.9547
451 | 12.7341 | 19.2071
452 | 0.12485 | 0
453 | 1.5264 | 0
454 | 0.12485 | 0
455 | 0.12485 | 0
456 | 0.12485 | 0
457 | 0.12485 | 0
458 | 0.12485 | 0
459 | 0.12485 | 0
460 | 0.12485 | 0
461 | 0.12485 | 0
462 | 12.7752 | 13.6856
463 | 1.495 | 0
464 | 1.9074 | 0
465 | 0.12485 | 0
466 | 0.12485 | 0
467 | 0.12485 | 0
468 | 0.99249 | 0
469 | 0.12485 | 0
470 | 0.12485 | 0
471 | 0.12485 | 0
472 | 0.12485 | 0
473 | 0.12485 | 0
474 | 6.5523 | 6.9577
475 | 12.6883 | 19.2947
476 | 0.12485 | 0
477 | 1.524 | 0
478 | 0.12485 | 0
479 | 0.12485 | 0
480 | 0.12485 | 0
481 | 0.12485 | 0
482 | 0.12485 | 0
483 | 0.12485 | 0
484 | 0.12485 | 0
485 | 0.12485 | 0
486 | 12.7543 | 13.6905
487 | 1.4932 | 0
488 | 1.905 | 0
489 | 0.12485 | 0
490 | 0.12485 | 0
491 | 0.12485 | 0
492 | 0.99136 | 0
493 | 0.12485 | 0
494 | 0.12485 | 0
495 | 0.12485 | 0
496 | 0.12485 | 0
497 | 0.12485 | 0
498 | 6.5444 | 6.9577
499 | 12.6747 | 19.334
500 | 0.12485 | 0
501 | 1.5235 | 0
502 | 0.12485 | 0
503 | 0.12485 | 0
504 | 0.12485 | 0
505 | 0.12485 | 0
506 | 0.12485 | 0
507 | 0.12485 | 0
508 | 0.12485 | 0
509 | 0.12485 | 0
510 | 13.1601 | 13.7279
511 | 1.4856 | 0
512 | 1.8951 | 0
513 | 0.12485 | 0
514 | 0.12485 | 0
515 | 0.12485 | 0
516 | 0.98658 | 0
517 | 0.12485 | 0
518 | 0.12485 | 0
519 | 0.12485 | 6.3451
520 | 0.12485 | 0
521 | 0.12485 | 0
522 | 6.7597 | 6.6444
523 | 12.9915 | 13.3844
524 | 0.12485 | 0
525 | 1.5067 | 0
526 | 0.12485 | 0
527 | 0.12485 | 0
528 | 0.12485 | 0
529 | 0.12485 | 0
530 | 0.12485 | 0
531 | 0.12485 | 0
532 | 0.12485 | 0
533 | 0.12485 | 0
534 | 13.2252 | 13.5136
535 | 1.4642 | 0
536 | 1.8673 | 0
537 | 0.12485 | 0
538 | 0.12485 | 0
539 | 0.12485 | 0
540 | 0.97313 | 6.6408
541 | 0.12485 | 0
542 | 0.12485 | 0
543 | 0.12485 | 0
544 | 0.12485 | 0
545 | 0.12485 | 0
546 | 6.6883 | 6.8319
547 | 12.9017 | 13.5154
548 | 0.12485 | 0
549 | 1.5011 | 0
550 | 0.12485 | 0
551 | 0.12485 | 0
552 | 0.12485 | 0
553 | 0.12485 | 0
554 | 0.12485 | 0
555 | 0.12485 | 0
556 | 0.12485 | 0
557 | 0.12485 | 0
558 | 13.1797 | 13.5898
559 | 1.4612 | 0
560 | 1.8635 | 0
561 | 0.12485 | 0
562 | 0.12485 | 0
563 | 0.12485 | 6.3659
564 | 1.0532 | 0
565 | 0.12485 | 0
566 | 0.12485 | 0
567 | 0.12485 | 0
568 | 0.12485 | 0
569 | 0.12485 | 0
570 | 6.6417 | 6.9014
571 | 12.8336 | 13.5106
572 | 0.12485 | 0
573 | 1.495 | 0
574 | 0.12485 | 0
575 | 0.12485 | 0
576 | 0.12485 | 0
577 | 0.12485 | 0
578 | 0.12485 | 0
579 | 0.12485 | 0
580 | 0.12485 | 0
581 | 0.12485 | 0
582 | 13.1251 | 13.5872
583 | 1.4562 | 0
584 | 1.8571 | 0
585 | 0.12485 | 6.3518
586 | 0.12485 | 0
587 | 0.12485 | 0
588 | 1.0494 | 0
589 | 0.12485 | 0
590 | 0.12485 | 0
591 | 0.12485 | 0
592 | 0.12485 | 0
593 | 0.12485 | 0
594 | 6.7302 | 6.8435
595 | 13.3695 | 13.2012
596 | 0.12485 | 0
597 | 1.4706 | 0
598 | 0.12485 | 0
599 | 0.12485 | 0
600 | 0.12485 | 0
601 | 0.12485 | 0
602 | 0.12485 | 0
603 | 0.12485 | 0
604 | 0.12485 | 0
605 | 0.12485 | 0
606 | 12.9254 | 19.1331
607 | 1.5436 | 0
608 | 1.9706 | 0
609 | 0.12485 | 0
610 | 0.12485 | 0
611 | 0.12485 | 0
612 | 1.0232 | 0
613 | 0.12485 | 0
614 | 0.12485 | 0
615 | 0.12485 | 0
616 | 0.12485 | 0
617 | 0.12485 | 0
618 | 6.5516 | 7.0917
619 | 13.1046 | 13.4455
620 | 0.12485 | 0
621 | 1.4507 | 0
622 | 0.12485 | 0
623 | 0.12485 | 0
624 | 0.12485 | 0
625 | 0.12485 | 0
626 | 0.12485 | 0
627 | 0.12485 | 0
628 | 0.12485 | 0
629 | 0.12485 | 0
630 | 12.7517 | 19.4238
631 | 1.5335 | 0
632 | 1.9574 | 0
633 | 0.12485 | 0
634 | 0.12485 | 0
635 | 0.12485 | 0
636 | 1.0168 | 0
637 | 0.12485 | 0
638 | 0.12485 | 0
639 | 0.12485 | 0
640 | 0.12485 | 0
641 | 0.12485 | 0
642 | 6.7207 | 6.9181
643 | 12.9781 | 13.644
644 | 0.12485 | 0
645 | 1.4411 | 0
646 | 0.12485 | 0
647 | 0.12485 | 0
648 | 0.12485 | 0
649 | 0.12485 | 0
650 | 0.12485 | 0
651 | 0.12485 | 0
652 | 0.12485 | 0
653 | 0.12485 | 0
654 | 12.6664 | 19.5625
655 | 1.5285 | 0
656 | 1.951 | 0
657 | 0.12485 | 0
658 | 0.12485 | 0
659 | 0.12485 | 0
660 | 1.0137 | 0
661 | 0.12485 | 0
662 | 0.12485 | 0
663 | 0.12485 | 0
664 | 0.12485 | 0
665 | 0.12485 | 0
666 | 6.6996 | 6.928
667 | 12.9422 | 19.0538
668 | 0.12485 | 0
669 | 1.542 | 0
670 | 0.12485 | 0
671 | 0.12485 | 0
672 | 0.12485 | 0
673 | 0.12485 | 0
674 | 0.12485 | 0
675 | 0.12485 | 0
676 | 0.12485 | 0
677 | 0.12485 | 0
678 | 12.9098 | 13.6857
679 | 1.5071 | 0
680 | 1.9231 | 0
681 | 0.12485 | 0
682 | 0.12485 | 0
683 | 0.12485 | 0
684 | 1.0002 | 0
685 | 0.12485 | 0
686 | 0.12485 | 0
687 | 0.12485 | 0
688 | 0.12485 | 0
689 | 0.12485 | 0
690 | 6.607 | 6.9623
691 | 12.7839 | 19.2984
692 | 0.12485 | 0
693 | 1.5326 | 0
694 | 0.12485 | 0
695 | 0.12485 | 0
696 | 0.12485 | 0
697 | 0.12485 | 0
698 | 0.12485 | 0
699 | 0.12485 | 0
700 | 0.12485 | 0
701 | 0.12485 | 0
702 | 12.828 | 13.6975
703 | 1.4999 | 0
704 | 1.9138 | 0
705 | 0.12485 | 0
706 | 0.12485 | 0
707 | 0.12485 | 0
708 | 0.99567 | 0
709 | 0.12485 | 0
710 | 0.12485 | 0
711 | 0.12485 | 0
712 | 0.12485 | 0
713 | 0.12485 | 0
714 | 6.7711 | 6.7684
715 | 13.4091 | 19.6214
716 | 0.12485 | 0
717 | 1.5132 | 0
718 | 0.12485 | 0
719 | 0.12485 | 0
720 | 0.12485 | 0
721 | 0.12485 | 0
722 | 0.12485 | 0
723 | 0.12485 | 0
724 | 0.12485 | 0
725 | 0.12485 | 0
726 | 13.2813 | 13.5388
727 | 1.4696 | 0
728 | 1.8744 | 0
729 | 0.12485 | 0
730 | 0.12485 | 0
731 | 0.12485 | 0
732 | 0.9766 | 6.6673
733 | 0.12485 | 0
734 | 0.12485 | 0
735 | 0.12485 | 0
736 | 0.12485 | 0
737 | 0.12485 | 0
738 | 6.7155 | 6.8362
739 | 12.9496 | 13.5197
740 | 0.12485 | 0
741 | 1.5055 | 0
742 | 0.12485 | 0
743 | 0.12485 | 0
744 | 0.12485 | 0
745 | 0.12485 | 0
746 | 0.12485 | 0
747 | 0.12485 | 0
748 | 0.12485 | 0
749 | 0.12485 | 0
750 | 13.2165 | 13.5938
751 | 1.4645 | 0
752 | 1.8679 | 0
753 | 0.12485 | 0
754 | 0.12485 | 6.3579
755 | 0.12485 | 0
756 | 1.055 | 0
757 | 0.12485 | 0
758 | 0.12485 | 0
759 | 0.12485 | 0
760 | 0.12485 | 0
761 | 0.12485 | 0
762 | 6.7693 | 6.8325
763 | 13.4354 | 13.1887
764 | 0.12485 | 0
765 | 1.4763 | 0
766 | 0.12485 | 0
767 | 0.12485 | 0
768 | 0.12485 | 0
769 | 0.12485 | 0
770 | 0.12485 | 0
771 | 0.12485 | 0
772 | 0.12485 | 0
773 | 0.12485 | 0
774 | 12.974 | 19.1458
775 | 1.5482 | 0
776 | 1.9766 | 0
777 | 0.12485 | 0
778 | 0.12485 | 0
779 | 0.12485 | 0
780 | 1.0261 | 0
781 | 0.12485 | 0
782 | 0.12485 | 0
783 | 0.12485 | 0
784 | 0.12485 | 0
785 | 0.12485 | 0
786 | 6.7809 | 6.8098
787 | 13.0732 | 13.6498
788 | 0.12485 | 0
789 | 1.4497 | 0
790 | 0.12485 | 0
791 | 0.12485 | 0
792 | 0.12485 | 0
793 | 0.12485 | 0
794 | 0.12485 | 0
795 | 0.12485 | 0
796 | 0.12485 | 0
797 | 0.12485 | 0
798 | 12.7411 | 19.5187
799 | 1.5344 | 0
800 | 1.9585 | 0
801 | 0.12485 | 0
802 | 0.12485 | 0
803 | 0.12485 | 0
804 | 1.0174 | 0
805 | 0.12485 | 0
806 | 0.12485 | 0
807 | 0.12485 | 0
808 | 0.12485 | 0
809 | 0.12485 | 0
810 | 6.7256 | 6.9265
811 | 12.9874 | 19.0533
812 | 0.12485 | 0
813 | 1.546 | 0
814 | 0.12485 | 0
815 | 0.12485 | 0
816 | 0.12485 | 0
817 | 0.12485 | 0
818 | 0.12485 | 0
819 | 0.12485 | 0
820 | 0.12485 | 0
821 | 0.12485 | 0
822 | 12.9434 | 13.6887
823 | 1.5102 | 0
824 | 1.9271 | 0
825 | 0.12485 | 0
826 | 0.12485 | 0
827 | 0.12485 | 0
828 | 1.0022 | 0
829 | 0.12485 | 0
830 | 0.12485 | 0
831 | 0.12485 | 0
832 | 0.12485 | 0
833 | 0.12485 | 0
834 | 6.621 | 6.9639
835 | 12.8086 | 19.3233
836 | 0.12485 | 0
837 | 1.5353 | 0
838 | 0.12485 | 0
839 | 0.12485 | 0
840 | 0.12485 | 0
841 | 0.12485 | 0
842 | 0.12485 | 0
843 | 0.12485 | 0
844 | 0.12485 | 0
845 | 0.12485 | 0
846 | 13.4622 | 13.259
847 | 1.4817 | 0
848 | 1.8901 | 0
849 | 0.12485 | 0
850 | 0.12485 | 0
851 | 0.12485 | 0
852 | 0.98423 | 6.4988
853 | 0.12485 | 0
854 | 0.12485 | 0
855 | 0.12485 | 0
856 | 0.12485 | 0
857 | 0.12485 | 0
858 | 6.7538 | 6.8281
859 | 13.0145 | 13.5267
860 | 0.12485 | 0
861 | 1.5115 | 0
862 | 0.12485 | 0
863 | 0.12485 | 0
864 | 0.12485 | 0
865 | 0.12485 | 0
866 | 0.12485 | 0
867 | 0.12485 | 0
868 | 0.12485 | 0
869 | 0.12485 | 0
870 | 13.2669 | 13.5945
871 | 1.4691 | 0
872 | 1.8738 | 0
873 | 0.12485 | 0
874 | 0.12485 | 0
875 | 0.12485 | 6.3611
876 | 1.0581 | 0
877 | 0.12485 | 0
878 | 0.12485 | 0
879 | 0.12485 | 0
880 | 0.12485 | 0
881 | 0.12485 | 0
882 | 6.6766 | 6.9109
883 | 12.8958 | 13.5163
884 | 0.12485 | 0
885 | 1.5006 | 0
886 | 0.12485 | 0
887 | 0.12485 | 0
888 | 0.12485 | 0
889 | 0.12485 | 0
890 | 0.12485 | 0
891 | 0.12485 | 0
892 | 0.12485 | 0
893 | 0.12485 | 0
894 | 13.1717 | 13.5919
895 | 1.4605 | 0
896 | 1.8626 | 6.3822
897 | 0.12485 | 0
898 | 0.12485 | 0
899 | 0.12485 | 0
900 | 1.0524 | 0
901 | 0.12485 | 0
902 | 0.12485 | 0
903 | 0.12485 | 0
904 | 0.12485 | 0
905 | 0.12485 | 0
906 | 6.7518 | 6.8585
907 | 13.4118 | 13.2773
908 | 0.12485 | 0
909 | 1.4755 | 0
910 | 0.12485 | 0
911 | 0.12485 | 0
912 | 0.12485 | 0
913 | 0.12485 | 0
914 | 0.12485 | 0
915 | 0.12485 | 0
916 | 0.12485 | 0
917 | 0.12485 | 0
918 | 12.9663 | 19.2051
919 | 1.5486 | 0
920 | 1.9771 | 0
921 | 0.12485 | 0
922 | 0.12485 | 0
923 | 0.12485 | 0
924 | 1.0264 | 0
925 | 0.12485 | 0
926 | 0.12485 | 0
927 | 0.12485 | 0
928 | 0.12485 | 0
929 | 0.12485 | 0
930 | 6.7848 | 6.8489
931 | 13.0835 | 13.6527
932 | 0.12485 | 0
933 | 1.4506 | 0
934 | 0.12485 | 0
935 | 0.12485 | 0
936 | 0.12485 | 0
937 | 0.12485 | 0
938 | 0.12485 | 0
939 | 0.12485 | 0
940 | 0.12485 | 0
941 | 0.12485 | 0
942 | 12.7474 | 19.5463
943 | 1.5355 | 0
944 | 1.96 | 0
945 | 0.12485 | 0
946 | 0.12485 | 0
947 | 0.12485 | 0
948 | 1.0181 | 0
949 | 0.12485 | 0
950 | 0.12485 | 0
951 | 0.12485 | 0
952 | 0.12485 | 0
953 | 0.12485 | 0
954 | 6.7308 | 6.9293
955 | 12.9968 | 19.0764
956 | 0.12485 | 0
957 | 1.5473 | 0
958 | 0.12485 | 0
959 | 0.12485 | 0
960 | 0.12485 | 0
961 | 0.12485 | 0
962 | 0.12485 | 0
963 | 0.12485 | 0
964 | 0.12485 | 0
965 | 0.12485 | 0
966 | 12.9527 | 13.6914
967 | 1.511 | 0
968 | 1.9283 | 0
969 | 0.12485 | 0
970 | 0.12485 | 0
971 | 0.12485 | 0
972 | 1.0027 | 0
973 | 0.12485 | 0
974 | 0.12485 | 0
975 | 0.12485 | 0
976 | 0.12485 | 0
977 | 0.12485 | 0
978 | 6.6251 | 6.9646
979 | 12.8159 | 19.3447
980 | 0.12485 | 0
981 | 1.5363 | 0
982 | 0.12485 | 0
983 | 0.12485 | 0
984 | 0.12485 | 0
985 | 0.12485 | 0
986 | 0.12485 | 0
987 | 0.12485 | 0
988 | 0.12485 | 0
989 | 0.12485 | 0
990 | 13.4701 | 13.2764
991 | 1.4826 | 0
992 | 1.8914 | 0
993 | 0.12485 | 0
994 | 0.12485 | 0
995 | 0.12485 | 0
996 | 0.98485 | 6.5114
997 | 0.12485 | 0
998 | 0.12485 | 0
999 | 0.12485 | 0
1000 | 0.12485 | 0
1001 | 0.12485 | 0
1002 | 6.7594 | 6.8295
1003 | 13.0244 | 13.5275
1004 | 0.12485 | 0
1005 | 1.5124 | 0
1006 | 0.12485 | 0
1007 | 0.12485 | 0
1008 | 0.12485 | 0
1009 | 0.12485 | 0
1010 | 0.12485 | 0
1011 | 0.12485 | 0
1012 | 0.12485 | 0
1013 | 0.12485 | 0
1014 | 13.2729 | 13.5967
1015 | 1.4696 | 0
1016 | 1.8745 | 0
1017 | 0.12485 | 0
1018 | 0.12485 | 6.3668
1019 | 0.12485 | 0
1020 | 1.0585 | 0
1021 | 0.12485 | 0
1022 | 0.12485 | 0
1023 | 0.12485 | 0
1024 | 0.12485 | 0
1025 | 0.12485 | 0
1026 | 6.7937 | 6.8115
1027 | 12.8668 | 13.6103
1028 | 0.12485 | 0
1029 | 1.4995 | 0
1030 | 0.12485 | 0
1031 | 0.12485 | 0
1032 | 0.12485 | 0
1033 | 0.12485 | 0
1034 | 0.12485 | 0
1035 | 0.12485 | 0
1036 | 0.12485 | 0
1037 | 0.12485 | 0
1038 | 13.1593 | 13.5903
1039 | 1.4593 | 0
1040 | 1.8612 | 6.4182
1041 | 0.12485 | 0
1042 | 0.12485 | 0
1043 | 0.12485 | 0
1044 | 1.0521 | 0
1045 | 0.12485 | 0
1046 | 0.12485 | 0
1047 | 0.12485 | 0
1048 | 0.12485 | 0
1049 | 0.12485 | 0
1050 | 6.7502 | 6.8614
1051 | 13.4101 | 13.2984
1052 | 0.12485 | 0
1053 | 1.4757 | 0
1054 | 0.12485 | 0
1055 | 0.12485 | 0
1056 | 0.12485 | 0
1057 | 0.12485 | 0
1058 | 0.12485 | 0
1059 | 0.12485 | 0
1060 | 0.12485 | 0
1061 | 0.12485 | 0
1062 | 12.9657 | 19.22
1063 | 1.5488 | 0
1064 | 1.9773 | 0
1065 | 0.12485 | 0
1066 | 0.12485 | 0
1067 | 0.12485 | 0
1068 | 1.0265 | 0
1069 | 0.12485 | 0
1070 | 0.12485 | 0
1071 | 0.12485 | 0
1072 | 0.12485 | 0
1073 | 0.12485 | 0
1074 | 6.7863 | 6.8589
1075 | 13.0871 | 13.6536
1076 | 0.12485 | 0
1077 | 1.451 | 0
1078 | 0.12485 | 0
1079 | 0.12485 | 0
1080 | 0.12485 | 0
1081 | 0.12485 | 0
1082 | 0.12485 | 0
1083 | 0.12485 | 0
1084 | 0.12485 | 0
1085 | 0.12485 | 0
1086 | 12.7479 | 19.5533
1087 | 1.5356 | 0
1088 | 1.9602 | 0
1089 | 0.12485 | 0
1090 | 0.12485 | 0
1091 | 0.12485 | 0
1092 | 1.0182 | 0
1093 | 0.12485 | 0
1094 | 0.12485 | 0
1095 | 0.12485 | 0
1096 | 0.12485 | 0
1097 | 0.12485 | 0
1098 | 6.7317 | 6.9299
1099 | 12.9983 | 19.0817
1100 | 0.12485 | 0
1101 | 1.5475 | 0
1102 | 0.12485 | 0
1103 | 0.12485 | 0
1104 | 0.12485 | 0
1105 | 0.12485 | 0
1106 | 0.12485 | 0
1107 | 0.12485 | 0
1108 | 0.12485 | 0
1109 | 0.12485 | 0
1110 | 12.9524 | 13.6918
1111 | 1.511 | 0
1112 | 1.9282 | 0
1113 | 0.12485 | 0
1114 | 0.12485 | 0
1115 | 0.12485 | 0
1116 | 1.0027 | 0
1117 | 0.12485 | 0
1118 | 0.12485 | 0
1119 | 0.12485 | 0
1120 | 0.12485 | 0
1121 | 0.12485 | 0
1122 | 6.6251 | 6.9647
1123 | 12.8157 | 19.3477
1124 | 0.12485 | 0
1125 | 1.5364 | 0
1126 | 0.12485 | 0
1127 | 0.12485 | 0
1128 | 0.12485 | 0
1129 | 0.12485 | 0
1130 | 0.12485 | 0
1131 | 0.12485 | 0
1132 | 0.12485 | 0
1133 | 0.12485 | 0
1134 | 13.4679 | 13.2778
1135 | 1.4825 | 0
1136 | 1.8911 | 0
1137 | 0.12485 | 0
1138 | 0.12485 | 0
1139 | 0.12485 | 0
1140 | 0.98474 | 6.5121
1141 | 0.12485 | 0
1142 | 0.12485 | 0
1143 | 0.12485 | 0
1144 | 0.12485 | 0
1145 | 0.12485 | 0
1146 | 6.7587 | 6.8295
1147 | 13.0232 | 13.5274
1148 | 0.12485 | 0
1149 | 1.5123 | 0
1150 | 0.12485 | 0
1151 | 0.12485 | 0
1152 | 0.12485 | 0
1153 | 0.12485 | 0
1154 | 0.12485 | 0
1155 | 0.12485 | 0
1156 | 0.12485 | 0
1157 | 0.12485 | 0
1158 | 13.2693 | 13.5964
1159 | 1.4693 | 0
1160 | 1.8741 | 0
1161 | 0.12485 | 0
1162 | 0.12485 | 6.3651
1163 | 0.12485 | 0
1164 | 1.0583 | 0
1165 | 0.12485 | 0
1166 | 0.12485 | 0
1167 | 0.12485 | 0
1168 | 0.12485 | 0
1169 | 0.12485 | 0
1170 | 6.792 | 6.8097
1171 | 12.8636 | 13.6099
1172 | 0.12485 | 0
1173 | 1.4992 | 0
1174 | 0.12485 | 0
1175 | 0.12485 | 0
1176 | 0.12485 | 0
1177 | 0.12485 | 0
1178 | 0.12485 | 0
1179 | 0.12485 | 0
1180 | 0.12485 | 0
1181 | 0.12485 | 0
1182 | 13.154 | 13.5899
1183 | 1.4589 | 0
1184 | 1.8605 | 6.4141
1185 | 0.12485 | 0
1186 | 0.12485 | 0
1187 | 0.12485 | 0
1188 | 1.0518 | 0
1189 | 0.12485 | 0
1190 | 0.12485 | 0
1191 | 0.12485 | 0
1192 | 0.12485 | 0
1193 | 0.12485 | 0
1194 | 6.7476 | 6.8608
1195 | 13.4054 | 13.2934
1196 | 0.12485 | 0
1197 | 1.4752 | 0
1198 | 0.12485 | 0
1199 | 0.12485 | 0
1200 | 0.12485 | 0
1201 | 0.12485 | 0
1202 | 0.12485 | 0
1203 | 0.12485 | 0
1204 | 0.12485 | 0
1205 | 0.12485 | 0
1206 | 12.9585 | 19.2134
1207 | 1.548 | 0
1208 | 1.9763 | 0
1209 | 0.12485 | 0
1210 | 0.12485 | 0
1211 | 0.12485 | 0
1212 | 1.026 | 0
1213 | 0.12485 | 0
1214 | 0.12485 | 0
1215 | 0.12485 | 0
1216 | 0.12485 | 0
1217 | 0.12485 | 0
1218 | 6.7826 | 6.8535
1219 | 13.08 | 13.6526
1220 | 0.12485 | 0
1221 | 1.4503 | 0
1222 | 0.12485 | 0
1223 | 0.12485 | 0
1224 | 0.12485 | 0
1225 | 0.12485 | 0
1226 | 0.12485 | 0
1227 | 0.12485 | 0
1228 | 0.12485 | 0
1229 | 0.12485 | 0
1230 | 12.7394 | 19.5441
1231 | 1.5347 | 0
1232 | 1.959 | 0
1233 | 0.12485 | 0
1234 | 0.12485 | 0
1235 | 0.12485 | 0
1236 | 1.0176 | 0
1237 | 0.12485 | 0
1238 | 0.12485 | 0
1239 | 0.12485 | 0
1240 | 0.12485 | 0
1241 | 0.12485 | 0
1242 | 6.7274 | 6.9288
1243 | 12.9907 | 19.0712
1244 | 0.12485 | 0
1245 | 1.5466 | 0
1246 | 0.12485 | 0
1247 | 0.12485 | 0
1248 | 0.12485 | 0
1249 | 0.12485 | 0
1250 | 0.12485 | 0
1251 | 0.12485 | 0
1252 | 0.12485 | 0
1253 | 0.12485 | 0
1254 | 12.9417 | 13.69
1255 | 1.51 | 0
1256 | 1.927 | 0
1257 | 0.12485 | 0
1258 | 0.12485 | 0
1259 | 0.12485 | 0
1260 | 1.0021 | 0
1261 | 0.12485 | 0
1262 | 0.12485 | 0
1263 | 0.12485 | 0
1264 | 0.12485 | 0
1265 | 0.12485 | 0
1266 | 6.6205 | 6.964
1267 | 12.8077 | 19.3329
1268 | 0.12485 | 0
1269 | 1.5354 | 0
1270 | 0.12485 | 0
1271 | 0.12485 | 0
1272 | 0.12485 | 0
1273 | 0.12485 | 0
1274 | 0.12485 | 0
1275 | 0.12485 | 0
1276 | 0.12485 | 0
1277 | 0.12485 | 0
1278 | 13.4557 | 13.2636
1279 | 1.4812 | 0
1280 | 1.8894 | 0
1281 | 0.12485 | 0
1282 | 0.12485 | 0
1283 | 0.12485 | 0
1284 | 0.9839 | 6.5011
1285 | 0.12485 | 0
1286 | 0.12485 | 0
1287 | 0.12485 | 0
1288 | 0.12485 | 0
1289 | 0.12485 | 0
1290 | 6.7516 | 6.8281
1291 | 13.0107 | 13.5263
1292 | 0.12485 | 0
1293 | 1.5111 | 0
1294 | 0.12485 | 0
1295 | 0.12485 | 0
1296 | 0.12485 | 0
1297 | 0.12485 | 0
1298 | 0.12485 | 0
1299 | 0.12485 | 0
1300 | 0.12485 | 0
1301 | 0.12485 | 0
1302 | 13.2561 | 13.5936
1303 | 1.4681 | 0
1304 | 1.8725 | 0
1305 | 0.12485 | 0
1306 | 0.12485 | 0
1307 | 0.12485 | 6.3636
1308 | 1.0575 | 0
1309 | 0.12485 | 0
1310 | 0.12485 | 0
1311 | 0.12485 | 0
1312 | 0.12485 | 0
1313 | 0.12485 | 0
1314 | 6.6726 | 6.9086
1315 | 12.8883 | 13.5157
1316 | 0.12485 | 0
1317 | 1.5 | 0
1318 | 0.12485 | 0
1319 | 0.12485 | 0
1320 | 0.12485 | 0
1321 | 0.12485 | 0
1322 | 0.12485 | 0
1323 | 0.12485 | 0
1324 | 0.12485 | 0
1325 | 0.12485 | 0
1326 | 13.1577 | 13.5908
1327 | 1.4592 | 0
1328 | 1.861 | 6.3674
1329 | 0.12485 | 0
1330 | 0.12485 | 0
1331 | 0.12485 | 0
1332 | 1.0514 | 0
1333 | 0.12485 | 0
1334 | 0.12485 | 0
1335 | 0.12485 | 0
1336 | 0.12485 | 0
1337 | 0.12485 | 0
1338 | 6.7445 | 6.8566
1339 | 13.3984 | 13.2614
1340 | 0.12485 | 0
1341 | 1.4741 | 0
1342 | 0.12485 | 0
1343 | 0.12485 | 0
1344 | 0.12485 | 0
1345 | 0.12485 | 0
1346 | 0.12485 | 0
1347 | 0.12485 | 0
1348 | 0.12485 | 0
1349 | 0.12485 | 0
1350 | 12.9452 | 19.1849
1351 | 1.5463 | 0
1352 | 1.9741 | 0
1353 | 0.12485 | 0
1354 | 0.12485 | 0
1355 | 0.12485 | 0
1356 | 1.0249 | 0
1357 | 0.12485 | 0
1358 | 0.12485 | 0
1359 | 0.12485 | 0
1360 | 0.12485 | 0
1361 | 0.12485 | 0
1362 | 6.7736 | 6.8323
1363 | 13.0626 | 13.6498
1364 | 0.12485 | 0
1365 | 1.4487 | 0
1366 | 0.12485 | 0
1367 | 0.12485 | 0
1368 | 0.12485 | 0
1369 | 0.12485 | 0
1370 | 0.12485 | 0
1371 | 0.12485 | 0
1372 | 0.12485 | 0
1373 | 0.12485 | 0
1374 | 12.7222 | 19.5186
1375 | 1.5327 | 0
1376 | 1.9563 | 0
1377 | 0.12485 | 0
1378 | 0.12485 | 0
1379 | 0.12485 | 0
1380 | 1.0163 | 0
1381 | 0.12485 | 0
1382 | 0.12485 | 0
1383 | 0.12485 | 0
1384 | 0.12485 | 0
1385 | 0.12485 | 0
1386 | 6.7179 | 6.9258
1387 | 12.9739 | 19.045
1388 | 0.12485 | 0
1389 | 1.5446 | 0
1390 | 0.12485 | 0
1391 | 0.12485 | 0
1392 | 0.12485 | 0
1393 | 0.12485 | 0
1394 | 0.12485 | 0
1395 | 0.12485 | 0
1396 | 0.12485 | 0
1397 | 0.12485 | 0
1398 | 12.9208 | 13.686
1399 | 1.5081 | 0
1400 | 1.9244 | 0
1401 | 0.12485 | 0
1402 | 0.12485 | 0
1403 | 0.12485 | 0
1404 | 1.0008 | 0
1405 | 0.12485 | 0
1406 | 0.12485 | 0
1407 | 0.12485 | 0
1408 | 0.12485 | 0
1409 | 0.12485 | 0
1410 | 6.6115 | 6.9627
1411 | 12.7918 | 19.3004
1412 | 0.12485 | 0
1413 | 1.5333 | 0
1414 | 0.12485 | 0
1415 | 0.12485 | 0
1416 | 0.12485 | 0
1417 | 0.12485 | 0
1418 | 0.12485 | 0
1419 | 0.12485 | 0
1420 | 0.12485 | 0
1421 | 0.12485 | 0
1422 | 12.8219 | 13.6971
1423 | 1.4994 | 0
1424 | 1.9131 | 0
1425 | 0.12485 | 0
1426 | 0.12485 | 0
1427 | 0.12485 | 0
1428 | 0.99531 | 0
1429 | 0.12485 | 0
1430 | 0.12485 | 0
1431 | 0.12485 | 0
1432 | 0.12485 | 0
1433 | 0.12485 | 0
1434 | 6.7686 | 6.7682
1435 | 13.4043 | 19.6149
1436 | 0.12485 | 0
1437 | 1.5127 | 0
1438 | 0.12485 | 0
1439 | 0.12485 | 0
1440 | 0.12485 | 0
1441 | 0.12485 | 0
1442 | 0.12485 | 0
1443 | 0.12485 | 0
1444 | 0.12485 | 0
1445 | 0.12485 | 0
1446 | 13.2635 | 13.5309
1447 | 1.4679 | 0
1448 | 1.8722 | 0
1449 | 0.12485 | 0
1450 | 0.12485 | 0
1451 | 0.12485 | 0
1452 | 0.9755 | 6.6598
1453 | 0.12485 | 0
1454 | 0.12485 | 0
1455 | 0.12485 | 0
1456 | 0.12485 | 0
1457 | 0.12485 | 0
1458 | 6.707 | 6.8349
1459 | 12.9346 | 13.5184
1460 | 0.12485 | 0
1461 | 1.5042 | 0
1462 | 0.12485 | 0
1463 | 0.12485 | 0
1464 | 0.12485 | 0
1465 | 0.12485 | 0
1466 | 0.12485 | 0
1467 | 0.12485 | 0
1468 | 0.12485 | 0
1469 | 0.12485 | 0
1470 | 13.1911 | 13.5915
1471 | 1.4622 | 0
1472 | 1.8648 | 0
1473 | 0.12485 | 0
1474 | 0.12485 | 6.359
1475 | 0.12485 | 0
1476 | 1.0536 | 0
1477 | 0.12485 | 0
1478 | 0.12485 | 0
1479 | 0.12485 | 0
1480 | 0.12485 | 0
1481 | 0.12485 | 0
1482 | 6.645 | 6.9118
1483 | 12.8411 | 13.5113
1484 | 0.12485 | 0
1485 | 1.4956 | 0
1486 | 0.12485 | 0
1487 | 0.12485 | 0
1488 | 0.12485 | 0
1489 | 0.12485 | 0
1490 | 0.12485 | 0
1491 | 0.12485 | 0
1492 | 0.12485 | 0
1493 | 0.12485 | 0
1494 | 13.1156 | 13.5871
1495 | 1.4554 | 0
1496 | 1.856 | 6.3531
1497 | 0.12485 | 0
1498 | 0.12485 | 0
1499 | 0.12485 | 0
1500 | 1.0488 | 0
1501 | 0.12485 | 0
1502 | 0.12485 | 0
1503 | 0.12485 | 0
1504 | 0.12485 | 0
1505 | 0.12485 | 0
1506 | 6.7259 | 6.8517
1507 | 13.3642 | 13.2279
1508 | 0.12485 | 0
1509 | 1.4705 | 0
1510 | 0.12485 | 0
1511 | 0.12485 | 0
1512 | 0.12485 | 0
1513 | 0.12485 | 0
1514 | 0.12485 | 0
1515 | 0.12485 | 0
1516 | 0.12485 | 0
1517 | 0.12485 | 0
1518 | 12.9093 | 19.1456
1519 | 1.5424 | 0
1520 | 1.969 | 0
1521 | 0.12485 | 0
1522 | 0.12485 | 0
1523 | 0.12485 | 0
1524 | 1.0224 | 0
1525 | 0.12485 | 0
1526 | 0.12485 | 0
1527 | 0.12485 | 0
1528 | 0.12485 | 0
1529 | 0.12485 | 0
1530 | 6.5461 | 7.0919
1531 | 13.0951 | 13.4446
1532 | 0.12485 | 0
1533 | 1.4498 | 0
1534 | 0.12485 | 0
1535 | 0.12485 | 0
1536 | 0.12485 | 0
1537 | 0.12485 | 0
1538 | 0.12485 | 0
1539 | 0.12485 | 0
1540 | 0.12485 | 0
1541 | 0.12485 | 0
1542 | 12.7277 | 19.4155
1543 | 1.5312 | 0
1544 | 1.9544 | 0
1545 | 0.12485 | 0
1546 | 0.12485 | 0
1547 | 0.12485 | 0
1548 | 1.0153 | 0
1549 | 0.12485 | 0
1550 | 0.12485 | 0
1551 | 0.12485 | 0
1552 | 0.12485 | 0
1553 | 0.12485 | 0
1554 | 6.7101 | 6.9165
1555 | 12.9595 | 13.6421
1556 | 0.12485 | 0
1557 | 1.4394 | 0
1558 | 0.12485 | 0
1559 | 0.12485 | 0
1560 | 0.12485 | 0
1561 | 0.12485 | 0
1562 | 0.12485 | 0
1563 | 0.12485 | 0
1564 | 0.12485 | 0
1565 | 0.12485 | 0
1566 | 12.6348 | 19.5349
1567 | 1.5252 | 0
1568 | 1.9466 | 0
1569 | 0.12485 | 0
1570 | 0.12485 | 0
1571 | 0.12485 | 0
1572 | 1.0115 | 0
1573 | 0.12485 | 0
1574 | 0.12485 | 0
1575 | 0.12485 | 0
1576 | 0.12485 | 0
1577 | 0.12485 | 0
1578 | 6.6841 | 6.9244
1579 | 12.9148 | 19.0196
1580 | 0.12485 | 0
1581 | 1.5389 | 0
1582 | 0.12485 | 0
1583 | 0.12485 | 0
1584 | 0.12485 | 0
1585 | 0.12485 | 0
1586 | 0.12485 | 0
1587 | 0.12485 | 0
1588 | 0.12485 | 0
1589 | 0.12485 | 0
1590 | 12.8654 | 13.679
1591 | 1.503 | 0
1592 | 1.9178 | 0
1593 | 0.12485 | 0
1594 | 0.12485 | 0
1595 | 0.12485 | 0
1596 | 0.99755 | 0
1597 | 0.12485 | 0
1598 | 0.12485 | 0
1599 | 0.12485 | 0
1600 | 0.12485 | 0
1601 | 0.12485 | 0
1602 | 6.588 | 6.9596
1603 | 12.7505 | 19.2424
1604 | 0.12485 | 0
1605 | 1.5285 | 0
1606 | 0.12485 | 0
1607 | 0.12485 | 0
1608 | 0.12485 | 0
1609 | 0.12485 | 0
1610 | 0.12485 | 0
1611 | 0.12485 | 0
1612 | 0.12485 | 0
1613 | 0.12485 | 0
1614 | 12.7748 | 13.6883
1615 | 1.495 | 0
1616 | 1.9074 | 0
1617 | 0.12485 | 0
1618 | 0.12485 | 0
1619 | 0.12485 | 0
1620 | 0.9925 | 0
1621 | 0.12485 | 0
1622 | 0.12485 | 0
1623 | 0.12485 | 0
1624 | 0.12485 | 0
1625 | 0.12485 | 0
1626 | 6.5524 | 6.9581
1627 | 12.6887 | 19.3155
1628 | 0.12485 | 0
1629 | 1.5244 | 0
1630 | 0.12485 | 0
1631 | 0.12485 | 0
1632 | 0.12485 | 0
1633 | 0.12485 | 0
1634 | 0.12485 | 0
1635 | 0.12485 | 0
1636 | 0.12485 | 0
1637 | 0.12485 | 0
1638 | 12.7383 | 13.6906
1639 | 1.4917 | 0
1640 | 1.9031 | 0
1641 | 0.12485 | 0
1642 | 0.12485 | 0
1643 | 0.12485 | 0
1644 | 0.99044 | 0
1645 | 0.12485 | 0
1646 | 0.12485 | 0
1647 | 0.12485 | 0
1648 | 0.12485 | 0
1649 | 0.12485 | 0
1650 | 6.5379 | 6.9572
1651 | 12.6633 | 19.3338
1652 | 0.12485 | 0
1653 | 1.5225 | 0
1654 | 0.12485 | 0
1655 | 0.12485 | 0
1656 | 0.12485 | 0
1657 | 0.12485 | 0
1658 | 0.12485 | 0
1659 | 0.12485 | 0
1660 | 0.12485 | 0
1661 | 0.12485 | 0
1662 | 12.7209 | 13.6905
1663 | 1.4902 | 0
1664 | 1.9011 | 0
1665 | 0.12485 | 0
1666 | 0.12485 | 0
1667 | 0.12485 | 0
1668 | 0.98945 | 0
1669 | 0.12485 | 0
1670 | 0.12485 | 0
1671 | 0.12485 | 0
1672 | 0.12485 | 0
1673 | 0.12485 | 0
1674 | 6.5309 | 6.9565
1675 | 12.651 | 19.3322
1676 | 0.12485 | 0
1677 | 1.5214 | 0
1678 | 0.12485 | 0
1679 | 0.12485 | 0
1680 | 0.12485 | 0
1681 | 0.12485 | 0
1682 | 0.12485 | 0
1683 | 0.12485 | 0
1684 | 0.12485 | 0
1685 | 0.12485 | 0
1686 | 12.7104 | 13.6894
1687 | 1.4892 | 0
1688 | 1.8999 | 0
1689 | 0.12485 | 0
1690 | 0.12485 | 0
1691 | 0.12485 | 0
1692 | 0.98883 | 0
1693 | 0.12485 | 0
1694 | 0.12485 | 0
1695 | 0.12485 | 0
1696 | 0.12485 | 0
1697 | 0.12485 | 0
1698 | 6.5264 | 6.956
1699 | 12.6432 | 19.3232
1700 | 0.12485 | 0
1701 | 1.5205 | 0
1702 | 0.12485 | 0
1703 | 0.12485 | 0
1704 | 0.12485 | 0
1705 | 0.12485 | 0
1706 | 0.12485 | 0
1707 | 0.12485 | 0
1708 | 0.12485 | 0
1709 | 0.12485 | 0
1710 | 12.702 | 13.6879
1711 | 1.4885 | 0
1712 | 1.8988 | 0
1713 | 0.12485 | 0
1714 | 0.12485 | 0
1715 | 0.12485 | 0
1716 | 0.98833 | 0
1717 | 0.12485 | 0
1718 | 0.12485 | 0
1719 | 0.12485 | 0
1720 | 0.12485 | 0
1721 | 0.12485 | 0
1722 | 6.5229 | 6.9555
1723 | 12.6369 | 19.3112
1724 | 0.12485 | 0
1725 | 1.5197 | 0
1726 | 0.12485 | 0
1727 | 0.12485 | 0
1728 | 0.12485 | 0
1729 | 0.12485 | 0
1730 | 0.12485 | 0
1731 | 0.12485 | 0
1732 | 0.12485 | 0
1733 | 0.12485 | 0
1734 | 12.6944 | 13.6863
1735 | 1.4877 | 0
1736 | 1.8979 | 0
1737 | 0.12485 | 0
1738 | 0.12485 | 0
1739 | 0.12485 | 0
1740 | 0.98787 | 0
1741 | 0.12485 | 0
1742 | 0.12485 | 0
1743 | 0.12485 | 0
1744 | 0.12485 | 0
1745 | 0.12485 | 0
1746 | 6.5195 | 6.955
1747 | 12.631 | 19.2978
1748 | 0.12485 | 0
1749 | 1.519 | 0
1750 | 0.12485 | 0
1751 | 0.12485 | 0
1752 | 0.12485 | 0
1753 | 0.12485 | 0
1754 | 0.12485 | 0
1755 | 0.12485 | 0
1756 | 0.12485 | 0
1757 | 0.12485 | 0
1758 | 12.6868 | 13.6846
1759 | 1.487 | 0
1760 | 1.897 | 0
1761 | 0.12485 | 0
1762 | 0.12485 | 0
1763 | 0.12485 | 0
1764 | 0.98741 | 0
1765 | 0.12485 | 0
1766 | 0.12485 | 0
1767 | 0.12485 | 0
1768 | 0.12485 | 0
1769 | 0.12485 | 0
1770 | 6.5162 | 6.9545
1771 | 12.6252 | 19.2837
1772 | 0.12485 | 0
1773 | 1.5182 | 0
1774 | 0.12485 | 0
1775 | 0.12485 | 0
1776 | 0.12485 | 0
1777 | 0.12485 | 0
1778 | 0.12485 | 0
1779 | 0.12485 | 0
1780 | 0.12485 | 0
1781 | 0.12485 | 0
1782 | 12.6791 | 13.6827
1783 | 1.4863 | 0
1784 | 1.8961 | 0
1785 | 0.12485 | 0
1786 | 0.12485 | 0
1787 | 0.12485 | 0
1788 | 0.98695 | 0
1789 | 0.12485 | 0
1790 | 0.12485 | 0
1791 | 0.12485 | 0
1792 | 0.12485 | 0
1793 | 0.12485 | 0
1794 | 6.5128 | 6.9539
1795 | 12.6192 | 19.2689
1796 | 0.12485 | 0
1797 | 1.5174 | 0
1798 | 0.12485 | 0
1799 | 0.12485 | 0
1800 | 0.12485 | 0
1801 | 0.12485 | 0
1802 | 0.12485 | 0
1803 | 0.12485 | 0
1804 | 0.12485 | 0
1805 | 0.12485 | 0
1806 | 12.6713 | 13.6809
1807 | 1.4856 | 0
1808 | 1.8951 | 0
1809 | 0.12485 | 0
1810 | 0.12485 | 0
1811 | 0.12485 | 0
1812 | 0.98647 | 0
1813 | 0.12485 | 0
1814 | 0.12485 | 0
1815 | 0.12485 | 0
1816 | 0.12485 | 0
1817 | 0.12485 | 0
1818 | 6.5094 | 6.9533
1819 | 12.6131 | 19.2537
1820 | 0.12485 | 0
1821 | 1.5165 | 0
1822 | 0.12485 | 0
1823 | 0.12485 | 0
1824 | 0.12485 | 0
1825 | 0.12485 | 0
1826 | 0.12485 | 0
1827 | 0.12485 | 0
1828 | 0.12485 | 0
1829 | 0.12485 | 0
1830 | 12.6632 | 13.6789
1831 | 1.4848 | 0
1832 | 1.8941 | 0
1833 | 0.12485 | 0
1834 | 0.12485 | 0
1835 | 0.12485 | 0
1836 | 0.98599 | 0
1837 | 0.12485 | 0
1838 | 0.12485 | 0
1839 | 0.12485 | 0
1840 | 0.12485 | 0
1841 | 0.12485 | 0
1842 | 6.5058 | 6.9527
1843 | 12.6069 | 19.238
1844 | 0.12485 | 0
1845 | 1.5157 | 0
1846 | 0.12485 | 0
1847 | 0.12485 | 0
1848 | 0.12485 | 0
1849 | 0.12485 | 0
1850 | 0.12485 | 0
1851 | 0.12485 | 0
1852 | 0.12485 | 0
1853 | 0.12485 | 0
1854 | 12.6549 | 13.677
1855 | 1.4841 | 0
1856 | 1.8931 | 0
1857 | 0.12485 | 0
1858 | 0.12485 | 0
1859 | 0.12485 | 0
1860 | 0.98548 | 0
1861 | 0.12485 | 0
1862 | 0.12485 | 0
1863 | 0.12485 | 0
1864 | 0.12485 | 0
1865 | 0.12485 | 0
1866 | 6.5022 | 6.9521
1867 | 12.6005 | 19.2219
1868 | 0.12485 | 0
1869 | 1.5148 | 0
1870 | 0.12485 | 0
1871 | 0.12485 | 0
1872 | 0.12485 | 0
1873 | 0.12485 | 0
1874 | 0.12485 | 0
1875 | 0.12485 | 0
1876 | 0.12485 | 0
1877 | 0.12485 | 0
1878 | 12.6464 | 13.6749
1879 | 1.4833 | 0
1880 | 1.8921 | 0
1881 | 0.12485 | 0
1882 | 0.12485 | 0
1883 | 0.12485 | 0
1884 | 0.98497 | 0
1885 | 0.12485 | 0
1886 | 0.12485 | 0
1887 | 0.12485 | 0
1888 | 0.12485 | 0
1889 | 0.12485 | 0
1890 | 6.4985 | 6.9515
1891 | 12.5939 | 19.2053
1892 | 0.12485 | 0
1893 | 1.5139 | 0
1894 | 0.12485 | 0
1895 | 0.12485 | 0
1896 | 0.12485 | 0
1897 | 0.12485 | 0
1898 | 0.12485 | 0
1899 | 0.12485 | 0
1900 | 0.12485 | 0
1901 | 0.12485 | 0
1902 | 12.6377 | 13.6728
1903 | 1.4825 | 0
1904 | 1.891 | 0
1905 | 0.12485 | 0
1906 | 0.12485 | 0
1907 | 0.12485 | 0
1908 | 0.98444 | 0
1909 | 0.12485 | 0
1910 | 0.12485 | 0
1911 | 0.12485 | 0
1912 | 0.12485 | 0
1913 | 0.12485 | 0
1914 | 6.4947 | 6.9509
1915 | 12.5872 | 19.1883
1916 | 0.12485 | 0
1917 | 1.513 | 0
1918 | 0.12485 | 0
1919 | 0.12485 | 0
1920 | 0.12485 | 0
1921 | 0.12485 | 0
1922 | 0.12485 | 0
1923 | 0.12485 | 0
1924 | 0.12485 | 0
1925 | 0.12485 | 0
1926 | 12.6288 | 13.6707
1927 | 1.4816 | 0
1928 | 1.8899 | 0
1929 | 0.12485 | 0
1930 | 0.12485 | 0
1931 | 0.12485 | 0
1932 | 0.9839 | 0
1933 | 0.12485 | 0
1934 | 0.12485 | 0
1935 | 0.12485 | 0
1936 | 0.12485 | 0
1937 | 0.12485 | 0
1938 | 6.4908 | 6.9502
1939 | 12.5803 | 19.1708
1940 | 0.12485 | 0
1941 | 1.512 | 0
1942 | 0.12485 | 0
1943 | 0.12485 | 0
1944 | 0.12485 | 0
1945 | 0.12485 | 0
1946 | 0.12485 | 0
1947 | 0.12485 | 0
1948 | 0.12485 | 0
1949 | 0.12485 | 0
1950 | 12.6197 | 13.6685
1951 | 1.4808 | 0
1952 | 1.8888 | 0
1953 | 0.12485 | 0
1954 | 0.12485 | 0
1955 | 0.12485 | 0
1956 | 0.98335 | 0
1957 | 0.12485 | 0
1958 | 0.12485 | 0
1959 | 0.12485 | 0
1960 | 0.12485 | 0
1961 | 0.12485 | 0
1962 | 6.4868 | 6.9495
1963 | 12.5732 | 19.1529
1964 | 0.12485 | 0
1965 | 1.511 | 0
1966 | 0.12485 | 0
1967 | 0.12485 | 0
1968 | 0.12485 | 0
1969 | 0.12485 | 0
1970 | 0.12485 | 0
1971 | 0.12485 | 0
1972 | 0.12485 | 0
1973 | 0.12485 | 0
1974 | 12.6104 | 13.6662
1975 | 1.4799 | 0
1976 | 1.8877 | 0
1977 | 0.12485 | 0
1978 | 0.12485 | 0
1979 | 0.12485 | 0
1980 | 0.98279 | 0
1981 | 0.12485 | 0
1982 | 0.12485 | 0
1983 | 0.12485 | 0
1984 | 0.12485 | 0
1985 | 0.12485 | 0
1986 | 6.4827 | 6.9489
1987 | 12.566 | 19.1346
1988 | 0.12485 | 0
1989 | 1.51 | 0
1990 | 0.12485 | 0
1991 | 0.12485 | 0
1992 | 0.12485 | 0
1993 | 0.12485 | 0
1994 | 0.12485 | 0
1995 | 0.12485 | 0
1996 | 0.12485 | 0
1997 | 0.12485 | 0
1998 | 12.6009 | 13.6639
1999 | 1.479 | 0
2000 | 1.8865 | 0
2001 | 0.12485 | 0
2002 | 0.12485 | 0
2003 | 0.12485 | 0
2004 | 0.98221 | 0
2005 | 0.12485 | 0
2006 | 0.12485 | 0
2007 | 0.12485 | 0
2008 | 0.12485 | 0
2009 | 0.12485 | 0
2010 | 6.4785 | 6.9482
2011 | 12.5586 | 19.1159
2012 | 0.12485 | 0
2013 | 1.509 | 0
2014 | 0.12485 | 0
2015 | 0.12485 | 0
2016 | 0.12485 | 0
2017 | 0.12485 | 0
2018 | 0.12485 | 0
2019 | 0.12485 | 0
2020 | 0.12485 | 0
2021 | 0.12485 | 0
2022 | 12.5912 | 13.6616
2023 | 1.4781 | 0
2024 | 1.8853 | 0
2025 | 0.12485 | 0
2026 | 0.12485 | 0
2027 | 0.12485 | 0
2028 | 0.98162 | 0
2029 | 0.12485 | 0
2030 | 0.12485 | 0
2031 | 0.12485 | 0
2032 | 0.12485 | 0
2033 | 0.12485 | 0
2034 | 6.4742 | 6.9467
2035 | 12.551 | 19.0969
2036 | 0.12485 | 0
2037 | 1.508 | 0
2038 | 0.12485 | 0
2039 | 0.12485 | 0
2040 | 0.12485 | 0
2041 | 0.12485 | 0
2042 | 0.12485 | 0
2043 | 0.12485 | 0
2044 | 0.12485 | 0
2045 | 0.12485 | 0
2046 | 12.5812 | 13.6592
2047 | 1.4772 | 0
2048 | 1.8841 | 0
2049 | 0.12485 | 0
2050 | 0.12485 | 0
2051 | 0.12485 | 0
2052 | 0.98102 | 0
2053 | 0.12485 | 0
2054 | 0.12485 | 0
2055 | 0.12485 | 0
2056 | 0.12485 | 0
2057 | 0.12485 | 0
2058 | 6.4697 | 6.9441
2059 | 12.543 | 19.078
2060 | 0.12485 | 0
2061 | 1.5069 | 0
2062 | 0.12485 | 0
2063 | 0.12485 | 0
2064 | 0.12485 | 0
2065 | 0.12485 | 0
2066 | 0.12485 | 0
2067 | 0.12485 | 0
2068 | 0.12485 | 0
2069 | 0.12485 | 0
2070 | 12.5709 | 13.652
2071 | 1.4761 | 0
2072 | 1.8827 | 0
2073 | 0.12485 | 0
2074 | 0.12485 | 0
2075 | 0.12485 | 0
2076 | 0.98034 | 0
2077 | 0.12485 | 0
2078 | 0.12485 | 0
2079 | 0.12485 | 0
2080 | 0.12485 | 0
2081 | 0.12485 | 0
2082 | 6.4647 | 6.9417
2083 | 12.534 | 19.0597
2084 | 0.12485 | 0
2085 | 1.5057 | 0
2086 | 0.12485 | 0
2087 | 0.12485 | 0
2088 | 0.12485 | 0
2089 | 0.12485 | 0
2090 | 0.12485 | 0
2091 | 0.12485 | 0
2092 | 0.12485 | 0
2093 | 0.12485 | 0
2094 | 12.5601 | 13.6351
2095 | 1.4748 | 0
2096 | 1.881 | 0
2097 | 0.12485 | 0
2098 | 0.12485 | 0
2099 | 0.12485 | 0
2100 | 0.97951 | 0
2101 | 0.12485 | 0
2102 | 0.12485 | 0
2103 | 0.12485 | 0
2104 | 0.12485 | 0
2105 | 0.12485 | 0
2106 | 6.4587 | 6.9398
2107 | 12.5234 | 19.0434
2108 | 0.12485 | 0
2109 | 1.5045 | 0
2110 | 0.12485 | 0
2111 | 0.12485 | 0
2112 | 0.12485 | 0
2113 | 0.12485 | 0
2114 | 0.12485 | 0
2115 | 0.12485 | 0
2116 | 0.12485 | 0
2117 | 0.12485 | 0
2118 | 12.5482 | 13.6193
2119 | 1.4735 | 0
2120 | 1.8793 | 0
2121 | 0.12485 | 0
2122 | 0.12485 | 0
2123 | 0.12485 | 0
2124 | 0.97863 | 0
2125 | 0.12485 | 0
2126 | 0.12485 | 0
2127 | 0.12485 | 0
2128 | 0.12485 | 0
2129 | 0.12485 | 0
2130 | 6.4523 | 6.9381
2131 | 12.5121 | 19.0274
2132 | 0.12485 | 0
2133 | 1.5032 | 0
2134 | 0.12485 | 0
2135 | 0.12485 | 0
2136 | 0.12485 | 0
2137 | 0.12485 | 0
2138 | 0.12485 | 0
2139 | 0.12485 | 0
2140 | 0.12485 | 0
2141 | 0.12485 | 0
2142 | 12.5359 | 13.6036
2143 | 1.4721 | 0
2144 | 1.8774 | 0
2145 | 0.12485 | 0
2146 | 0.12485 | 0
2147 | 0.12485 | 0
2148 | 0.97773 | 0
2149 | 0.12485 | 0
2150 | 0.12485 | 0
2151 | 0.12485 | 0
2152 | 0.12485 | 0
2153 | 0.12485 | 0
2154 | 6.4458 | 6.9363
2155 | 12.5006 | 19.0111
2156 | 0.12485 | 0
2157 | 1.5018 | 0
2158 | 0.12485 | 0
2159 | 0.12485 | 0
2160 | 0.12485 | 0
2161 | 0.12485 | 0
2162 | 0.12485 | 0
2163 | 0.12485 | 0
2164 | 0.12485 | 0
2165 | 0.12485 | 0
2166 | 12.5233 | 13.5876
2167 | 1.4706 | 0
2168 | 1.8756 | 0
2169 | 0.12485 | 0
2170 | 0.12485 | 0
2171 | 0.12485 | 0
2172 | 0.97682 | 0
2173 | 0.12485 | 0
2174 | 0.12485 | 0
2175 | 0.12485 | 0
2176 | 0.12485 | 0
2177 | 0.12485 | 0
2178 | 6.4392 | 6.9345
2179 | 12.4889 | 18.9946
2180 | 0.12485 | 0
2181 | 1.5005 | 0
2182 | 0.12485 | 0
2183 | 0.12485 | 0
2184 | 0.12485 | 0
2185 | 0.12485 | 0
2186 | 0.12485 | 0
2187 | 0.12485 | 0
2188 | 0.12485 | 0
2189 | 0.12485 | 0
2190 | 12.5106 | 13.5713
2191 | 1.4692 | 0
2192 | 1.8737 | 0
2193 | 0.12485 | 0
2194 | 0.12485 | 0
2195 | 0.12485 | 0
2196 | 0.97589 | 0
2197 | 0.12485 | 0
2198 | 0.12485 | 0
2199 | 0.12485 | 0
2200 | 0.12485 | 0
2201 | 0.12485 | 0
2202 | 6.4325 | 6.9326
2203 | 12.477 | 18.9778
2204 | 0.12485 | 0
2205 | 1.4991 | 0
2206 | 0.12485 | 0
2207 | 0.12485 | 0
2208 | 0.12485 | 0
2209 | 0.12485 | 0
2210 | 0.12485 | 0
2211 | 0.12485 | 0
2212 | 0.12485 | 0
2213 | 0.12485 | 0
2214 | 12.4976 | 13.5548
2215 | 1.4677 | 0
2216 | 1.8718 | 0
2217 | 0.12485 | 0
2218 | 0.12485 | 0
2219 | 0.12485 | 0
2220 | 0.97494 | 0
2221 | 0.12485 | 0
2222 | 0.12485 | 0
2223 | 0.12485 | 0
2224 | 0.12485 | 0
2225 | 0.12485 | 0
2226 | 6.4256 | 6.9308
2227 | 12.4649 | 18.9607
2228 | 0.12485 | 0
2229 | 1.4977 | 0
2230 | 0.12485 | 0
2231 | 0.12485 | 0
2232 | 0.12485 | 0
2233 | 0.12485 | 0
2234 | 0.12485 | 0
2235 | 0.12485 | 0
2236 | 0.12485 | 0
2237 | 0.12485 | 0
2238 | 12.4844 | 13.538
2239 | 1.4662 | 0
2240 | 1.8698 | 0
2241 | 0.12485 | 0
2242 | 0.12485 | 0
2243 | 0.12485 | 0
2244 | 0.97398 | 0
2245 | 0.12485 | 0
2246 | 0.12485 | 0
2247 | 0.12485 | 0
2248 | 0.12485 | 0
2249 | 0.12485 | 0
2250 | 6.4187 | 6.9289
2251 | 12.4526 | 18.9433
2252 | 0.12485 | 0
2253 | 1.4963 | 0
2254 | 0.12485 | 0
2255 | 0.12485 | 0
2256 | 0.12485 | 0
2257 | 0.12485 | 0
2258 | 0.12485 | 0
2259 | 0.12485 | 0
2260 | 0.12485 | 0
2261 | 0.12485 | 0
2262 | 12.4711 | 13.521
2263 | 1.4647 | 0
2264 | 1.8678 | 0
2265 | 0.12485 | 0
2266 | 0.12485 | 0
2267 | 0.12485 | 0
2268 | 0.973 | 0
2269 | 0.12485 | 0
2270 | 0.12485 | 0
2271 | 0.12485 | 0
2272 | 0.12485 | 0
2273 | 0.12485 | 0
2274 | 6.4116 | 6.9269
2275 | 12.4401 | 13.5845
2276 | 0.12485 | 0
2277 | 1.3921 | 0
2278 | 0.12485 | 0
2279 | 0.12485 | 0
2280 | 0.12485 | 0
2281 | 0.12485 | 0
2282 | 0.12485 | 0
2283 | 0.12485 | 0
2284 | 0.12485 | 0
2285 | 0.12485 | 0
2286 | 12.1957 | 19.3536
2287 | 1.4826 | 0
2288 | 1.8911 | 0
2289 | 0.12485 | 0
2290 | 0.12485 | 0
2291 | 0.12485 | 0
2292 | 0.98427 | 0
2293 | 0.12485 | 0
2294 | 0.12485 | 0
2295 | 0.12485 | 0
2296 | 0.12485 | 0
2297 | 0.12485 | 0
2298 | 6.4878 | 6.8781
2299 | 12.5685 | 13.6004
2300 | 0.12485 | 0
2301 | 1.4038 | 0
2302 | 0.12485 | 0
2303 | 0.12485 | 0
2304 | 0.12485 | 0
2305 | 0.12485 | 0
2306 | 0.12485 | 0
2307 | 0.12485 | 0
2308 | 0.12485 | 0
2309 | 0.12485 | 0
2310 | 12.2985 | 19.1656
2311 | 1.4882 | 0
2312 | 1.8983 | 0
2313 | 0.12485 | 0
2314 | 0.12485 | 0
2315 | 0.12485 | 0
2316 | 0.98775 | 0
2317 | 0.12485 | 0
2318 | 0.12485 | 0
2319 | 0.12485 | 0
2320 | 0.12485 | 0
2321 | 0.12485 | 0
2322 | 6.2997 | 7.0639
2323 | 12.6621 | 13.4065
2324 | 0.12485 | 0
2325 | 1.4104 | 0
2326 | 0.12485 | 0
2327 | 0.12485 | 0
2328 | 0.12485 | 0
2329 | 0.12485 | 0
2330 | 0.12485 | 0
2331 | 0.12485 | 0
2332 | 0.12485 | 0
2333 | 0.12485 | 0
2334 | 12.3567 | 13.699
2335 | 1.388 | 0
2336 | 1.7682 | 6.5052
2337 | 0.12485 | 0
2338 | 0.12485 | 0
2339 | 0.12485 | 0
2340 | 1.0077 | 0
2341 | 0.12485 | 0
2342 | 0.12485 | 0
2343 | 0.12485 | 0
2344 | 0.12485 | 0
2345 | 0.12485 | 0
2346 | 6.4346 | 6.8414
2347 | 12.6515 | 13.5822
2348 | 0.12485 | 0
2349 | 1.4358 | 0
2350 | 0.12485 | 0
2351 | 0.12485 | 0
2352 | 0.12485 | 0
2353 | 0.12485 | 0
2354 | 0.12485 | 0
2355 | 0.12485 | 0
2356 | 0.12485 | 0
2357 | 0.12485 | 0
2358 | 12.5626 | 13.5386
2359 | 1.4051 | 0
2360 | 1.7904 | 0
2361 | 0.12485 | 0
2362 | 0.12485 | 0
2363 | 0.12485 | 0
2364 | 0.98009 | 6.5265
2365 | 0.12485 | 0
2366 | 0.12485 | 0
2367 | 0.12485 | 0
2368 | 0.12485 | 0
2369 | 0.12485 | 0
2370 | 6.406 | 6.8373
2371 | 12.4133 | 13.3372
2372 | 0.12485 | 0
2373 | 1.454 | 0
2374 | 0.12485 | 0
2375 | 0.12485 | 0
2376 | 0.12485 | 0
2377 | 0.12485 | 0
2378 | 0.12485 | 0
2379 | 0.12485 | 0
2380 | 0.12485 | 0
2381 | 0.12485 | 0
2382 | 12.7135 | 13.3191
2383 | 1.4153 | 0
2384 | 1.8037 | 0
2385 | 0.12485 | 0
2386 | 0.12485 | 0
2387 | 0.12485 | 0
2388 | 0.94184 | 6.4474
2389 | 0.12485 | 0
2390 | 0.12485 | 0
2391 | 0.12485 | 0
2392 | 0.12485 | 0
2393 | 0.12485 | 0
2394 | 6.4478 | 6.7152
2395 | 12.4637 | 13.2185
2396 | 0.12485 | 0
2397 | 1.4562 | 0
2398 | 0.12485 | 0
2399 | 0.12485 | 0
2400 | 0.12485 | 0
2401 | 0.12485 | 0
2402 | 0.12485 | 0
2403 | 0.12485 | 0
2404 | 0.12485 | 0
2405 | 0.12485 | 0
2406 | 12.7294 | 13.2437
2407 | 1.4157 | 0
2408 | 1.8041 | 0
2409 | 0.12485 | 0
2410 | 0.12485 | 0
2411 | 0.12485 | 0
2412 | 0.94202 | 6.3988
2413 | 0.12485 | 0
2414 | 0.12485 | 0
2415 | 0.12485 | 0
2416 | 0.12485 | 0
2417 | 0.12485 | 0
2418 | 6.4445 | 6.684
2419 | 12.4523 | 13.195
2420 | 0.12485 | 0
2421 | 1.4548 | 0
2422 | 0.12485 | 0
2423 | 0.12485 | 0
2424 | 0.12485 | 0
2425 | 0.12485 | 0
2426 | 0.12485 | 0
2427 | 0.12485 | 0
2428 | 0.12485 | 0
2429 | 0.12485 | 0
2430 | 12.715 | 13.2242
2431 | 1.4141 | 0
2432 | 1.802 | 0
2433 | 0.12485 | 0
2434 | 0.12485 | 0
2435 | 0.12485 | 0
2436 | 0.941 | 6.3839
2437 | 0.12485 | 0
2438 | 0.12485 | 0
2439 | 0.12485 | 0
2440 | 0.12485 | 0
2441 | 0.12485 | 0
2442 | 6.4359 | 6.6715
2443 | 12.4351 | 13.1806
2444 | 0.12485 | 0
2445 | 1.453 | 0
2446 | 0.12485 | 0
2447 | 0.12485 | 0
2448 | 0.12485 | 0
2449 | 0.12485 | 0
2450 | 0.12485 | 0
2451 | 0.12485 | 0
2452 | 0.12485 | 0
2453 | 0.12485 | 0
2454 | 12.6978 | 13.2094
2455 | 1.4123 | 0
2456 | 1.7997 | 0
2457 | 0.12485 | 0
2458 | 0.12485 | 0
2459 | 0.12485 | 0
2460 | 0.93986 | 6.3719
2461 | 0.12485 | 0
2462 | 0.12485 | 0
2463 | 0.12485 | 0
2464 | 0.12485 | 0
2465 | 0.12485 | 0
2466 | 6.4267 | 6.6607
2467 | 12.4171 | 13.1669
2468 | 0.12485 | 0
2469 | 1.4511 | 0
2470 | 0.12485 | 0
2471 | 0.12485 | 0
2472 | 0.12485 | 0
2473 | 0.12485 | 0
2474 | 0.12485 | 0
2475 | 0.12485 | 0
2476 | 0.12485 | 0
2477 | 0.12485 | 0
2478 | 12.6801 | 13.1949
2479 | 1.4105 | 0
2480 | 1.7973 | 0
2481 | 0.12485 | 0
2482 | 0.12485 | 0
2483 | 0.12485 | 0
2484 | 0.93871 | 6.3674
2485 | 0.12485 | 0
2486 | 0.12485 | 0
2487 | 0.12485 | 0
2488 | 0.12485 | 0
2489 | 0.12485 | 0
2490 | 6.4182 | 6.6466
2491 | 12.4 | 13.1516
2492 | 0.12485 | 0
2493 | 1.4493 | 0
2494 | 0.12485 | 0
2495 | 0.12485 | 0
2496 | 0.12485 | 0
2497 | 0.12485 | 0
2498 | 0.12485 | 0
2499 | 0.12485 | 0
2500 | 0.12485 | 0
2501 | 0.12485 | 0
2502 | 12.6627 | 13.1795
2503 | 1.4087 | 0
2504 | 1.795 | 0
2505 | 0.12485 | 0
2506 | 0.12485 | 0
2507 | 0.12485 | 0
2508 | 0.93755 | 6.3697
2509 | 0.12485 | 0
2510 | 0.12485 | 0
2511 | 0.12485 | 0
2512 | 0.12485 | 0
2513 | 0.12485 | 0
2514 | 6.4107 | 6.6288
2515 | 12.3836 | 13.1343
2516 | 0.12485 | 0
2517 | 1.4475 | 0
2518 | 0.12485 | 0
2519 | 0.12485 | 0
2520 | 0.12485 | 0
2521 | 0.12485 | 0
2522 | 0.12485 | 0
2523 | 0.12485 | 0
2524 | 0.12485 | 0
2525 | 0.12485 | 0
2526 | 12.4451 | 13.6756
2527 | 1.4206 | 0
2528 | 1.8104 | 0
2529 | 0.12485 | 0
2530 | 0.12485 | 0
2531 | 0.12485 | 0
2532 | 0.94498 | 0
2533 | 0.12485 | 0
2534 | 0.12485 | 0
2535 | 0.12485 | 0
2536 | 0.12485 | 0
2537 | 0.12485 | 0
2538 | 6.2137 | 6.9245
2539 | 12.0952 | 19.0045
2540 | 0.12485 | 0
2541 | 1.4656 | 0
2542 | 0.12485 | 0
2543 | 0.12485 | 0
2544 | 0.12485 | 0
2545 | 0.12485 | 0
2546 | 0.12485 | 0
2547 | 0.12485 | 0
2548 | 0.12485 | 0
2549 | 0.12485 | 0
2550 | 12.1929 | 13.4712
2551 | 1.4388 | 0
2552 | 1.8341 | 0
2553 | 0.12485 | 0
2554 | 0.12485 | 0
2555 | 0.12485 | 0
2556 | 0.95644 | 0
2557 | 0.12485 | 0
2558 | 0.12485 | 0
2559 | 0.12485 | 0
2560 | 0.12485 | 0
2561 | 0.12485 | 0
2562 | 6.2932 | 6.9119
2563 | 12.2323 | 13.5631
2564 | 0.12485 | 0
2565 | 1.3731 | 0
2566 | 0.12485 | 0
2567 | 0.12485 | 0
2568 | 0.12485 | 0
2569 | 0.12485 | 0
2570 | 0.12485 | 0
2571 | 0.12485 | 0
2572 | 0.12485 | 0
2573 | 0.12485 | 0
2574 | 12.0196 | 19.1374
2575 | 1.4628 | 0
2576 | 1.8652 | 0
2577 | 0.12485 | 0
2578 | 0.12485 | 0
2579 | 0.12485 | 0
2580 | 0.97154 | 0
2581 | 0.12485 | 0
2582 | 0.12485 | 0
2583 | 0.12485 | 0
2584 | 0.12485 | 0
2585 | 0.12485 | 0
2586 | 6.1843 | 7.0485
2587 | 12.4558 | 13.2954
2588 | 0.12485 | 0
2589 | 1.3902 | 0
2590 | 0.12485 | 0
2591 | 0.12485 | 0
2592 | 0.12485 | 0
2593 | 0.12485 | 0
2594 | 0.12485 | 0
2595 | 0.12485 | 0
2596 | 0.12485 | 0
2597 | 0.12485 | 0
2598 | 12.169 | 13.6704
2599 | 1.3708 | 0
2600 | 1.7458 | 6.3446
2601 | 0.12485 | 0
2602 | 0.12485 | 0
2603 | 0.12485 | 0
2604 | 0.99458 | 0
2605 | 0.12485 | 0
2606 | 0.12485 | 0
2607 | 0.12485 | 0
2608 | 0.12485 | 0
2609 | 0.12485 | 0
2610 | 6.3404 | 6.7875
2611 | 12.0767 | 13.5039
2612 | 0.12485 | 0
2613 | 1.4267 | 0
2614 | 0.12485 | 0
2615 | 0.12485 | 0
2616 | 0.12485 | 0
2617 | 0.12485 | 0
2618 | 0.12485 | 0
2619 | 0.12485 | 0
2620 | 0.12485 | 0
2621 | 0.12485 | 0
2622 | 12.4661 | 13.2985
2623 | 1.3928 | 0
2624 | 1.7743 | 0
2625 | 0.12485 | 0
2626 | 0.12485 | 0
2627 | 0.12485 | 0
2628 | 0.92744 | 6.4032
2629 | 0.12485 | 0
2630 | 0.12485 | 0
2631 | 0.12485 | 0
2632 | 0.12485 | 0
2633 | 0.12485 | 0
2634 | 6.3414 | 6.6482
2635 | 12.267 | 13.0999
2636 | 0.12485 | 0
2637 | 1.4364 | 0
2638 | 0.12485 | 0
2639 | 0.12485 | 0
2640 | 0.12485 | 0
2641 | 0.12485 | 0
2642 | 0.12485 | 0
2643 | 0.12485 | 0
2644 | 0.12485 | 0
2645 | 0.12485 | 0
2646 | 12.3432 | 13.6633
2647 | 1.4113 | 0
2648 | 1.7983 | 0
2649 | 0.12485 | 0
2650 | 0.12485 | 0
2651 | 0.12485 | 0
2652 | 0.939 | 0
2653 | 0.12485 | 0
2654 | 0.12485 | 0
2655 | 0.12485 | 0
2656 | 0.12485 | 0
2657 | 0.12485 | 0
2658 | 6.1709 | 6.9204
2659 | 12.02 | 18.9029
2660 | 0.12485 | 0
2661 | 1.457 | 0
2662 | 0.12485 | 0
2663 | 0.12485 | 0
2664 | 0.12485 | 0
2665 | 0.12485 | 0
2666 | 0.12485 | 0
2667 | 0.12485 | 0
2668 | 0.12485 | 0
2669 | 0.12485 | 0
2670 | 12.1129 | 13.3713
2671 | 1.4298 | 0
2672 | 1.8223 | 0
2673 | 0.12485 | 0
2674 | 0.12485 | 0
2675 | 0.12485 | 0
2676 | 0.95064 | 0
2677 | 0.12485 | 0
2678 | 0.12485 | 0
2679 | 0.12485 | 0
2680 | 0.12485 | 0
2681 | 0.12485 | 0
2682 | 6.2511 | 6.9005
2683 | 12.158 | 13.5559
2684 | 0.12485 | 0
2685 | 1.3664 | 0
2686 | 0.12485 | 0
2687 | 0.12485 | 0
2688 | 0.12485 | 0
2689 | 0.12485 | 0
2690 | 0.12485 | 0
2691 | 0.12485 | 0
2692 | 0.12485 | 0
2693 | 0.12485 | 0
2694 | 11.9561 | 19.0155
2695 | 1.4548 | 0
2696 | 1.8548 | 0
2697 | 0.12485 | 0
2698 | 0.12485 | 0
2699 | 0.12485 | 0
2700 | 0.96639 | 0
2701 | 0.12485 | 0
2702 | 0.12485 | 0
2703 | 0.12485 | 0
2704 | 0.12485 | 0
2705 | 0.12485 | 0
2706 | 6.1471 | 7.034
2707 | 12.3854 | 13.1831
2708 | 0.12485 | 0
2709 | 1.3822 | 0
2710 | 0.12485 | 0
2711 | 0.12485 | 0
2712 | 0.12485 | 0
2713 | 0.12485 | 0
2714 | 0.12485 | 0
2715 | 0.12485 | 0
2716 | 0.12485 | 0
2717 | 0.12485 | 0
2718 | 12.0932 | 13.6544
2719 | 1.3639 | 0
2720 | 1.7367 | 0
2721 | 0.12485 | 0
2722 | 0.12485 | 6.3461
2723 | 0.12485 | 0
2724 | 0.99056 | 0
2725 | 0.12485 | 0
2726 | 0.12485 | 0
2727 | 0.12485 | 0
2728 | 0.12485 | 0
2729 | 0.12485 | 0
2730 | 6.1973 | 6.8681
2731 | 12.057 | 13.2488
2732 | 0.12485 | 0
2733 | 1.4204 | 0
2734 | 0.12485 | 0
2735 | 0.12485 | 0
2736 | 0.12485 | 0
2737 | 0.12485 | 0
2738 | 0.12485 | 0
2739 | 0.12485 | 0
2740 | 0.12485 | 0
2741 | 0.12485 | 0
2742 | 12.4013 | 13.1625
2743 | 1.385 | 0
2744 | 1.7641 | 0
2745 | 0.12485 | 0
2746 | 0.12485 | 0
2747 | 0.12485 | 0
2748 | 0.92238 | 0
2749 | 0.12485 | 6.3633
2750 | 0.12485 | 0
2751 | 0.12485 | 0
2752 | 0.12485 | 0
2753 | 0.12485 | 0
2754 | 6.3033 | 6.5436
2755 | 12.1822 | 13.0028
2756 | 0.12485 | 0
2757 | 1.4269 | 0
2758 | 0.12485 | 0
2759 | 0.12485 | 0
2760 | 0.12485 | 0
2761 | 0.12485 | 0
2762 | 0.12485 | 0
2763 | 0.12485 | 0
2764 | 0.12485 | 0
2765 | 0.12485 | 0
2766 | 11.8474 | 13.6135
2767 | 1.4105 | 0
2768 | 1.7972 | 0
2769 | 0.12485 | 0
2770 | 0.12485 | 0
2771 | 0.12485 | 0
2772 | 0.9384 | 0
2773 | 0.12485 | 0
2774 | 0.12485 | 0
2775 | 0.12485 | 0
2776 | 0.12485 | 0
2777 | 0.12485 | 0
2778 | 6.1653 | 6.9112
2779 | 12.0094 | 13.5389
2780 | 0.12485 | 0
2781 | 1.3528 | 0
2782 | 0.12485 | 0
2783 | 0.12485 | 0
2784 | 0.12485 | 0
2785 | 0.12485 | 0
2786 | 0.12485 | 0
2787 | 0.12485 | 0
2788 | 0.12485 | 0
2789 | 0.12485 | 0
2790 | 11.8335 | 19.0178
2791 | 1.4439 | 0
2792 | 1.8406 | 0
2793 | 0.12485 | 0
2794 | 0.12485 | 0
2795 | 0.12485 | 0
2796 | 0.95945 | 0
2797 | 0.12485 | 0
2798 | 0.12485 | 0
2799 | 0.12485 | 0
2800 | 0.12485 | 0
2801 | 0.12485 | 0
2802 | 6.0978 | 7.0286
2803 | 12.2975 | 13.1389
2804 | 0.12485 | 0
2805 | 1.3736 | 0
2806 | 0.12485 | 0
2807 | 0.12485 | 0
2808 | 0.12485 | 0
2809 | 0.12485 | 0
2810 | 0.12485 | 0
2811 | 0.12485 | 0
2812 | 0.12485 | 0
2813 | 0.12485 | 0
2814 | 12.0144 | 13.6434
2815 | 1.3567 | 0
2816 | 1.7273 | 0
2817 | 0.12485 | 0
2818 | 0.12485 | 0
2819 | 0.12485 | 0
2820 | 0.94909 | 6.5163
2821 | 0.12485 | 0
2822 | 0.12485 | 0
2823 | 0.12485 | 0
2824 | 0.12485 | 0
2825 | 0.12485 | 0
2826 | 6.1853 | 6.816
2827 | 12.0266 | 13.1141
2828 | 0.12485 | 0
2829 | 1.4151 | 0
2830 | 0.12485 | 0
2831 | 0.12485 | 0
2832 | 0.12485 | 0
2833 | 0.12485 | 0
2834 | 0.12485 | 0
2835 | 0.12485 | 0
2836 | 0.12485 | 0
2837 | 0.12485 | 0
2838 | 12.1498 | 13.6455
2839 | 1.3937 | 0
2840 | 1.7753 | 0
2841 | 0.12485 | 0
2842 | 0.12485 | 0
2843 | 0.12485 | 0
2844 | 0.92772 | 0
2845 | 0.12485 | 0
2846 | 0.12485 | 0
2847 | 0.12485 | 0
2848 | 0.12485 | 0
2849 | 0.12485 | 0
2850 | 6.0901 | 6.9122
2851 | 11.8784 | 13.5239
2852 | 0.12485 | 0
2853 | 1.3409 | 0
2854 | 0.12485 | 0
2855 | 0.12485 | 0
2856 | 0.12485 | 0
2857 | 0.12485 | 0
2858 | 0.12485 | 0
2859 | 0.12485 | 0
2860 | 0.12485 | 0
2861 | 0.12485 | 0
2862 | 11.7259 | 19.0398
2863 | 1.4348 | 0
2864 | 1.8287 | 0
2865 | 0.12485 | 0
2866 | 0.12485 | 0
2867 | 0.12485 | 0
2868 | 0.9536 | 0
2869 | 0.12485 | 0
2870 | 0.12485 | 0
2871 | 0.12485 | 0
2872 | 0.12485 | 0
2873 | 0.12485 | 0
2874 | 6.0563 | 7.0258
2875 | 12.2243 | 13.1147
2876 | 0.12485 | 0
2877 | 1.3667 | 0
2878 | 0.12485 | 0
2879 | 0.12485 | 0
2880 | 0.12485 | 0
2881 | 0.12485 | 0
2882 | 0.12485 | 0
2883 | 0.12485 | 0
2884 | 0.12485 | 0
2885 | 0.12485 | 0
2886 | 11.9509 | 13.6354
2887 | 1.3509 | 0
2888 | 1.7197 | 0
2889 | 0.12485 | 0
2890 | 0.12485 | 0
2891 | 0.12485 | 0
2892 | 0.90076 | 6.6088
2893 | 0.12485 | 0
2894 | 0.12485 | 0
2895 | 0.12485 | 0
2896 | 0.12485 | 0
2897 | 0.12485 | 0
2898 | 6.1713 | 6.7233
2899 | 11.9857 | 13.0341
2900 | 0.12485 | 0
2901 | 1.4099 | 0
2902 | 0.12485 | 0
2903 | 0.12485 | 0
2904 | 0.12485 | 0
2905 | 0.12485 | 0
2906 | 0.12485 | 0
2907 | 0.12485 | 0
2908 | 0.12485 | 0
2909 | 0.12485 | 0
2910 | 11.6934 | 13.5784
2911 | 1.396 | 0
2912 | 1.7784 | 0
2913 | 0.12485 | 0
2914 | 0.12485 | 0
2915 | 0.12485 | 0
2916 | 0.92914 | 0
2917 | 0.12485 | 0
2918 | 0.12485 | 0
2919 | 0.12485 | 0
2920 | 0.12485 | 0
2921 | 0.12485 | 0
2922 | 6.099 | 6.9013
2923 | 11.8929 | 13.5269
2924 | 0.12485 | 0
2925 | 1.3422 | 0
2926 | 0.12485 | 0
2927 | 0.12485 | 0
2928 | 0.12485 | 0
2929 | 0.12485 | 0
2930 | 0.12485 | 0
2931 | 0.12485 | 0
2932 | 0.12485 | 0
2933 | 0.12485 | 0
2934 | 11.7355 | 13.6344
2935 | 1.3314 | 0
2936 | 1.6945 | 6.3678
2937 | 0.12485 | 0
2938 | 0.12485 | 0
2939 | 0.12485 | 0
2940 | 0.96971 | 0
2941 | 0.12485 | 0
2942 | 0.12485 | 0
2943 | 0.12485 | 0
2944 | 0.12485 | 0
2945 | 0.12485 | 0
2946 | 6.05 | 6.8849
2947 | 11.8046 | 13.2181
2948 | 0.12485 | 0
2949 | 1.3972 | 0
2950 | 0.12485 | 0
2951 | 0.12485 | 0
2952 | 0.12485 | 0
2953 | 0.12485 | 0
2954 | 0.12485 | 0
2955 | 0.12485 | 0
2956 | 0.12485 | 0
2957 | 0.12485 | 0
2958 | 11.9895 | 13.6385
2959 | 1.3791 | 0
2960 | 1.7564 | 0
2961 | 0.12485 | 0
2962 | 0.12485 | 0
2963 | 0.12485 | 0
2964 | 0.91844 | 0
2965 | 0.12485 | 0
2966 | 0.12485 | 0
2967 | 0.12485 | 0
2968 | 0.12485 | 0
2969 | 0.12485 | 0
2970 | 6.0239 | 6.9049
2971 | 11.7624 | 13.5118
2972 | 0.12485 | 0
2973 | 1.3303 | 0
2974 | 0.12485 | 0
2975 | 0.12485 | 0
2976 | 0.12485 | 0
2977 | 0.12485 | 0
2978 | 0.12485 | 0
2979 | 0.12485 | 0
2980 | 0.12485 | 0
2981 | 0.12485 | 0
2982 | 11.6291 | 13.6224
2983 | 1.3217 | 0
2984 | 1.6819 | 6.4346
2985 | 0.12485 | 0
2986 | 0.12485 | 0
2987 | 0.12485 | 0
2988 | 0.96439 | 0
2989 | 0.12485 | 0
2990 | 0.12485 | 0
2991 | 0.12485 | 0
2992 | 0.12485 | 0
2993 | 0.12485 | 0
2994 | 6.1263 | 6.7811
2995 | 11.7042 | 13.34
2996 | 0.12485 | 0
2997 | 1.3902 | 0
2998 | 0.12485 | 0
2999 | 0.12485 | 0
3000 | 0.12485 | 0
3001 | 0.12485 | 0
3002 | 0.12485 | 0
3003 | 0.12485 | 0
3004 | 0.12485 | 0
3005 | 0.12485 | 0
3006 | 11.9271 | 13.6352
3007 | 1.3735 | 0
3008 | 1.749 | 0
3009 | 0.12485 | 0
3010 | 0.12485 | 0
3011 | 0.12485 | 0
3012 | 0.91482 | 0
3013 | 0.12485 | 0
3014 | 0.12485 | 0
3015 | 0.12485 | 0
3016 | 0.12485 | 0
3017 | 0.12485 | 0
3018 | 5.9981 | 6.9022
3019 | 11.7172 | 13.5071
3020 | 0.12485 | 0
3021 | 1.3262 | 0
3022 | 0.12485 | 0
3023 | 0.12485 | 0
3024 | 0.12485 | 0
3025 | 0.12485 | 0
3026 | 0.12485 | 0
3027 | 0.12485 | 0
3028 | 0.12485 | 0
3029 | 0.12485 | 0
3030 | 11.5913 | 13.6186
3031 | 1.3183 | 0
3032 | 1.6774 | 6.3975
3033 | 0.12485 | 0
3034 | 0.12485 | 0
3035 | 0.12485 | 0
3036 | 0.96171 | 0
3037 | 0.12485 | 0
3038 | 0.12485 | 0
3039 | 0.12485 | 0
3040 | 0.12485 | 0
3041 | 0.12485 | 0
3042 | 5.9932 | 6.8817
3043 | 11.7056 | 13.1793
3044 | 0.12485 | 0
3045 | 1.3876 | 0
3046 | 0.12485 | 0
3047 | 0.12485 | 0
3048 | 0.12485 | 0
3049 | 0.12485 | 0
3050 | 0.12485 | 0
3051 | 0.12485 | 0
3052 | 0.12485 | 0
3053 | 0.12485 | 0
3054 | 11.9018 | 13.6272
3055 | 1.3711 | 0
3056 | 1.7459 | 0
3057 | 0.12485 | 0
3058 | 0.12485 | 0
3059 | 0.12485 | 0
3060 | 0.91329 | 0
3061 | 0.12485 | 0
3062 | 0.12485 | 0
3063 | 0.12485 | 0
3064 | 0.12485 | 0
3065 | 0.12485 | 0
3066 | 5.987 | 6.9013
3067 | 11.6977 | 13.5051
3068 | 0.12485 | 0
3069 | 1.3244 | 0
3070 | 0.12485 | 0
3071 | 0.12485 | 0
3072 | 0.12485 | 0
3073 | 0.12485 | 0
3074 | 0.12485 | 0
3075 | 0.12485 | 0
3076 | 0.12485 | 0
3077 | 0.12485 | 0
3078 | 11.5743 | 13.6173
3079 | 1.3168 | 0
3080 | 1.6753 | 6.3288
3081 | 0.12485 | 0
3082 | 0.12485 | 0
3083 | 0.12485 | 0
3084 | 0.95981 | 0
3085 | 0.12485 | 0
3086 | 0.12485 | 0
3087 | 0.12485 | 0
3088 | 0.12485 | 0
3089 | 0.12485 | 0
3090 | 5.9796 | 6.8746
3091 | 11.6806 | 13.1226
3092 | 0.12485 | 0
3093 | 1.3843 | 0
3094 | 0.12485 | 0
3095 | 0.12485 | 0
3096 | 0.12485 | 0
3097 | 0.12485 | 0
3098 | 0.12485 | 0
3099 | 0.12485 | 0
3100 | 0.12485 | 0
3101 | 0.12485 | 0
3102 | 11.8707 | 13.6145
3103 | 1.3681 | 0
3104 | 1.742 | 0
3105 | 0.12485 | 0
3106 | 0.12485 | 0
3107 | 0.12485 | 0
3108 | 0.91137 | 0
3109 | 0.12485 | 0
3110 | 0.12485 | 0
3111 | 0.12485 | 0
3112 | 0.12485 | 0
3113 | 0.12485 | 0
3114 | 5.973 | 6.8977
3115 | 11.6729 | 13.5027
3116 | 0.12485 | 0
3117 | 1.3222 | 0
3118 | 0.12485 | 0
3119 | 0.12485 | 0
3120 | 0.12485 | 0
3121 | 0.12485 | 0
3122 | 0.12485 | 0
3123 | 0.12485 | 0
3124 | 0.12485 | 0
3125 | 0.12485 | 0
3126 | 11.5531 | 13.6154
3127 | 1.3148 | 0
3128 | 1.6728 | 0
3129 | 0.12485 | 6.3326
3130 | 0.12485 | 0
3131 | 0.12485 | 0
3132 | 0.95889 | 0
3133 | 0.12485 | 0
3134 | 0.12485 | 0
3135 | 0.12485 | 0
3136 | 0.12485 | 0
3137 | 0.12485 | 0
3138 | 5.9727 | 6.8551
3139 | 11.6651 | 13.051
3140 | 0.12485 | 0
3141 | 1.3815 | 0
3142 | 0.12485 | 0
3143 | 0.12485 | 0
3144 | 0.12485 | 0
3145 | 0.12485 | 0
3146 | 0.12485 | 0
3147 | 0.12485 | 0
3148 | 0.12485 | 0
3149 | 0.12485 | 0
3150 | 11.4369 | 13.4933
3151 | 1.3714 | 0
3152 | 1.7463 | 0
3153 | 0.12485 | 0
3154 | 0.12485 | 0
3155 | 0.12485 | 0
3156 | 0.91339 | 0
3157 | 0.12485 | 0
3158 | 0.12485 | 0
3159 | 0.12485 | 0
3160 | 0.12485 | 0
3161 | 0.12485 | 0
3162 | 5.9862 | 6.8842
3163 | 11.6946 | 13.5066
3164 | 0.12485 | 0
3165 | 1.3242 | 0
3166 | 0.12485 | 0
3167 | 0.12485 | 0
3168 | 0.12485 | 0
3169 | 0.12485 | 0
3170 | 0.12485 | 0
3171 | 0.12485 | 0
3172 | 0.12485 | 0
3173 | 0.12485 | 0
3174 | 11.5692 | 13.6164
3175 | 1.3163 | 0
3176 | 1.6747 | 0
3177 | 0.12485 | 0
3178 | 0.12485 | 0
3179 | 0.12485 | 0
3180 | 0.87868 | 6.6071
3181 | 0.12485 | 0
3182 | 0.12485 | 0
3183 | 0.12485 | 0
3184 | 0.12485 | 0
3185 | 0.12485 | 0
3186 | 6.0143 | 6.6701
3187 | 11.7039 | 12.8903
3188 | 0.12485 | 0
3189 | 1.3819 | 0
3190 | 0.12485 | 0
3191 | 0.12485 | 0
3192 | 0.12485 | 0
3193 | 0.12485 | 0
3194 | 0.12485 | 0
3195 | 0.12485 | 0
3196 | 0.12485 | 0
3197 | 0.12485 | 0
3198 | 11.4389 | 13.3864
3199 | 1.3696 | 0
3200 | 1.7439 | 0
3201 | 0.12485 | 0
3202 | 0.12485 | 0
3203 | 0.12485 | 0
3204 | 0.91219 | 0
3205 | 0.12485 | 0
3206 | 0.12485 | 0
3207 | 0.12485 | 0
3208 | 0.12485 | 0
3209 | 0.12485 | 0
3210 | 5.977 | 6.8755
3211 | 11.6768 | 13.4781
3212 | 0.12485 | 0
3213 | 1.3221 | 0
3214 | 0.12485 | 0
3215 | 0.12485 | 0
3216 | 0.12485 | 0
3217 | 0.12485 | 0
3218 | 0.12485 | 0
3219 | 0.12485 | 0
3220 | 0.12485 | 0
3221 | 0.12485 | 0
3222 | 11.5495 | 13.6096
3223 | 1.3145 | 0
3224 | 1.6723 | 0
3225 | 0.12485 | 0
3226 | 0.12485 | 0
3227 | 0.12485 | 0
3228 | 0.87747 | 6.5426
3229 | 0.12485 | 0
3230 | 0.12485 | 0
3231 | 0.12485 | 0
3232 | 0.12485 | 0
3233 | 0.12485 | 0
3234 | 5.9996 | 6.6179
3235 | 11.669 | 12.8448
3236 | 0.12485 | 0
3237 | 1.3779 | 0
3238 | 0.12485 | 0
3239 | 0.12485 | 0
3240 | 0.12485 | 0
3241 | 0.12485 | 0
3242 | 0.12485 | 0
3243 | 0.12485 | 0
3244 | 0.12485 | 0
3245 | 0.12485 | 0
3246 | 11.4024 | 13.3433
3247 | 1.3655 | 0
3248 | 1.7386 | 0
3249 | 0.12485 | 0
3250 | 0.12485 | 0
3251 | 0.12485 | 0
3252 | 0.90958 | 0
3253 | 0.12485 | 0
3254 | 0.12485 | 0
3255 | 0.12485 | 0
3256 | 0.12485 | 0
3257 | 0.12485 | 0
3258 | 5.958 | 6.8705
3259 | 11.642 | 13.4341
3260 | 0.12485 | 0
3261 | 1.3183 | 0
3262 | 0.12485 | 0
3263 | 0.12485 | 0
3264 | 0.12485 | 0
3265 | 0.12485 | 0
3266 | 0.12485 | 0
3267 | 0.12485 | 0
3268 | 0.12485 | 0
3269 | 0.12485 | 0
3270 | 11.5143 | 13.6029
3271 | 1.3113 | 0
3272 | 1.6681 | 0
3273 | 0.12485 | 0
3274 | 0.12485 | 0
3275 | 0.12485 | 0
3276 | 0.87539 | 6.5003
3277 | 0.12485 | 0
3278 | 0.12485 | 0
3279 | 0.12485 | 0
3280 | 0.12485 | 0
3281 | 0.12485 | 0
3282 | 5.9808 | 6.5806
3283 | 11.6297 | 12.8066
3284 | 0.12485 | 0
3285 | 1.3737 | 0
3286 | 0.12485 | 0
3287 | 0.12485 | 0
3288 | 0.12485 | 0
3289 | 0.12485 | 0
3290 | 0.12485 | 0
3291 | 0.12485 | 0
3292 | 0.12485 | 0
3293 | 0.12485 | 0
3294 | 11.3638 | 13.3039
3295 | 1.3613 | 0
3296 | 1.7331 | 0
3297 | 0.12485 | 0
3298 | 0.12485 | 0
3299 | 0.12485 | 0
3300 | 0.90688 | 0
3301 | 0.12485 | 0
3302 | 0.12485 | 0
3303 | 0.12485 | 0
3304 | 0.12485 | 0
3305 | 0.12485 | 0
3306 | 5.9385 | 6.8657
3307 | 11.6063 | 13.3917
3308 | 0.12485 | 0
3309 | 1.3145 | 0
3310 | 0.12485 | 0
3311 | 0.12485 | 0
3312 | 0.12485 | 0
3313 | 0.12485 | 0
3314 | 0.12485 | 0
3315 | 0.12485 | 0
3316 | 0.12485 | 0
3317 | 0.12485 | 0
3318 | 11.4788 | 13.5962
3319 | 1.308 | 0
3320 | 1.6638 | 0
3321 | 0.12485 | 0
3322 | 0.12485 | 0
3323 | 0.12485 | 0
3324 | 0.87328 | 6.4587
3325 | 0.12485 | 0
3326 | 0.12485 | 0
3327 | 0.12485 | 0
3328 | 0.12485 | 0
3329 | 0.12485 | 0
3330 | 5.9619 | 6.5439
3331 | 11.5903 | 12.7687
3332 | 0.12485 | 0
3333 | 1.3694 | 0
3334 | 0.12485 | 0
3335 | 0.12485 | 0
3336 | 0.12485 | 0
3337 | 0.12485 | 0
3338 | 0.12485 | 0
3339 | 0.12485 | 0
3340 | 0.12485 | 0
3341 | 0.12485 | 0
3342 | 11.3252 | 13.2646
3343 | 1.3571 | 0
3344 | 1.7276 | 0
3345 | 0.12485 | 0
3346 | 0.12485 | 0
3347 | 0.12485 | 0
3348 | 0.90418 | 0
3349 | 0.12485 | 0
3350 | 0.12485 | 0
3351 | 0.12485 | 0
3352 | 0.12485 | 0
3353 | 0.12485 | 0
3354 | 5.9191 | 6.8609
3355 | 11.5706 | 13.3493
3356 | 0.12485 | 0
3357 | 1.3106 | 0
3358 | 0.12485 | 0
3359 | 0.12485 | 0
3360 | 0.12485 | 0
3361 | 0.12485 | 0
3362 | 0.12485 | 0
3363 | 0.12485 | 0
3364 | 0.12485 | 0
3365 | 0.12485 | 0
3366 | 11.4432 | 13.5896
3367 | 1.3047 | 0
3368 | 1.6595 | 0
3369 | 0.12485 | 0
3370 | 0.12485 | 0
3371 | 0.12485 | 0
3372 | 0.87117 | 6.4164
3373 | 0.12485 | 0
3374 | 0.12485 | 0
3375 | 0.12485 | 0
3376 | 0.12485 | 0
3377 | 0.12485 | 0
3378 | 5.943 | 6.5075
3379 | 11.5509 | 12.731
3380 | 0.12485 | 0
3381 | 1.3652 | 0
3382 | 0.12485 | 0
3383 | 0.12485 | 0
3384 | 0.12485 | 0
3385 | 0.12485 | 0
3386 | 0.12485 | 0
3387 | 0.12485 | 0
3388 | 0.12485 | 0
3389 | 0.12485 | 0
3390 | 11.2866 | 13.2255
3391 | 1.3529 | 0
3392 | 1.7221 | 0
3393 | 0.12485 | 0
3394 | 0.12485 | 0
3395 | 0.12485 | 0
3396 | 0.90149 | 0
3397 | 0.12485 | 0
3398 | 0.12485 | 0
3399 | 0.12485 | 0
3400 | 0.12485 | 0
3401 | 0.12485 | 0
3402 | 5.8996 | 6.8555
3403 | 11.5348 | 13.3072
3404 | 0.12485 | 0
3405 | 1.3068 | 0
3406 | 0.12485 | 0
3407 | 0.12485 | 0
3408 | 0.12485 | 0
3409 | 0.12485 | 0
3410 | 0.12485 | 0
3411 | 0.12485 | 0
3412 | 0.12485 | 0
3413 | 0.12485 | 0
3414 | 11.4068 | 13.556
3415 | 1.301 | 0
3416 | 1.6546 | 0
3417 | 0.12485 | 0
3418 | 0.12485 | 0
3419 | 0.12485 | 0
3420 | 0.86876 | 6.3801
3421 | 0.12485 | 0
3422 | 0.12485 | 0
3423 | 0.12485 | 0
3424 | 0.12485 | 0
3425 | 0.12485 | 0
3426 | 5.9224 | 6.4774
3427 | 11.5098 | 12.6964
3428 | 0.12485 | 0
3429 | 1.3609 | 0
3430 | 0.12485 | 0
3431 | 0.12485 | 0
3432 | 0.12485 | 0
3433 | 0.12485 | 0
3434 | 0.12485 | 0
3435 | 0.12485 | 0
3436 | 0.12485 | 0
3437 | 0.12485 | 0
3438 | 11.2472 | 13.188
3439 | 1.3487 | 0
3440 | 1.7166 | 0
3441 | 0.12485 | 0
3442 | 0.12485 | 0
3443 | 0.12485 | 0
3444 | 0.89878 | 0
3445 | 0.12485 | 0
3446 | 0.12485 | 0
3447 | 0.12485 | 0
3448 | 0.12485 | 0
3449 | 0.12485 | 0
3450 | 5.8787 | 6.8246
3451 | 11.4946 | 13.2714
3452 | 0.12485 | 0
3453 | 1.3026 | 0
3454 | 0.12485 | 0
3455 | 0.12485 | 0
3456 | 0.12485 | 0
3457 | 0.12485 | 0
3458 | 0.12485 | 0
3459 | 0.12485 | 0
3460 | 0.12485 | 0
3461 | 0.12485 | 0
3462 | 11.3678 | 13.5178
3463 | 1.2969 | 0
3464 | 1.6493 | 0
3465 | 0.12485 | 0
3466 | 0.12485 | 0
3467 | 0.12485 | 0
3468 | 0.86615 | 6.3648
3469 | 0.12485 | 0
3470 | 0.12485 | 0
3471 | 0.12485 | 0
3472 | 0.12485 | 0
3473 | 0.12485 | 0
3474 | 5.9028 | 6.4442
3475 | 11.4698 | 12.6604
3476 | 0.12485 | 0
3477 | 1.3566 | 0
3478 | 0.12485 | 0
3479 | 0.12485 | 0
3480 | 0.12485 | 0
3481 | 0.12485 | 0
3482 | 0.12485 | 0
3483 | 0.12485 | 0
3484 | 0.12485 | 0
3485 | 0.12485 | 0
3486 | 11.2085 | 13.15
3487 | 1.3445 | 0
3488 | 1.7112 | 0
3489 | 0.12485 | 0
3490 | 0.12485 | 0
3491 | 0.12485 | 0
3492 | 0.89609 | 0
3493 | 0.12485 | 0
3494 | 0.12485 | 0
3495 | 0.12485 | 0
3496 | 0.12485 | 0
3497 | 0.12485 | 0
3498 | 5.858 | 6.7933
3499 | 11.4547 | 13.2356
3500 | 0.12485 | 0
3501 | 1.2985 | 0
3502 | 0.12485 | 0
3503 | 0.12485 | 0
3504 | 0.12485 | 0
3505 | 0.12485 | 0
3506 | 0.12485 | 0
3507 | 0.12485 | 0
3508 | 0.12485 | 0
3509 | 0.12485 | 0
3510 | 11.3291 | 13.4796
3511 | 1.2929 | 0
3512 | 1.6441 | 0
3513 | 0.12485 | 0
3514 | 0.12485 | 0
3515 | 0.12485 | 0
3516 | 0.86355 | 0
3517 | 0.12485 | 6.3643
3518 | 0.12485 | 0
3519 | 0.12485 | 0
3520 | 0.12485 | 0
3521 | 0.12485 | 0
3522 | 5.8851 | 6.4044
3523 | 11.432 | 12.6213
3524 | 0.12485 | 0
3525 | 1.3525 | 0
3526 | 0.12485 | 0
3527 | 0.12485 | 0
3528 | 0.12485 | 0
3529 | 0.12485 | 0
3530 | 0.12485 | 0
3531 | 0.12485 | 0
3532 | 0.12485 | 0
3533 | 0.12485 | 0
3534 | 11.1711 | 13.1104
3535 | 1.3404 | 0
3536 | 1.7058 | 0
3537 | 0.12485 | 0
3538 | 0.12485 | 0
3539 | 0.12485 | 0
3540 | 0.89346 | 0
3541 | 0.12485 | 0
3542 | 0.12485 | 0
3543 | 0.12485 | 0
3544 | 0.12485 | 0
3545 | 0.12485 | 0
3546 | 5.8377 | 6.7613
3547 | 11.4153 | 13.1992
3548 | 0.12485 | 0
3549 | 1.2944 | 0
3550 | 0.12485 | 0
3551 | 0.12485 | 0
3552 | 0.12485 | 0
3553 | 0.12485 | 0
3554 | 0.12485 | 0
3555 | 0.12485 | 0
3556 | 0.12485 | 0
3557 | 0.12485 | 0
3558 | 11.2907 | 13.4416
3559 | 1.2889 | 0
3560 | 1.6388 | 0
3561 | 0.12485 | 0
3562 | 0.12485 | 0
3563 | 0.12485 | 0
3564 | 0.86098 | 0
3565 | 0.12485 | 6.364
3566 | 0.12485 | 0
3567 | 0.12485 | 0
3568 | 0.12485 | 0
3569 | 0.12485 | 0
3570 | 5.8676 | 6.3648
3571 | 11.3945 | 12.5824
3572 | 0.12485 | 0
3573 | 1.3484 | 0
3574 | 0.12485 | 0
3575 | 0.12485 | 0
3576 | 0.12485 | 0
3577 | 0.12485 | 0
3578 | 0.12485 | 0
3579 | 0.12485 | 0
3580 | 0.12485 | 0
3581 | 0.12485 | 0
3582 | 11.1339 | 13.0712
3583 | 1.3364 | 0
3584 | 1.7005 | 0
3585 | 0.12485 | 0
3586 | 0.12485 | 0
3587 | 0.12485 | 0
3588 | 0.89085 | 0
3589 | 0.12485 | 0
3590 | 0.12485 | 0
3591 | 0.12485 | 0
3592 | 0.12485 | 0
3593 | 0.12485 | 0
3594 | 5.6116 | 7.0016
3595 | 11.4417 | 12.9052
3596 | 0.12485 | 0
3597 | 1.2934 | 0
3598 | 0.12485 | 0
3599 | 0.12485 | 0
3600 | 0.12485 | 0
3601 | 0.12485 | 0
3602 | 0.12485 | 0
3603 | 0.12485 | 0
3604 | 0.12485 | 0
3605 | 0.12485 | 0
3606 | 11.2771 | 13.3585
3607 | 1.2864 | 0
3608 | 1.6356 | 0
3609 | 0.12485 | 0
3610 | 0.12485 | 0
3611 | 0.12485 | 0
3612 | 0.85939 | 0
3613 | 0.12485 | 0
3614 | 0.12485 | 0
3615 | 0.12485 | 6.366
3616 | 0.12485 | 0
3617 | 0.12485 | 0
3618 | 5.8582 | 0
3619 | 10.9122 | 13.7119
3620 | 0.12485 | 0
3621 | 1.2555 | 0
3622 | 0.12485 | 0
3623 | 0.12485 | 0
3624 | 0.12485 | 0
3625 | 0.12485 | 0
3626 | 0.12485 | 0
3627 | 0.12485 | 0
3628 | 0.12485 | 0
3629 | 0.12485 | 0
3630 | 10.9518 | 13.5503
3631 | 1.2601 | 0
3632 | 1.6014 | 0
3633 | 0.12485 | 0
3634 | 0.12485 | 0
3635 | 0.12485 | 6.336
3636 | 0.92427 | 0
3637 | 0.12485 | 0
3638 | 0.12485 | 0
3639 | 0.12485 | 0
3640 | 0.12485 | 0
3641 | 0.12485 | 0
3642 | 5.7265 | 6.7268
3643 | 11.2151 | 12.7312
3644 | 0.12485 | 0
3645 | 1.3351 | 0
3646 | 0.12485 | 0
3647 | 0.12485 | 0
3648 | 0.12485 | 0
3649 | 0.12485 | 0
3650 | 0.12485 | 0
3651 | 0.12485 | 0
3652 | 0.12485 | 0
3653 | 0.12485 | 0
3654 | 11.016 | 13.1177
3655 | 1.3266 | 0
3656 | 1.6879 | 0
3657 | 0.12485 | 0
3658 | 0.12485 | 0
3659 | 0.12485 | 0
3660 | 0.88466 | 0
3661 | 0.12485 | 0
3662 | 0.12485 | 0
3663 | 0.12485 | 0
3664 | 0.12485 | 0
3665 | 0.12485 | 0
3666 | 5.7744 | 6.7445
3667 | 11.3018 | 13.1394
3668 | 0.12485 | 0
3669 | 1.2833 | 0
3670 | 0.12485 | 0
3671 | 0.12485 | 0
3672 | 0.12485 | 0
3673 | 0.12485 | 0
3674 | 0.12485 | 0
3675 | 0.12485 | 0
3676 | 0.12485 | 0
3677 | 0.12485 | 0
3678 | 11.1879 | 13.3632
3679 | 1.2785 | 0
3680 | 1.6253 | 0
3681 | 0.12485 | 0
3682 | 0.12485 | 0
3683 | 0.12485 | 0
3684 | 0.85431 | 0
3685 | 0.12485 | 0
3686 | 0.12485 | 0
3687 | 0.12485 | 6.3663
3688 | 0.12485 | 0
3689 | 0.12485 | 0
3690 | 5.8223 | 0
3691 | 10.8494 | 13.7016
3692 | 0.12485 | 0
3693 | 1.2498 | 0
3694 | 0.12485 | 0
3695 | 0.12485 | 0
3696 | 0.12485 | 0
3697 | 0.12485 | 0
3698 | 0.12485 | 0
3699 | 0.12485 | 0
3700 | 0.12485 | 0
3701 | 0.12485 | 0
3702 | 10.8996 | 13.5451
3703 | 1.2553 | 0
3704 | 1.5952 | 0
3705 | 0.12485 | 0
3706 | 0.12485 | 0
3707 | 0.12485 | 0
3708 | 0.83971 | 6.568
3709 | 0.12485 | 0
3710 | 0.12485 | 0
3711 | 0.12485 | 0
3712 | 0.12485 | 0
3713 | 0.12485 | 0
3714 | 5.7338 | 6.5484
3715 | 11.1956 | 12.6152
3716 | 0.12485 | 0
3717 | 1.3311 | 0
3718 | 0.12485 | 0
3719 | 0.12485 | 0
3720 | 0.12485 | 0
3721 | 0.12485 | 0
3722 | 0.12485 | 0
3723 | 0.12485 | 0
3724 | 0.12485 | 0
3725 | 0.12485 | 0
3726 | 10.9797 | 13.0303
3727 | 1.3218 | 0
3728 | 1.6815 | 0
3729 | 0.12485 | 0
3730 | 0.12485 | 0
3731 | 0.12485 | 0
3732 | 0.88151 | 0
3733 | 0.12485 | 0
3734 | 0.12485 | 0
3735 | 0.12485 | 0
3736 | 0.12485 | 0
3737 | 0.12485 | 0
3738 | 5.5449 | 6.9902
3739 | 11.1255 | 13.415
3740 | 0.12485 | 0
3741 | 1.2964 | 0
3742 | 0.12485 | 0
3743 | 0.12485 | 0
3744 | 0.12485 | 0
3745 | 0.12485 | 0
3746 | 0.12485 | 0
3747 | 0.12485 | 0
3748 | 0.12485 | 0
3749 | 0.12485 | 0
3750 | 11.0834 | 13.5525
3751 | 1.2964 | 0
3752 | 1.6485 | 0
3753 | 0.12485 | 0
3754 | 0.12485 | 0
3755 | 0.12485 | 0
3756 | 0.86551 | 0
3757 | 0.12485 | 0
3758 | 0.12485 | 0
3759 | 0.12485 | 0
3760 | 0.12485 | 0
3761 | 0.12485 | 0
3762 | 5.6454 | 6.8616
3763 | 11.0935 | 13.2922
3764 | 0.12485 | 0
3765 | 1.2671 | 0
3766 | 0.12485 | 0
3767 | 0.12485 | 0
3768 | 0.12485 | 0
3769 | 0.12485 | 0
3770 | 0.12485 | 0
3771 | 0.12485 | 0
3772 | 0.12485 | 0
3773 | 0.12485 | 0
3774 | 11.0455 | 13.4171
3775 | 1.2665 | 0
3776 | 1.6097 | 0
3777 | 0.12485 | 0
3778 | 0.12485 | 0
3779 | 0.12485 | 0
3780 | 0.84667 | 0
3781 | 0.12485 | 0
3782 | 0.12485 | 6.3637
3783 | 0.12485 | 0
3784 | 0.12485 | 0
3785 | 0.12485 | 0
3786 | 5.7672 | 0
3787 | 10.7537 | 13.6949
3788 | 0.12485 | 0
3789 | 1.2411 | 0
3790 | 0.12485 | 0
3791 | 0.12485 | 0
3792 | 0.12485 | 0
3793 | 0.12485 | 0
3794 | 0.12485 | 0
3795 | 0.12485 | 0
3796 | 0.12485 | 0
3797 | 0.12485 | 0
3798 | 10.8211 | 13.537
3799 | 1.2482 | 0
3800 | 1.5859 | 0
3801 | 0.12485 | 0
3802 | 0.12485 | 0
3803 | 0.12485 | 0
3804 | 0.83511 | 6.5069
3805 | 0.12485 | 0
3806 | 0.12485 | 0
3807 | 0.12485 | 0
3808 | 0.12485 | 0
3809 | 0.12485 | 0
3810 | 5.6954 | 6.491
3811 | 11.1186 | 12.5498
3812 | 0.12485 | 0
3813 | 1.323 | 0
3814 | 0.12485 | 0
3815 | 0.12485 | 0
3816 | 0.12485 | 0
3817 | 0.12485 | 0
3818 | 0.12485 | 0
3819 | 0.12485 | 0
3820 | 0.12485 | 0
3821 | 0.12485 | 0
3822 | 10.9063 | 12.9599
3823 | 1.3138 | 0
3824 | 1.6712 | 0
3825 | 0.12485 | 0
3826 | 0.12485 | 0
3827 | 0.12485 | 0
3828 | 0.87644 | 0
3829 | 0.12485 | 0
3830 | 0.12485 | 0
3831 | 0.12485 | 0
3832 | 0.12485 | 0
3833 | 0.12485 | 0
3834 | 5.5086 | 6.9804
3835 | 11.0609 | 13.3354
3836 | 0.12485 | 0
3837 | 1.2891 | 0
3838 | 0.12485 | 0
3839 | 0.12485 | 0
3840 | 0.12485 | 0
3841 | 0.12485 | 0
3842 | 0.12485 | 0
3843 | 0.12485 | 0
3844 | 0.12485 | 0
3845 | 0.12485 | 0
3846 | 11.0167 | 13.4717
3847 | 1.289 | 0
3848 | 1.6388 | 0
3849 | 0.12485 | 0
3850 | 0.12485 | 0
3851 | 0.12485 | 0
3852 | 0.86073 | 0
3853 | 0.12485 | 0
3854 | 0.12485 | 0
3855 | 0.12485 | 0
3856 | 0.12485 | 0
3857 | 0.12485 | 0
3858 | 5.6109 | 6.8523
3859 | 11.0298 | 13.2104
3860 | 0.12485 | 0
3861 | 1.2601 | 0
3862 | 0.12485 | 0
3863 | 0.12485 | 0
3864 | 0.12485 | 0
3865 | 0.12485 | 0
3866 | 0.12485 | 0
3867 | 0.12485 | 0
3868 | 0.12485 | 0
3869 | 0.12485 | 0
3870 | 10.9794 | 13.3354
3871 | 1.2594 | 0
3872 | 1.6004 | 0
3873 | 0.12485 | 0
3874 | 0.12485 | 0
3875 | 0.12485 | 0
3876 | 0.84207 | 0
3877 | 0.12485 | 0
3878 | 0.12485 | 0
3879 | 0.12485 | 0
3880 | 0.12485 | 6.3682
3881 | 0.12485 | 0
3882 | 5.7368 | 0
3883 | 10.6988 | 13.6697
3884 | 0.12485 | 0
3885 | 1.2359 | 0
3886 | 0.12485 | 0
3887 | 0.12485 | 0
3888 | 0.12485 | 0
3889 | 0.12485 | 0
3890 | 0.12485 | 0
3891 | 0.12485 | 0
3892 | 0.12485 | 0
3893 | 0.12485 | 0
3894 | 10.7739 | 13.5326
3895 | 1.2439 | 0
3896 | 1.5803 | 0
3897 | 0.12485 | 0
3898 | 0.12485 | 0
3899 | 0.12485 | 0
3900 | 0.83231 | 6.405
3901 | 0.12485 | 0
3902 | 0.12485 | 0
3903 | 0.12485 | 0
3904 | 0.12485 | 0
3905 | 0.12485 | 0
3906 | 5.6659 | 6.4065
3907 | 11.0523 | 12.4722
3908 | 0.12485 | 0
3909 | 1.3156 | 0
3910 | 0.12485 | 0
3911 | 0.12485 | 0
3912 | 0.12485 | 0
3913 | 0.12485 | 0
3914 | 0.12485 | 0
3915 | 0.12485 | 0
3916 | 0.12485 | 0
3917 | 0.12485 | 0
3918 | 10.8395 | 12.8844
3919 | 1.3064 | 0
3920 | 1.6615 | 0
3921 | 0.12485 | 0
3922 | 0.12485 | 0
3923 | 0.12485 | 0
3924 | 0.87169 | 0
3925 | 0.12485 | 0
3926 | 0.12485 | 0
3927 | 0.12485 | 0
3928 | 0.12485 | 0
3929 | 0.12485 | 0
3930 | 5.4744 | 6.9705
3931 | 10.6008 | 13.1908
3932 | 0.12485 | 0
3933 | 1.2886 | 0
3934 | 0.12485 | 0
3935 | 0.12485 | 0
3936 | 0.12485 | 0
3937 | 0.12485 | 0
3938 | 0.12485 | 0
3939 | 0.12485 | 0
3940 | 0.12485 | 0
3941 | 0.12485 | 0
3942 | 10.6033 | 13.2323
3943 | 1.2918 | 0
3944 | 1.6424 | 0
3945 | 0.12485 | 0
3946 | 0.12485 | 0
3947 | 0.12485 | 0
3948 | 0.86241 | 0
3949 | 0.12485 | 0
3950 | 0.12485 | 0
3951 | 0.12485 | 0
3952 | 0.12485 | 0
3953 | 0.12485 | 0
3954 | 5.6177 | 6.7647
3955 | 11.0277 | 13.0311
3956 | 0.12485 | 0
3957 | 1.2571 | 0
3958 | 0.12485 | 0
3959 | 0.12485 | 0
3960 | 0.12485 | 0
3961 | 0.12485 | 0
3962 | 0.12485 | 0
3963 | 0.12485 | 0
3964 | 0.12485 | 0
3965 | 0.12485 | 0
3966 | 10.9464 | 13.199
3967 | 1.2544 | 0
3968 | 1.5939 | 0
3969 | 0.12485 | 0
3970 | 0.12485 | 0
3971 | 0.12485 | 0
3972 | 0.83885 | 0
3973 | 0.12485 | 0
3974 | 0.12485 | 0
3975 | 0.12485 | 0
3976 | 0.12485 | 0
3977 | 0.12485 | 0
3978 | 5.4626 | 6.9703
3979 | 10.7885 | 13.3829
3980 | 0.12485 | 0
3981 | 1.2412 | 0
3982 | 0.12485 | 0
3983 | 0.12485 | 0
3984 | 0.12485 | 0
3985 | 0.12485 | 0
3986 | 0.12485 | 0
3987 | 0.12485 | 0
3988 | 0.12485 | 0
3989 | 0.12485 | 0
3990 | 10.8142 | 13.3958
3991 | 1.2454 | 0
3992 | 1.5822 | 0
3993 | 0.12485 | 0
3994 | 0.12485 | 0
3995 | 0.12485 | 0
3996 | 0.83318 | 0
3997 | 0.12485 | 0
3998 | 0.12485 | 0
3999 | 0.12485 | 6.3672
4000 | 0.12485 | 0
4001 | 0.12485 | 0
4002 | 5.6729 | 0
4003 | 10.5878 | 13.6611
4004 | 0.12485 | 0
4005 | 1.2258 | 0
4006 | 0.12485 | 0
4007 | 0.12485 | 0
4008 | 0.12485 | 0
4009 | 0.12485 | 0
4010 | 0.12485 | 0
4011 | 0.12485 | 0
4012 | 0.12485 | 0
4013 | 0.12485 | 0
4014 | 10.6832 | 13.5233
4015 | 1.2356 | 0
4016 | 1.5695 | 0
4017 | 0.12485 | 0
4018 | 0.12485 | 0
4019 | 0.12485 | 0
4020 | 0.827 | 6.3621
4021 | 0.12485 | 0
4022 | 0.12485 | 0
4023 | 0.12485 | 0
4024 | 0.12485 | 0
4025 | 0.12485 | 0
4026 | 5.6249 | 0
4027 | 10.5077 | 13.6869
4028 | 0.12485 | 0
4029 | 1.2189 | 0
4030 | 0.12485 | 0
4031 | 0.12485 | 0
4032 | 0.12485 | 0
4033 | 0.12485 | 0
4034 | 0.12485 | 0
4035 | 0.12485 | 0
4036 | 0.12485 | 0
4037 | 0.12485 | 0
4038 | 10.6211 | 13.5161
4039 | 1.23 | 0
4040 | 1.5621 | 0
4041 | 0.12485 | 0
4042 | 0.12485 | 0
4043 | 0.12485 | 0
4044 | 0.82341 | 6.3836
4045 | 0.12485 | 0
4046 | 0.12485 | 0
4047 | 0.12485 | 0
4048 | 0.12485 | 0
4049 | 0.12485 | 0
4050 | 5.6007 | 6.3692
4051 | 10.9324 | 12.4021
4052 | 0.12485 | 0
4053 | 1.3035 | 0
4054 | 0.12485 | 0
4055 | 0.12485 | 0
4056 | 0.12485 | 0
4057 | 0.12485 | 0
4058 | 0.12485 | 0
4059 | 0.12485 | 0
4060 | 0.12485 | 0
4061 | 0.12485 | 0
4062 | 10.7312 | 12.7971
4063 | 1.2951 | 0
4064 | 1.6467 | 0
4065 | 0.12485 | 0
4066 | 0.12485 | 0
4067 | 0.12485 | 0
4068 | 0.86441 | 0
4069 | 0.12485 | 0
4070 | 0.12485 | 0
4071 | 0.12485 | 0
4072 | 0.12485 | 0
4073 | 0.12485 | 0
4074 | 5.4223 | 6.9575
4075 | 10.5084 | 13.0835
4076 | 0.12485 | 0
4077 | 1.2782 | 0
4078 | 0.12485 | 0
4079 | 0.12485 | 0
4080 | 0.12485 | 0
4081 | 0.12485 | 0
4082 | 0.12485 | 0
4083 | 0.12485 | 0
4084 | 0.12485 | 0
4085 | 0.12485 | 0
4086 | 10.5103 | 13.1224
4087 | 1.2814 | 0
4088 | 1.6289 | 0
4089 | 0.12485 | 0
4090 | 0.12485 | 0
4091 | 0.12485 | 0
4092 | 0.85574 | 0
4093 | 0.12485 | 0
4094 | 0.12485 | 0
4095 | 0.12485 | 0
4096 | 0.12485 | 0
4097 | 0.12485 | 0
4098 | 5.3618 | 6.9739
4099 | 10.8045 | 13.2621
4100 | 0.12485 | 0
4101 | 1.2648 | 0
4102 | 0.12485 | 0
4103 | 0.12485 | 0
4104 | 0.12485 | 0
4105 | 0.12485 | 0
4106 | 0.12485 | 0
4107 | 0.12485 | 0
4108 | 0.12485 | 0
4109 | 0.12485 | 0
4110 | 10.7987 | 13.3426
4111 | 1.2671 | 0
4112 | 1.6103 | 0
4113 | 0.12485 | 0
4114 | 0.12485 | 0
4115 | 0.12485 | 0
4116 | 0.84671 | 0
4117 | 0.12485 | 0
4118 | 0.12485 | 0
4119 | 0.12485 | 0
4120 | 0.12485 | 0
4121 | 0.12485 | 0
4122 | 5.51 | 6.833
4123 | 10.8468 | 13.0307
4124 | 0.12485 | 0
4125 | 1.2409 | 0
4126 | 0.12485 | 0
4127 | 0.12485 | 0
4128 | 0.12485 | 0
4129 | 0.12485 | 0
4130 | 0.12485 | 0
4131 | 0.12485 | 0
4132 | 0.12485 | 0
4133 | 0.12485 | 0
4134 | 10.7999 | 13.1438
4135 | 1.2404 | 0
4136 | 1.5757 | 0
4137 | 0.12485 | 0
4138 | 0.12485 | 0
4139 | 0.12485 | 0
4140 | 0.8299 | 0
4141 | 0.12485 | 0
4142 | 0.12485 | 0
4143 | 0.12485 | 0
4144 | 0.12485 | 0
4145 | 0.12485 | 0
4146 | 5.3983 | 6.9581
4147 | 10.6722 | 13.2775
4148 | 0.12485 | 0
4149 | 1.2292 | 0
4150 | 0.12485 | 0
4151 | 0.12485 | 0
4152 | 0.12485 | 0
4153 | 0.12485 | 0
4154 | 0.12485 | 0
4155 | 0.12485 | 0
4156 | 0.12485 | 0
4157 | 0.12485 | 0
4158 | 10.7019 | 13.2809
4159 | 1.2336 | 0
4160 | 1.5668 | 0
4161 | 0.12485 | 0
4162 | 0.12485 | 0
4163 | 0.12485 | 0
4164 | 0.82561 | 0
4165 | 0.12485 | 0
4166 | 0.12485 | 0
4167 | 0.12485 | 0
4168 | 0.12485 | 0
4169 | 0.12485 | 6.3668
4170 | 5.6216 | 0
4171 | 10.4956 | 13.6245
4172 | 0.12485 | 0
4173 | 1.2172 | 0
4174 | 0.12485 | 0
4175 | 0.12485 | 0
4176 | 0.12485 | 0
4177 | 0.12485 | 0
4178 | 0.12485 | 0
4179 | 0.12485 | 0
4180 | 0.12485 | 0
4181 | 0.12485 | 0
4182 | 10.6016 | 13.4162
4183 | 1.2267 | 0
4184 | 1.5578 | 0
4185 | 0.12485 | 0
4186 | 0.12485 | 0
4187 | 0.12485 | 0
4188 | 0.82121 | 0
4189 | 0.12485 | 0
4190 | 0.12485 | 0
4191 | 0.12485 | 0
4192 | 0.12485 | 6.3689
4193 | 0.12485 | 0
4194 | 5.5883 | 0
4195 | 10.4398 | 13.6396
4196 | 0.12485 | 0
4197 | 1.2123 | 0
4198 | 0.12485 | 0
4199 | 0.12485 | 0
4200 | 0.12485 | 0
4201 | 0.12485 | 0
4202 | 0.12485 | 0
4203 | 0.12485 | 0
4204 | 0.12485 | 0
4205 | 0.12485 | 0
4206 | 10.5594 | 13.4465
4207 | 1.2234 | 0
4208 | 1.5535 | 0
4209 | 0.12485 | 0
4210 | 0.12485 | 0
4211 | 0.12485 | 0
4212 | 0.8191 | 0
4213 | 0.12485 | 0
4214 | 0.12485 | 0
4215 | 0.12485 | 6.3658
4216 | 0.12485 | 0
4217 | 0.12485 | 0
4218 | 5.5724 | 0
4219 | 10.4126 | 13.6419
4220 | 0.12485 | 0
4221 | 1.2099 | 0
4222 | 0.12485 | 0
4223 | 0.12485 | 0
4224 | 0.12485 | 0
4225 | 0.12485 | 0
4226 | 0.12485 | 0
4227 | 0.12485 | 0
4228 | 0.12485 | 0
4229 | 0.12485 | 0
4230 | 10.5377 | 13.4432
4231 | 1.2214 | 0
4232 | 1.5509 | 0
4233 | 0.12485 | 0
4234 | 0.12485 | 0
4235 | 0.12485 | 0
4236 | 0.81783 | 0
4237 | 0.12485 | 0
4238 | 0.12485 | 0
4239 | 0.12485 | 6.3691
4240 | 0.12485 | 0
4241 | 0.12485 | 0
4242 | 5.5639 | 0
4243 | 10.3976 | 13.6381
4244 | 0.12485 | 0
4245 | 1.2085 | 0
4246 | 0.12485 | 0
4247 | 0.12485 | 0
4248 | 0.12485 | 0
4249 | 0.12485 | 0
4250 | 0.12485 | 0
4251 | 0.12485 | 0
4252 | 0.12485 | 0
4253 | 0.12485 | 0
4254 | 10.5247 | 13.4264
4255 | 1.22 | 0
4256 | 1.549 | 0
4257 | 0.12485 | 0
4258 | 0.12485 | 0
4259 | 0.12485 | 0
4260 | 0.81692 | 0
4261 | 0.12485 | 0
4262 | 0.12485 | 0
4263 | 0.12485 | 0
4264 | 0.12485 | 6.3703
4265 | 0.12485 | 0
4266 | 5.5579 | 0
4267 | 10.3867 | 13.6327
4268 | 0.12485 | 0
4269 | 1.2075 | 0
4270 | 0.12485 | 0
4271 | 0.12485 | 0
4272 | 0.12485 | 0
4273 | 0.12485 | 0
4274 | 0.12485 | 0
4275 | 0.12485 | 0
4276 | 0.12485 | 0
4277 | 0.12485 | 0
4278 | 10.5147 | 13.4052
4279 | 1.2187 | 0
4280 | 1.5474 | 0
4281 | 0.12485 | 0
4282 | 0.12485 | 0
4283 | 0.12485 | 0
4284 | 0.81613 | 0
4285 | 0.12485 | 0
4286 | 0.12485 | 0
4287 | 0.12485 | 0
4288 | 0.12485 | 6.3684
4289 | 0.12485 | 0
4290 | 5.5526 | 0
4291 | 10.3769 | 13.6272
4292 | 0.12485 | 0
4293 | 1.2065 | 0
4294 | 0.12485 | 0
4295 | 0.12485 | 0
4296 | 0.12485 | 0
4297 | 0.12485 | 0
4298 | 0.12485 | 0
4299 | 0.12485 | 0
4300 | 0.12485 | 0
4301 | 0.12485 | 0
4302 | 10.5056 | 13.383
4303 | 1.2176 | 0
4304 | 1.5459 | 0
4305 | 0.12485 | 0
4306 | 0.12485 | 0
4307 | 0.12485 | 0
4308 | 0.81538 | 0
4309 | 0.12485 | 0
4310 | 0.12485 | 0
4311 | 0.12485 | 0
4312 | 0.12485 | 6.3661
4313 | 0.12485 | 0
4314 | 5.5474 | 0
4315 | 10.3675 | 13.6218
4316 | 0.12485 | 0
4317 | 1.2056 | 0
4318 | 0.12485 | 0
4319 | 0.12485 | 0
4320 | 0.12485 | 0
4321 | 0.12485 | 0
4322 | 0.12485 | 0
4323 | 0.12485 | 0
4324 | 0.12485 | 0
4325 | 0.12485 | 0
4326 | 10.4968 | 13.3608
4327 | 1.2165 | 0
4328 | 1.5444 | 0
4329 | 0.12485 | 0
4330 | 0.12485 | 0
4331 | 0.12485 | 0
4332 | 0.81465 | 0
4333 | 0.12485 | 0
4334 | 0.12485 | 0
4335 | 0.12485 | 0
4336 | 0.12485 | 0
4337 | 0.12485 | 6.3639
4338 | 5.5424 | 0
4339 | 10.3583 | 13.6164
4340 | 0.12485 | 0
4341 | 1.2047 | 0
4342 | 0.12485 | 0
4343 | 0.12485 | 0
4344 | 0.12485 | 0
4345 | 0.12485 | 0
4346 | 0.12485 | 0
4347 | 0.12485 | 0
4348 | 0.12485 | 0
4349 | 0.12485 | 0
4350 | 10.4882 | 13.3388
4351 | 1.2153 | 0
4352 | 1.543 | 0
4353 | 0.12485 | 0
4354 | 0.12485 | 0
4355 | 0.12485 | 0
4356 | 0.81393 | 0
4357 | 0.12485 | 0
4358 | 0.12485 | 0
4359 | 0.12485 | 0
4360 | 0.12485 | 0
4361 | 0.12485 | 6.3693
4362 | 5.5385 | 0
4363 | 10.3508 | 13.6096
4364 | 0.12485 | 0
4365 | 1.204 | 0
4366 | 0.12485 | 0
4367 | 0.12485 | 0
4368 | 0.12485 | 0
4369 | 0.12485 | 0
4370 | 0.12485 | 0
4371 | 0.12485 | 0
4372 | 0.12485 | 0
4373 | 0.12485 | 0
4374 | 10.4807 | 13.3155
4375 | 1.2143 | 0
4376 | 1.5417 | 0
4377 | 0.12485 | 0
4378 | 0.12485 | 0
4379 | 0.12485 | 0
4380 | 0.81327 | 0
4381 | 0.12485 | 0
4382 | 0.12485 | 0
4383 | 0.12485 | 0
4384 | 0.12485 | 0
4385 | 0.12485 | 6.3664
4386 | 5.5339 | 0
4387 | 10.3424 | 13.6043
4388 | 0.12485 | 0
4389 | 1.2032 | 0
4390 | 0.12485 | 0
4391 | 0.12485 | 0
4392 | 0.12485 | 0
4393 | 0.12485 | 0
4394 | 0.12485 | 0
4395 | 0.12485 | 0
4396 | 0.12485 | 0
4397 | 0.12485 | 0
4398 | 10.4727 | 13.2938
4399 | 1.2133 | 0
4400 | 1.5403 | 0
4401 | 0.12485 | 0
4402 | 0.12485 | 0
4403 | 0.12485 | 0
4404 | 0.81259 | 0
4405 | 0.12485 | 0
4406 | 0.12485 | 0
4407 | 0.12485 | 0
4408 | 0.12485 | 0
4409 | 0.12485 | 0
4410 | 5.2754 | 6.9535
4411 | 10.4563 | 13.2181
4412 | 0.12485 | 0
4413 | 1.2089 | 0
4414 | 0.12485 | 0
4415 | 0.12485 | 0
4416 | 0.12485 | 0
4417 | 0.12485 | 0
4418 | 0.12485 | 0
4419 | 0.12485 | 0
4420 | 0.12485 | 0
4421 | 0.12485 | 0
4422 | 10.5181 | 13.1734
4423 | 1.2156 | 0
4424 | 1.5433 | 0
4425 | 0.12485 | 0
4426 | 0.12485 | 0
4427 | 0.12485 | 0
4428 | 0.81402 | 0
4429 | 0.12485 | 0
4430 | 0.12485 | 0
4431 | 0.12485 | 0
4432 | 0.12485 | 0
4433 | 0.12485 | 0
4434 | 5.2849 | 6.9459
4435 | 10.4702 | 13.1619
4436 | 0.12485 | 0
4437 | 1.2093 | 0
4438 | 0.12485 | 0
4439 | 0.12485 | 0
4440 | 0.12485 | 0
4441 | 0.12485 | 0
4442 | 0.12485 | 0
4443 | 0.12485 | 0
4444 | 0.12485 | 0
4445 | 0.12485 | 0
4446 | 10.5197 | 13.134
4447 | 1.2151 | 0
4448 | 1.5427 | 0
4449 | 0.12485 | 0
4450 | 0.12485 | 0
4451 | 0.12485 | 0
4452 | 0.81372 | 0
4453 | 0.12485 | 0
4454 | 0.12485 | 0
4455 | 0.12485 | 0
4456 | 0.12485 | 0
4457 | 0.12485 | 0
4458 | 5.2826 | 6.9427
4459 | 10.465 | 13.1373
4460 | 0.12485 | 0
4461 | 1.2084 | 0
4462 | 0.12485 | 0
4463 | 0.12485 | 0
4464 | 0.12485 | 0
4465 | 0.12485 | 0
4466 | 0.12485 | 0
4467 | 0.12485 | 0
4468 | 0.12485 | 0
4469 | 0.12485 | 0
4470 | 10.5113 | 13.1135
4471 | 1.2141 | 0
4472 | 1.5413 | 0
4473 | 0.12485 | 0
4474 | 0.12485 | 0
4475 | 0.12485 | 0
4476 | 0.81304 | 0
4477 | 0.12485 | 0
4478 | 0.12485 | 0
4479 | 0.12485 | 0
4480 | 0.12485 | 0
4481 | 0.12485 | 0
4482 | 5.2776 | 6.9406
4483 | 10.4556 | 13.1203
4484 | 0.12485 | 0
4485 | 1.2073 | 0
4486 | 0.12485 | 0
4487 | 0.12485 | 0
4488 | 0.12485 | 0
4489 | 0.12485 | 0
4490 | 0.12485 | 0
4491 | 0.12485 | 0
4492 | 0.12485 | 0
4493 | 0.12485 | 0
4494 | 10.5009 | 13.0977
4495 | 1.2129 | 0
4496 | 1.5398 | 0
4497 | 0.12485 | 0
4498 | 0.12485 | 0
4499 | 0.12485 | 0
4500 | 0.81229 | 0
4501 | 0.12485 | 0
4502 | 0.12485 | 0
4503 | 0.12485 | 0
4504 | 0.12485 | 0
4505 | 0.12485 | 0
4506 | 5.2721 | 6.9388
4507 | 10.4454 | 13.1051
4508 | 0.12485 | 0
4509 | 1.2062 | 0
4510 | 0.12485 | 0
4511 | 0.12485 | 0
4512 | 0.12485 | 0
4513 | 0.12485 | 0
4514 | 0.12485 | 0
4515 | 0.12485 | 0
4516 | 0.12485 | 0
4517 | 0.12485 | 0
4518 | 10.4901 | 13.0831
4519 | 1.2117 | 0
4520 | 1.5382 | 0
4521 | 0.12485 | 0
4522 | 0.12485 | 0
4523 | 0.12485 | 0
4524 | 0.81153 | 0
4525 | 0.12485 | 0
4526 | 0.12485 | 0
4527 | 0.12485 | 0
4528 | 0.12485 | 0
4529 | 0.12485 | 0
4530 | 5.2666 | 6.937
4531 | 10.4352 | 13.0907
4532 | 0.12485 | 0
4533 | 1.205 | 0
4534 | 0.12485 | 0
4535 | 0.12485 | 0
4536 | 0.12485 | 0
4537 | 0.12485 | 0
4538 | 0.12485 | 0
4539 | 0.12485 | 0
4540 | 0.12485 | 0
4541 | 0.12485 | 0
4542 | 10.4796 | 13.0691
4543 | 1.2106 | 0
4544 | 1.5367 | 0
4545 | 0.12485 | 0
4546 | 0.12485 | 0
4547 | 0.12485 | 0
4548 | 0.81079 | 0
4549 | 0.12485 | 0
4550 | 0.12485 | 0
4551 | 0.12485 | 0
4552 | 0.12485 | 0
4553 | 0.12485 | 0
4554 | 5.2612 | 6.9353
4555 | 10.4252 | 13.0767
4556 | 0.12485 | 0
4557 | 1.2039 | 0
4558 | 0.12485 | 0
4559 | 0.12485 | 0
4560 | 0.12485 | 0
4561 | 0.12485 | 0
4562 | 0.12485 | 0
4563 | 0.12485 | 0
4564 | 0.12485 | 0
4565 | 0.12485 | 0
4566 | 10.4692 | 13.0554
4567 | 1.2094 | 0
4568 | 1.5352 | 0
4569 | 0.12485 | 0
4570 | 0.12485 | 0
4571 | 0.12485 | 0
4572 | 0.81006 | 0
4573 | 0.12485 | 0
4574 | 0.12485 | 0
4575 | 0.12485 | 0
4576 | 0.12485 | 0
4577 | 0.12485 | 0
4578 | 5.2559 | 6.9336
4579 | 10.4154 | 13.063
4580 | 0.12485 | 0
4581 | 1.2028 | 0
4582 | 0.12485 | 0
4583 | 0.12485 | 0
4584 | 0.12485 | 0
4585 | 0.12485 | 0
4586 | 0.12485 | 0
4587 | 0.12485 | 0
4588 | 0.12485 | 0
4589 | 0.12485 | 0
4590 | 10.2619 | 13.5979
4591 | 1.2227 | 0
4592 | 1.5525 | 0
4593 | 0.12485 | 0
4594 | 0.12485 | 0
4595 | 0.12485 | 0
4596 | 0.81842 | 0
4597 | 0.12485 | 0
4598 | 0.12485 | 0
4599 | 0.12485 | 0
4600 | 0.12485 | 0
4601 | 0.12485 | 0
4602 | 5.3091 | 6.8251
4603 | 10.2972 | 13.4619
4604 | 0.12485 | 0
4605 | 1.2217 | 0
4606 | 0.12485 | 0
4607 | 0.12485 | 0
4608 | 0.12485 | 0
4609 | 0.12485 | 0
4610 | 0.12485 | 0
4611 | 0.12485 | 0
4612 | 0.12485 | 0
4613 | 0.12485 | 0
4614 | 10.4164 | 13.2286
4615 | 1.2307 | 0
4616 | 1.5629 | 0
4617 | 0.12485 | 0
4618 | 0.12485 | 0
4619 | 0.12485 | 0
4620 | 0.82344 | 0
4621 | 0.12485 | 0
4622 | 0.12485 | 0
4623 | 0.12485 | 0
4624 | 0.12485 | 0
4625 | 0.12485 | 0
4626 | 5.3401 | 6.7433
4627 | 10.3439 | 13.3629
4628 | 0.12485 | 0
4629 | 1.224 | 0
4630 | 0.12485 | 0
4631 | 0.12485 | 0
4632 | 0.12485 | 0
4633 | 0.12485 | 0
4634 | 0.12485 | 0
4635 | 0.12485 | 0
4636 | 0.12485 | 0
4637 | 0.12485 | 0
4638 | 10.0306 | 13.0952
4639 | 1.2378 | 0
4640 | 1.5721 | 0
4641 | 0.12485 | 0
4642 | 0.12485 | 0
4643 | 0.12485 | 0
4644 | 0.82791 | 0
4645 | 0.12485 | 0
4646 | 0.12485 | 0
4647 | 0.12485 | 0
4648 | 0.12485 | 0
4649 | 0.12485 | 0
4650 | 5.1637 | 6.9472
4651 | 10.0581 | 12.9598
4652 | 0.12485 | 0
4653 | 1.2356 | 0
4654 | 0.12485 | 0
4655 | 0.12485 | 0
4656 | 0.12485 | 0
4657 | 0.12485 | 0
4658 | 0.12485 | 0
4659 | 0.12485 | 0
4660 | 0.12485 | 0
4661 | 0.12485 | 0
4662 | 10.1318 | 12.9016
4663 | 1.2433 | 0
4664 | 1.5792 | 0
4665 | 0.12485 | 0
4666 | 0.12485 | 0
4667 | 0.12485 | 0
4668 | 0.83133 | 0
4669 | 0.12485 | 0
4670 | 0.12485 | 0
4671 | 0.12485 | 0
4672 | 0.12485 | 0
4673 | 0.12485 | 0
4674 | 5.1873 | 6.9356
4675 | 10.0973 | 12.8765
4676 | 0.12485 | 0
4677 | 1.2375 | 0
4678 | 0.12485 | 0
4679 | 0.12485 | 0
4680 | 0.12485 | 0
4681 | 0.12485 | 0
4682 | 0.12485 | 0
4683 | 0.12485 | 0
4684 | 0.12485 | 0
4685 | 0.12485 | 0
4686 | 10.1483 | 12.8472
4687 | 1.2437 | 0
4688 | 1.5798 | 0
4689 | 0.12485 | 0
4690 | 0.12485 | 0
4691 | 0.12485 | 0
4692 | 0.83161 | 0
4693 | 0.12485 | 0
4694 | 0.12485 | 0
4695 | 0.12485 | 0
4696 | 0.12485 | 0
4697 | 0.12485 | 0
4698 | 5.189 | 6.9318
4699 | 10.0998 | 12.8483
4700 | 0.12485 | 0
4701 | 1.2371 | 0
4702 | 0.12485 | 0
4703 | 0.12485 | 0
4704 | 0.12485 | 0
4705 | 0.12485 | 0
4706 | 0.12485 | 0
4707 | 0.12485 | 0
4708 | 0.12485 | 0
4709 | 0.12485 | 0
4710 | 10.1455 | 12.8258
4711 | 1.2431 | 0
4712 | 1.5789 | 0
4713 | 0.12485 | 0
4714 | 0.12485 | 0
4715 | 0.12485 | 0
4716 | 0.83119 | 0
4717 | 0.12485 | 0
4718 | 0.12485 | 0
4719 | 0.12485 | 0
4720 | 0.12485 | 0
4721 | 0.12485 | 0
4722 | 5.1859 | 6.9299
4723 | 10.0941 | 12.8329
4724 | 0.12485 | 0
4725 | 1.2363 | 0
4726 | 0.12485 | 0
4727 | 0.12485 | 0
4728 | 0.12485 | 0
4729 | 0.12485 | 0
4730 | 0.12485 | 0
4731 | 0.12485 | 0
4732 | 0.12485 | 0
4733 | 0.12485 | 0
4734 | 10.1384 | 12.8123
4735 | 1.2422 | 0
4736 | 1.5778 | 0
4737 | 0.12485 | 0
4738 | 0.12485 | 0
4739 | 0.12485 | 0
4740 | 0.83061 | 0
4741 | 0.12485 | 0
4742 | 0.12485 | 0
4743 | 0.12485 | 0
4744 | 0.12485 | 0
4745 | 0.12485 | 0
4746 | 5.1818 | 6.9284
4747 | 10.0867 | 12.8207
4748 | 0.12485 | 0
4749 | 1.2354 | 0
4750 | 0.12485 | 0
4751 | 0.12485 | 0
4752 | 0.12485 | 0
4753 | 0.12485 | 0
4754 | 0.12485 | 0
4755 | 0.12485 | 0
4756 | 0.12485 | 0
4757 | 0.12485 | 0
4758 | 10.1306 | 12.8007
4759 | 1.2413 | 0
4760 | 1.5766 | 0
4761 | 0.12485 | 0
4762 | 0.12485 | 0
4763 | 0.12485 | 0
4764 | 0.83003 | 0
4765 | 0.12485 | 0
4766 | 0.12485 | 0
4767 | 0.12485 | 0
4768 | 0.12485 | 0
4769 | 0.12485 | 0
4770 | 5.1776 | 6.927
4771 | 10.0791 | 12.8095
4772 | 0.12485 | 0
4773 | 1.2345 | 0
4774 | 0.12485 | 0
4775 | 0.12485 | 0
4776 | 0.12485 | 0
4777 | 0.12485 | 0
4778 | 0.12485 | 0
4779 | 0.12485 | 0
4780 | 0.12485 | 0
4781 | 0.12485 | 0
4782 | 10.1228 | 12.79
4783 | 1.2404 | 0
4784 | 1.5754 | 0
4785 | 0.12485 | 0
4786 | 0.12485 | 0
4787 | 0.12485 | 0
4788 | 0.82945 | 0
4789 | 0.12485 | 0
4790 | 0.12485 | 0
4791 | 0.12485 | 0
4792 | 0.12485 | 0
4793 | 0.12485 | 0
4794 | 5.1734 | 6.9257
4795 | 10.0717 | 12.7988
4796 | 0.12485 | 0
4797 | 1.2337 | 0
4798 | 0.12485 | 0
4799 | 0.12485 | 0
4800 | 0.12485 | 0
4801 | 0.12485 | 0
4802 | 0.12485 | 0
4803 | 0.12485 | 0
4804 | 0.12485 | 0
4805 | 0.12485 | 0
4806 | 10.1152 | 12.7796
4807 | 1.2395 | 0
4808 | 1.5743 | 0
4809 | 0.12485 | 0
4810 | 0.12485 | 0
4811 | 0.12485 | 0
4812 | 0.82888 | 0
4813 | 0.12485 | 0
4814 | 0.12485 | 0
4815 | 0.12485 | 0
4816 | 0.12485 | 0
4817 | 0.12485 | 0
4818 | 5.1694 | 6.9244
4819 | 10.0645 | 12.7885
4820 | 0.12485 | 0
4821 | 1.2328 | 0
4822 | 0.12485 | 0
4823 | 0.12485 | 0
4824 | 0.12485 | 0
4825 | 0.12485 | 0
4826 | 0.12485 | 0
4827 | 0.12485 | 0
4828 | 0.12485 | 0
4829 | 0.12485 | 0
4830 | 10.1079 | 12.7697
4831 | 1.2387 | 0
4832 | 1.5732 | 0
4833 | 0.12485 | 0
4834 | 0.12485 | 0
4835 | 0.12485 | 0
4836 | 0.82834 | 0
4837 | 0.12485 | 0
4838 | 0.12485 | 0
4839 | 0.12485 | 0
4840 | 0.12485 | 0
4841 | 0.12485 | 0
4842 | 5.1655 | 6.9232
4843 | 10.0576 | 12.7786
4844 | 0.12485 | 0
4845 | 1.232 | 0
4846 | 0.12485 | 0
4847 | 0.12485 | 0
4848 | 0.12485 | 0
4849 | 0.12485 | 0
4850 | 0.12485 | 0
4851 | 0.12485 | 0
4852 | 0.12485 | 0
4853 | 0.12485 | 0
4854 | 10.1008 | 12.7601
4855 | 1.2378 | 0
4856 | 1.5721 | 0
4857 | 0.12485 | 0
4858 | 0.12485 | 0
4859 | 0.12485 | 0
4860 | 0.82782 | 0
4861 | 0.12485 | 0
4862 | 0.12485 | 0
4863 | 0.12485 | 0
4864 | 0.12485 | 0
4865 | 0.12485 | 0
4866 | 5.1617 | 6.922
4867 | 10.0509 | 12.769
4868 | 0.12485 | 0
4869 | 1.2312 | 0
4870 | 0.12485 | 0
4871 | 0.12485 | 0
4872 | 0.12485 | 0
4873 | 0.12485 | 0
4874 | 0.12485 | 0
4875 | 0.12485 | 0
4876 | 0.12485 | 0
4877 | 0.12485 | 0
4878 | 10.0941 | 12.7508
4879 | 1.2371 | 0
4880 | 1.5711 | 0
4881 | 0.12485 | 0
4882 | 0.12485 | 0
4883 | 0.12485 | 0
4884 | 0.82732 | 0
4885 | 0.12485 | 0
4886 | 0.12485 | 0
4887 | 0.12485 | 0
4888 | 0.12485 | 0
4889 | 0.12485 | 0
4890 | 5.1581 | 6.9208
4891 | 10.0445 | 12.7598
4892 | 0.12485 | 0
4893 | 1.2305 | 0
4894 | 0.12485 | 0
4895 | 0.12485 | 0
4896 | 0.12485 | 0
4897 | 0.12485 | 0
4898 | 0.12485 | 0
4899 | 0.12485 | 0
4900 | 0.12485 | 0
4901 | 0.12485 | 0
4902 | 10.0876 | 12.7419
4903 | 1.2363 | 0
4904 | 1.5701 | 0
4905 | 0.12485 | 0
4906 | 0.12485 | 0
4907 | 0.12485 | 0
4908 | 0.82684 | 0
4909 | 0.12485 | 0
4910 | 0.12485 | 0
4911 | 0.12485 | 0
4912 | 0.12485 | 0
4913 | 0.12485 | 0
4914 | 5.1547 | 6.9198
4915 | 10.0383 | 12.751
4916 | 0.12485 | 0
4917 | 1.2298 | 0
4918 | 0.12485 | 0
4919 | 0.12485 | 0
4920 | 0.12485 | 0
4921 | 0.12485 | 0
4922 | 0.12485 | 0
4923 | 0.12485 | 0
4924 | 0.12485 | 0
4925 | 0.12485 | 0
4926 | 10.0814 | 12.7334
4927 | 1.2356 | 0
4928 | 1.5692 | 0
4929 | 0.12485 | 0
4930 | 0.12485 | 0
4931 | 0.12485 | 0
4932 | 0.82638 | 0
4933 | 0.12485 | 0
4934 | 0.12485 | 0
4935 | 0.12485 | 0
4936 | 0.12485 | 0
4937 | 0.12485 | 0
4938 | 5.1514 | 6.9187
4939 | 10.0324 | 12.7425
4940 | 0.12485 | 0
4941 | 1.2291 | 0
4942 | 0.12485 | 0
4943 | 0.12485 | 0
4944 | 0.12485 | 0
4945 | 0.12485 | 0
4946 | 0.12485 | 0
4947 | 0.12485 | 0
4948 | 0.12485 | 0
4949 | 0.12485 | 0
4950 | 10.0754 | 12.7252
4951 | 1.2349 | 0
4952 | 1.5683 | 0
4953 | 0.12485 | 0
4954 | 0.12485 | 0
4955 | 0.12485 | 0
4956 | 0.82594 | 0
4957 | 0.12485 | 0
4958 | 0.12485 | 0
4959 | 0.12485 | 0
4960 | 0.12485 | 0
4961 | 0.12485 | 0
4962 | 5.1482 | 6.9177
4963 | 10.0267 | 12.7344
4964 | 0.12485 | 0
4965 | 1.2284 | 0
4966 | 0.12485 | 0
4967 | 0.12485 | 0
4968 | 0.12485 | 0
4969 | 0.12485 | 0
4970 | 0.12485 | 0
4971 | 0.12485 | 0
4972 | 0.12485 | 0
4973 | 0.12485 | 0
4974 | 10.0698 | 12.7174
4975 | 1.2343 | 0
4976 | 1.5674 | 0
4977 | 0.12485 | 0
4978 | 0.12485 | 0
4979 | 0.12485 | 0
4980 | 0.82552 | 0
4981 | 0.12485 | 0
4982 | 0.12485 | 0
4983 | 0.12485 | 0
4984 | 0.12485 | 0
4985 | 0.12485 | 0
4986 | 5.1452 | 6.9168
4987 | 10.0214 | 12.7267
4988 | 0.12485 | 0
4989 | 1.2278 | 0
4990 | 0.12485 | 0
4991 | 0.12485 | 0
4992 | 0.12485 | 0
4993 | 0.12485 | 0
4994 | 0.12485 | 0
4995 | 0.12485 | 0
4996 | 0.12485 | 0
4997 | 0.12485 | 0
4998 | 10.0644 | 12.71
4999 | 1.2336 | 0
5000 | 1.5666 | 0
5001 | 0.12485 | 0
5002 | 0.12485 | 0
5003 | 0.12485 | 0
5004 | 0.82512 | 0
5005 | 0.12485 | 0
5006 | 0.12485 | 0
5007 | 0.12485 | 0
5008 | 0.12485 | 0
5009 | 0.12485 | 0
5010 | 5.1423 | 6.9158
5011 | 10.0163 | 12.7193
5012 | 0.12485 | 0
5013 | 1.2272 | 0
5014 | 0.12485 | 0
5015 | 0.12485 | 0
5016 | 0.12485 | 0
5017 | 0.12485 | 0
5018 | 0.12485 | 0
5019 | 0.12485 | 0
5020 | 0.12485 | 0
5021 | 0.12485 | 0
5022 | 10.0594 | 12.7029
5023 | 1.2331 | 0
5024 | 1.5659 | 0
5025 | 0.12485 | 0
5026 | 0.12485 | 0
5027 | 0.12485 | 0
5028 | 0.82475 | 0
5029 | 0.12485 | 0
5030 | 0.12485 | 0
5031 | 0.12485 | 0
5032 | 0.12485 | 0
5033 | 0.12485 | 0
5034 | 5.1396 | 6.915
5035 | 10.0114 | 12.7123
5036 | 0.12485 | 0
5037 | 1.2266 | 0
5038 | 0.12485 | 0
5039 | 0.12485 | 0
5040 | 0.12485 | 0
5041 | 0.12485 | 0
5042 | 0.12485 | 0
5043 | 0.12485 | 0
5044 | 0.12485 | 0
5045 | 0.12485 | 0
5046 | 10.0546 | 12.6963
5047 | 1.2325 | 0
5048 | 1.5651 | 0
5049 | 0.12485 | 0
5050 | 0.12485 | 0
5051 | 0.12485 | 0
5052 | 0.82439 | 0
5053 | 0.12485 | 0
5054 | 0.12485 | 0
5055 | 0.12485 | 0
5056 | 0.12485 | 0
5057 | 0.12485 | 0
5058 | 5.1371 | 6.9142
5059 | 10.0069 | 12.7057
5060 | 0.12485 | 0
5061 | 1.2261 | 0
5062 | 0.12485 | 0
5063 | 0.12485 | 0
5064 | 0.12485 | 0
5065 | 0.12485 | 0
5066 | 0.12485 | 0
5067 | 0.12485 | 0
5068 | 0.12485 | 0
5069 | 0.12485 | 0
5070 | 10.0501 | 12.6899
5071 | 1.232 | 0
5072 | 1.5645 | 0
5073 | 0.12485 | 0
5074 | 0.12485 | 0
5075 | 0.12485 | 0
5076 | 0.82406 | 0
5077 | 0.12485 | 0
5078 | 0.12485 | 0
5079 | 0.12485 | 0
5080 | 0.12485 | 0
5081 | 0.12485 | 0
5082 | 5.1347 | 6.9134
5083 | 10.0026 | 12.6995
5084 | 0.12485 | 0
5085 | 1.2256 | 0
5086 | 0.12485 | 0
5087 | 0.12485 | 0
5088 | 0.12485 | 0
5089 | 0.12485 | 0
5090 | 0.12485 | 0
5091 | 0.12485 | 0
5092 | 0.12485 | 0
5093 | 0.12485 | 0
5094 | 10.0459 | 12.684
5095 | 1.2315 | 0
5096 | 1.5638 | 0
5097 | 0.12485 | 0
5098 | 0.12485 | 0
5099 | 0.12485 | 0
5100 | 0.82374 | 0
5101 | 0.12485 | 0
5102 | 0.12485 | 0
5103 | 0.12485 | 0
5104 | 0.12485 | 0
5105 | 0.12485 | 0
5106 | 5.1324 | 6.9127
5107 | 9.9986 | 12.6937
5108 | 0.12485 | 0
5109 | 1.2251 | 0
5110 | 0.12485 | 0
5111 | 0.12485 | 0
5112 | 0.12485 | 0
5113 | 0.12485 | 0
5114 | 0.12485 | 0
5115 | 0.12485 | 0
5116 | 0.12485 | 0
5117 | 0.12485 | 0
5118 | 10.042 | 12.6784
5119 | 1.231 | 0
5120 | 1.5632 | 0
5121 | 0.12485 | 0
5122 | 0.12485 | 0
5123 | 0.12485 | 0
5124 | 0.82345 | 0
5125 | 0.12485 | 0
5126 | 0.12485 | 0
5127 | 0.12485 | 0
5128 | 0.12485 | 0
5129 | 0.12485 | 0
5130 | 5.1303 | 6.912
5131 | 9.9948 | 12.6882
5132 | 0.12485 | 0
5133 | 1.2247 | 0
5134 | 0.12485 | 0
5135 | 0.12485 | 0
5136 | 0.12485 | 0
5137 | 0.12485 | 0
5138 | 0.12485 | 0
5139 | 0.12485 | 0
5140 | 0.12485 | 0
5141 | 0.12485 | 0
5142 | 10.0384 | 12.6733
5143 | 1.2306 | 0
5144 | 1.5627 | 0
5145 | 0.12485 | 0
5146 | 0.12485 | 0
5147 | 0.12485 | 0
5148 | 0.82318 | 0
5149 | 0.12485 | 0
5150 | 0.12485 | 0
5151 | 0.12485 | 0
5152 | 0.12485 | 0
5153 | 0.12485 | 0
5154 | 5.1284 | 6.9114
5155 | 9.9914 | 12.6831
5156 | 0.12485 | 0
5157 | 1.2243 | 0
5158 | 0.12485 | 0
5159 | 0.12485 | 0
5160 | 0.12485 | 0
5161 | 0.12485 | 0
5162 | 0.12485 | 0
5163 | 0.12485 | 0
5164 | 0.12485 | 0
5165 | 0.12485 | 0
5166 | 10.0351 | 12.6685
5167 | 1.2302 | 0
5168 | 1.5622 | 0
5169 | 0.12485 | 0
5170 | 0.12485 | 0
5171 | 0.12485 | 0
5172 | 0.82293 | 0
5173 | 0.12485 | 0
5174 | 0.12485 | 0
5175 | 0.12485 | 0
5176 | 0.12485 | 0
5177 | 0.12485 | 0
5178 | 5.1265 | 6.9093
5179 | 9.9879 | 12.6788
5180 | 0.12485 | 0
5181 | 1.2239 | 0
5182 | 0.12485 | 0
5183 | 0.12485 | 0
5184 | 0.12485 | 0
5185 | 0.12485 | 0
5186 | 0.12485 | 0
5187 | 0.12485 | 0
5188 | 0.12485 | 0
5189 | 0.12485 | 0
5190 | 10.0319 | 12.6643
5191 | 1.2299 | 0
5192 | 1.5617 | 0
5193 | 0.12485 | 0
5194 | 0.12485 | 0
5195 | 0.12485 | 0
5196 | 0.8227 | 0
5197 | 0.12485 | 0
5198 | 0.12485 | 0
5199 | 0.12485 | 0
5200 | 0.12485 | 0
5201 | 0.12485 | 0
5202 | 5.1248 | 6.9059
5203 | 9.9844 | 12.6752
5204 | 0.12485 | 0
5205 | 1.2235 | 0
5206 | 0.12485 | 0
5207 | 0.12485 | 0
5208 | 0.12485 | 0
5209 | 0.12485 | 0
5210 | 0.12485 | 0
5211 | 0.12485 | 0
5212 | 0.12485 | 0
5213 | 0.12485 | 0
5214 | 10.0289 | 12.6608
5215 | 1.2295 | 0
5216 | 1.5613 | 0
5217 | 0.12485 | 0
5218 | 0.12485 | 0
5219 | 0.12485 | 0
5220 | 0.82248 | 0
5221 | 0.12485 | 0
5222 | 0.12485 | 0
5223 | 0.12485 | 0
5224 | 0.12485 | 0
5225 | 0.12485 | 0
5226 | 5.1232 | 6.9029
5227 | 9.9812 | 12.6721
5228 | 0.12485 | 0
5229 | 1.2231 | 0
5230 | 0.12485 | 0
5231 | 0.12485 | 0
5232 | 0.12485 | 0
5233 | 0.12485 | 0
5234 | 0.12485 | 0
5235 | 0.12485 | 0
5236 | 0.12485 | 0
5237 | 0.12485 | 0
5238 | 10.0262 | 12.6577
5239 | 1.2292 | 0
5240 | 1.5609 | 0
5241 | 0.12485 | 0
5242 | 0.12485 | 0
5243 | 0.12485 | 0
5244 | 0.82229 | 0
5245 | 0.12485 | 0
5246 | 0.12485 | 0
5247 | 0.12485 | 0
5248 | 0.12485 | 0
5249 | 0.12485 | 0
5250 | 5.1218 | 6.9002
5251 | 9.9783 | 12.6692
5252 | 0.12485 | 0
5253 | 1.2228 | 0
5254 | 0.12485 | 0
5255 | 0.12485 | 0
5256 | 0.12485 | 0
5257 | 0.12485 | 0
5258 | 0.12485 | 0
5259 | 0.12485 | 0
5260 | 0.12485 | 0
5261 | 0.12485 | 0
5262 | 10.0237 | 12.655
5263 | 1.229 | 0
5264 | 1.5605 | 0
5265 | 0.12485 | 0
5266 | 0.12485 | 0
5267 | 0.12485 | 0
5268 | 0.82212 | 0
5269 | 0.12485 | 0
5270 | 0.12485 | 0
5271 | 0.12485 | 0
5272 | 0.12485 | 0
5273 | 0.12485 | 0
5274 | 5.1205 | 6.8979
5275 | 9.9758 | 12.6668
5276 | 0.12485 | 0
5277 | 1.2225 | 0
5278 | 0.12485 | 0
5279 | 0.12485 | 0
5280 | 0.12485 | 0
5281 | 0.12485 | 0
5282 | 0.12485 | 0
5283 | 0.12485 | 0
5284 | 0.12485 | 0
5285 | 0.12485 | 0
5286 | 10.0217 | 12.6525
5287 | 1.2287 | 0
5288 | 1.5602 | 0
5289 | 0.12485 | 0
5290 | 0.12485 | 0
5291 | 0.12485 | 0
5292 | 0.82197 | 0
5293 | 0.12485 | 0
5294 | 0.12485 | 0
5295 | 0.12485 | 0
5296 | 0.12485 | 0
5297 | 0.12485 | 0
5298 | 5.1194 | 6.8958
5299 | 9.9735 | 12.6646
5300 | 0.12485 | 0
5301 | 1.2223 | 0
5302 | 0.12485 | 0
5303 | 0.12485 | 0
5304 | 0.12485 | 0
5305 | 0.12485 | 0
5306 | 0.12485 | 0
5307 | 0.12485 | 0
5308 | 0.12485 | 0
5309 | 0.12485 | 0
5310 | 10.0199 | 12.6504
5311 | 1.2285 | 0
5312 | 1.56 | 0
5313 | 0.12485 | 0
5314 | 0.12485 | 0
5315 | 0.12485 | 0
5316 | 0.82184 | 0
5317 | 0.12485 | 0
5318 | 0.12485 | 0
5319 | 0.12485 | 0
5320 | 0.12485 | 0
5321 | 0.12485 | 0
5322 | 5.1185 | 6.8941
5323 | 9.9717 | 12.6627
5324 | 0.12485 | 0
5325 | 1.2221 | 0
5326 | 0.12485 | 0
5327 | 0.12485 | 0
5328 | 0.12485 | 0
5329 | 0.12485 | 0
5330 | 0.12485 | 0
5331 | 0.12485 | 0
5332 | 0.12485 | 0
5333 | 0.12485 | 0
5334 | 10.0185 | 12.6487
5335 | 1.2284 | 0
5336 | 1.5597 | 0
5337 | 0.12485 | 0
5338 | 0.12485 | 0
5339 | 0.12485 | 0
5340 | 0.82174 | 0
5341 | 0.12485 | 0
5342 | 0.12485 | 0
5343 | 0.12485 | 0
5344 | 0.12485 | 0
5345 | 0.12485 | 0
5346 | 5.1177 | 6.8926
5347 | 9.9701 | 12.6612
5348 | 0.12485 | 0
5349 | 1.2219 | 0
5350 | 0.12485 | 0
5351 | 0.12485 | 0
5352 | 0.12485 | 0
5353 | 0.12485 | 0
5354 | 0.12485 | 0
5355 | 0.12485 | 0
5356 | 0.12485 | 0
5357 | 0.12485 | 0
5358 | 10.0174 | 12.6473
5359 | 1.2283 | 0
5360 | 1.5596 | 0
5361 | 0.12485 | 0
5362 | 0.12485 | 0
5363 | 0.12485 | 0
5364 | 0.82166 | 0
5365 | 0.12485 | 0
5366 | 0.12485 | 0
5367 | 0.12485 | 0
5368 | 0.12485 | 0
5369 | 0.12485 | 0
5370 | 5.1171 | 6.8914
5371 | 9.9689 | 12.66
5372 | 0.12485 | 0
5373 | 1.2218 | 0
5374 | 0.12485 | 0
5375 | 0.12485 | 0
5376 | 0.12485 | 0
5377 | 0.12485 | 0
5378 | 0.12485 | 0
5379 | 0.12485 | 0
5380 | 0.12485 | 0
5381 | 0.12485 | 0
5382 | 10.0166 | 12.6462
5383 | 1.2282 | 0
5384 | 1.5595 | 0
5385 | 0.12485 | 0
5386 | 0.12485 | 0
5387 | 0.12485 | 0
5388 | 0.8216 | 0
5389 | 0.12485 | 0
5390 | 0.12485 | 0
5391 | 0.12485 | 0
5392 | 0.12485 | 0
5393 | 0.12485 | 0
5394 | 5.1167 | 6.8905
5395 | 9.9681 | 12.6591
5396 | 0.12485 | 0
5397 | 1.2217 | 0
5398 | 0.12485 | 0
5399 | 0.12485 | 0
5400 | 0.12485 | 0
5401 | 0.12485 | 0
5402 | 0.12485 | 0
5403 | 0.12485 | 0
5404 | 0.12485 | 0
5405 | 0.12485 | 0
5406 | 10.0162 | 12.6455
5407 | 1.2281 | 0
5408 | 1.5594 | 0
5409 | 0.12485 | 0
5410 | 0.12485 | 0
5411 | 0.12485 | 0
5412 | 0.82157 | 0
5413 | 0.12485 | 0
5414 | 0.12485 | 0
5415 | 0.12485 | 0
5416 | 0.12485 | 0
5417 | 0.12485 | 0
5418 | 5.1165 | 6.8899
5419 | 9.9676 | 12.6585
5420 | 0.12485 | 0
5421 | 1.2217 | 0
5422 | 0.12485 | 0
5423 | 0.12485 | 0
5424 | 0.12485 | 0
5425 | 0.12485 | 0
5426 | 0.12485 | 0
5427 | 0.12485 | 0
5428 | 0.12485 | 0
5429 | 0.12485 | 0
5430 | 10.0161 | 12.6451
5431 | 1.2281 | 0
5432 | 1.5594 | 0
5433 | 0.12485 | 0
5434 | 0.12485 | 0
5435 | 0.12485 | 0
5436 | 0.82156 | 0
5437 | 0.12485 | 0
5438 | 0.12485 | 0
5439 | 0.12485 | 0
5440 | 0.12485 | 0
5441 | 0.12485 | 0
5442 | 5.1164 | 6.8896
5443 | 9.9674 | 12.6583
5444 | 0.12485 | 0
5445 | 1.2216 | 0
5446 | 0.12485 | 0
5447 | 0.12485 | 0
5448 | 0.12485 | 0
5449 | 0.12485 | 0
5450 | 0.12485 | 0
5451 | 0.12485 | 0
5452 | 0.12485 | 0
5453 | 0.12485 | 0
5454 | 10.0164 | 12.645
5455 | 1.2281 | 0
5456 | 1.5594 | 0
5457 | 0.12485 | 0
5458 | 0.12485 | 0
5459 | 0.12485 | 0
5460 | 0.82157 | 0
5461 | 0.12485 | 0
5462 | 0.12485 | 0
5463 | 0.12485 | 0
5464 | 0.12485 | 0
5465 | 0.12485 | 0
5466 | 5.1165 | 6.8896
5467 | 9.9675 | 12.6583
5468 | 0.12485 | 0
5469 | 1.2216 | 0
5470 | 0.12485 | 0
5471 | 0.12485 | 0
5472 | 0.12485 | 0
5473 | 0.12485 | 0
5474 | 0.12485 | 0
5475 | 0.12485 | 0
5476 | 0.12485 | 0
5477 | 0.12485 | 0
5478 | 10.0169 | 12.6453
5479 | 1.2282 | 0
5480 | 1.5595 | 0
5481 | 0.12485 | 0
5482 | 0.12485 | 0
5483 | 0.12485 | 0
5484 | 0.82161 | 0
5485 | 0.12485 | 0
5486 | 0.12485 | 0
5487 | 0.12485 | 0
5488 | 0.12485 | 0
5489 | 0.12485 | 0
5490 | 5.1167 | 6.8899
5491 | 9.9681 | 12.6587
5492 | 0.12485 | 0
5493 | 1.2217 | 0
5494 | 0.12485 | 0
5495 | 0.12485 | 0
5496 | 0.12485 | 0
5497 | 0.12485 | 0
5498 | 0.12485 | 0
5499 | 0.12485 | 0
5500 | 0.12485 | 0
5501 | 0.12485 | 0
5502 | 10.0179 | 12.6459
5503 | 1.2283 | 0
5504 | 1.5596 | 0
5505 | 0.12485 | 0
5506 | 0.12485 | 0
5507 | 0.12485 | 0
5508 | 0.82167 | 0
5509 | 0.12485 | 0
5510 | 0.12485 | 0
5511 | 0.12485 | 0
5512 | 0.12485 | 0
5513 | 0.12485 | 0
5514 | 5.1172 | 6.8905
5515 | 9.9689 | 12.6594
5516 | 0.12485 | 0
5517 | 1.2218 | 0
5518 | 0.12485 | 0
5519 | 0.12485 | 0
5520 | 0.12485 | 0
5521 | 0.12485 | 0
5522 | 0.12485 | 0
5523 | 0.12485 | 0
5524 | 0.12485 | 0
5525 | 0.12485 | 0
5526 | 10.0191 | 12.6468
5527 | 1.2284 | 0
5528 | 1.5598 | 0
5529 | 0.12485 | 0
5530 | 0.12485 | 0
5531 | 0.12485 | 0
5532 | 0.82175 | 0
5533 | 0.12485 | 0
5534 | 0.12485 | 0
5535 | 0.12485 | 0
5536 | 0.12485 | 0
5537 | 0.12485 | 0
5538 | 5.1178 | 6.8914
5539 | 9.9701 | 12.6605
5540 | 0.12485 | 0
5541 | 1.2219 | 0
5542 | 0.12485 | 0
5543 | 0.12485 | 0
5544 | 0.12485 | 0
5545 | 0.12485 | 0
5546 | 0.12485 | 0
5547 | 0.12485 | 0
5548 | 0.12485 | 0
5549 | 0.12485 | 0
5550 | 10.0207 | 12.6481
5551 | 1.2286 | 0
5552 | 1.56 | 0
5553 | 0.12485 | 0
5554 | 0.12485 | 0
5555 | 0.12485 | 0
5556 | 0.82186 | 0
5557 | 0.12485 | 0
5558 | 0.12485 | 0
5559 | 0.12485 | 0
5560 | 0.12485 | 0
5561 | 0.12485 | 0
5562 | 5.1186 | 6.8926
5563 | 9.9716 | 12.6618
5564 | 0.12485 | 0
5565 | 1.2221 | 0
5566 | 0.12485 | 0
5567 | 0.12485 | 0
5568 | 0.12485 | 0
5569 | 0.12485 | 0
5570 | 0.12485 | 0
5571 | 0.12485 | 0
5572 | 0.12485 | 0
5573 | 0.12485 | 0
5574 | 10.0226 | 12.6497
5575 | 1.2288 | 0
5576 | 1.5603 | 0
5577 | 0.12485 | 0
5578 | 0.12485 | 0
5579 | 0.12485 | 0
5580 | 0.82198 | 0
5581 | 0.12485 | 0
5582 | 0.12485 | 0
5583 | 0.12485 | 0
5584 | 0.12485 | 0
5585 | 0.12485 | 0
5586 | 5.1195 | 6.8941
5587 | 9.9735 | 12.6635
5588 | 0.12485 | 0
5589 | 1.2223 | 0
5590 | 0.12485 | 0
5591 | 0.12485 | 0
5592 | 0.12485 | 0
5593 | 0.12485 | 0
5594 | 0.12485 | 0
5595 | 0.12485 | 0
5596 | 0.12485 | 0
5597 | 0.12485 | 0
5598 | 10.0248 | 12.6517
5599 | 1.229 | 0
5600 | 1.5606 | 0
5601 | 0.12485 | 0
5602 | 0.12485 | 0
5603 | 0.12485 | 0
5604 | 0.82214 | 0
5605 | 0.12485 | 0
5606 | 0.12485 | 0
5607 | 0.12485 | 0
5608 | 0.12485 | 0
5609 | 0.12485 | 0
5610 | 5.1206 | 6.8959
5611 | 9.9757 | 12.6655
5612 | 0.12485 | 0
5613 | 1.2225 | 0
5614 | 0.12485 | 0
5615 | 0.12485 | 0
5616 | 0.12485 | 0
5617 | 0.12485 | 0
5618 | 0.12485 | 0
5619 | 0.12485 | 0
5620 | 0.12485 | 0
5621 | 0.12485 | 0
5622 | 10.0274 | 12.654
5623 | 1.2293 | 0
5624 | 1.5609 | 0
5625 | 0.12485 | 0
5626 | 0.12485 | 0
5627 | 0.12485 | 0
5628 | 0.82231 | 0
5629 | 0.12485 | 0
5630 | 0.12485 | 0
5631 | 0.12485 | 0
5632 | 0.12485 | 0
5633 | 0.12485 | 0
5634 | 5.1219 | 6.8979
5635 | 9.9782 | 12.6678
5636 | 0.12485 | 0
5637 | 1.2228 | 0
5638 | 0.12485 | 0
5639 | 0.12485 | 0
5640 | 0.12485 | 0
5641 | 0.12485 | 0
5642 | 0.12485 | 0
5643 | 0.12485 | 0
5644 | 0.12485 | 0
5645 | 0.12485 | 0
5646 | 10.0303 | 12.6566
5647 | 1.2296 | 0
5648 | 1.5613 | 0
5649 | 0.12485 | 0
5650 | 0.12485 | 0
5651 | 0.12485 | 0
5652 | 0.82251 | 0
5653 | 0.12485 | 0
5654 | 0.12485 | 0
5655 | 0.12485 | 0
5656 | 0.12485 | 0
5657 | 0.12485 | 0
5658 | 5.1234 | 6.9003
5659 | 9.9811 | 12.6705
5660 | 0.12485 | 0
5661 | 1.2231 | 0
5662 | 0.12485 | 0
5663 | 0.12485 | 0
5664 | 0.12485 | 0
5665 | 0.12485 | 0
5666 | 0.12485 | 0
5667 | 0.12485 | 0
5668 | 0.12485 | 0
5669 | 0.12485 | 0
5670 | 10.0335 | 12.6596
5671 | 1.2299 | 0
5672 | 1.5618 | 0
5673 | 0.12485 | 0
5674 | 0.12485 | 0
5675 | 0.12485 | 0
5676 | 0.82273 | 0
5677 | 0.12485 | 0
5678 | 0.12485 | 0
5679 | 0.12485 | 0
5680 | 0.12485 | 0
5681 | 0.12485 | 0
5682 | 5.125 | 6.903
5683 | 9.9843 | 12.6734
5684 | 0.12485 | 0
5685 | 1.2234 | 0
5686 | 0.12485 | 0
5687 | 0.12485 | 0
5688 | 0.12485 | 0
5689 | 0.12485 | 0
5690 | 0.12485 | 0
5691 | 0.12485 | 0
5692 | 0.12485 | 0
5693 | 0.12485 | 0
5694 | 10.0371 | 12.6629
5695 | 1.2303 | 0
5696 | 1.5623 | 0
5697 | 0.12485 | 0
5698 | 0.12485 | 0
5699 | 0.12485 | 0
5700 | 0.82298 | 0
5701 | 0.12485 | 0
5702 | 0.12485 | 0
5703 | 0.12485 | 0
5704 | 0.12485 | 0
5705 | 0.12485 | 0
5706 | 5.1268 | 6.9059
5707 | 9.9878 | 12.6767
5708 | 0.12485 | 0
5709 | 1.2238 | 0
5710 | 0.12485 | 0
5711 | 0.12485 | 0
5712 | 0.12485 | 0
5713 | 0.12485 | 0
5714 | 0.12485 | 0
5715 | 0.12485 | 0
5716 | 0.12485 | 0
5717 | 0.12485 | 0
5718 | 10.041 | 12.6665
5719 | 1.2307 | 0
5720 | 1.5628 | 0
5721 | 0.12485 | 0
5722 | 0.12485 | 0
5723 | 0.12485 | 0
5724 | 0.82325 | 0
5725 | 0.12485 | 0
5726 | 0.12485 | 0
5727 | 0.12485 | 0
5728 | 0.12485 | 0
5729 | 0.12485 | 0
5730 | 5.1288 | 6.9092
5731 | 9.9917 | 12.6803
5732 | 0.12485 | 0
5733 | 1.2242 | 0
5734 | 0.12485 | 0
5735 | 0.12485 | 0
5736 | 0.12485 | 0
5737 | 0.12485 | 0
5738 | 0.12485 | 0
5739 | 0.12485 | 0
5740 | 0.12485 | 0
5741 | 0.12485 | 0
5742 | 10.0452 | 12.6705
5743 | 1.2312 | 0
5744 | 1.5634 | 0
5745 | 0.12485 | 0
5746 | 0.12485 | 0
5747 | 0.12485 | 0
5748 | 0.82354 | 0
5749 | 0.12485 | 0
5750 | 0.12485 | 0
5751 | 0.12485 | 0
5752 | 0.12485 | 0
5753 | 0.12485 | 0
5754 | 5.1309 | 6.9115
5755 | 9.9957 | 12.6845
5756 | 0.12485 | 0
5757 | 1.2247 | 0
5758 | 0.12485 | 0
5759 | 0.12485 | 0
5760 | 0.12485 | 0
5761 | 0.12485 | 0
5762 | 0.12485 | 0
5763 | 0.12485 | 0
5764 | 0.12485 | 0
5765 | 0.12485 | 0
5766 | 10.0496 | 12.675
5767 | 1.2317 | 0
5768 | 1.564 | 0
5769 | 0.12485 | 0
5770 | 0.12485 | 0
5771 | 0.12485 | 0
5772 | 0.82384 | 0
5773 | 0.12485 | 0
5774 | 0.12485 | 0
5775 | 0.12485 | 0
5776 | 0.12485 | 0
5777 | 0.12485 | 0
5778 | 5.1331 | 6.9121
5779 | 9.9997 | 12.6895
5780 | 0.12485 | 0
5781 | 1.2251 | 0
5782 | 0.12485 | 0
5783 | 0.12485 | 0
5784 | 0.12485 | 0
5785 | 0.12485 | 0
5786 | 0.12485 | 0
5787 | 0.12485 | 0
5788 | 0.12485 | 0
5789 | 0.12485 | 0
5790 | 10.0541 | 12.6802
5791 | 1.2322 | 0
5792 | 1.5647 | 0
5793 | 0.12485 | 0
5794 | 0.12485 | 0
5795 | 0.12485 | 0
5796 | 0.82417 | 0
5797 | 0.12485 | 0
5798 | 0.12485 | 0
5799 | 0.12485 | 0
5800 | 0.12485 | 0
5801 | 0.12485 | 0
5802 | 5.1354 | 6.9128
5803 | 10.0038 | 12.695
5804 | 0.12485 | 0
5805 | 1.2256 | 0
5806 | 0.12485 | 0
5807 | 0.12485 | 0
5808 | 0.12485 | 0
5809 | 0.12485 | 0
5810 | 0.12485 | 0
5811 | 0.12485 | 0
5812 | 0.12485 | 0
5813 | 0.12485 | 0
5814 | 10.0589 | 12.6859
5815 | 1.2327 | 0
5816 | 1.5654 | 0
5817 | 0.12485 | 0
5818 | 0.12485 | 0
5819 | 0.12485 | 0
5820 | 0.82451 | 0
5821 | 0.12485 | 0
5822 | 0.12485 | 0
5823 | 0.12485 | 0
5824 | 0.12485 | 0
5825 | 0.12485 | 0
5826 | 5.1379 | 6.9135
5827 | 10.0082 | 12.7009
5828 | 0.12485 | 0
5829 | 1.2261 | 0
5830 | 0.12485 | 0
5831 | 0.12485 | 0
5832 | 0.12485 | 0
5833 | 0.12485 | 0
5834 | 0.12485 | 0
5835 | 0.12485 | 0
5836 | 0.12485 | 0
5837 | 0.12485 | 0
5838 | 10.0639 | 12.6919
5839 | 1.2333 | 0
5840 | 1.5661 | 0
5841 | 0.12485 | 0
5842 | 0.12485 | 0
5843 | 0.12485 | 0
5844 | 0.82487 | 0
5845 | 0.12485 | 0
5846 | 0.12485 | 0
5847 | 0.12485 | 0
5848 | 0.12485 | 0
5849 | 0.12485 | 0
5850 | 5.1405 | 6.9143
5851 | 10.0128 | 12.7072
5852 | 0.12485 | 0
5853 | 1.2266 | 0
5854 | 0.12485 | 0
5855 | 0.12485 | 0
5856 | 0.12485 | 0
5857 | 0.12485 | 0
5858 | 0.12485 | 0
5859 | 0.12485 | 0
5860 | 0.12485 | 0
5861 | 0.12485 | 0
5862 | 10.0692 | 12.6983
5863 | 1.2339 | 0
5864 | 1.5669 | 0
5865 | 0.12485 | 0
5866 | 0.12485 | 0
5867 | 0.12485 | 0
5868 | 0.82525 | 0
5869 | 0.12485 | 0
5870 | 0.12485 | 0
5871 | 0.12485 | 0
5872 | 0.12485 | 0
5873 | 0.12485 | 0
5874 | 5.1432 | 6.9151
5875 | 10.0177 | 12.7139
5876 | 0.12485 | 0
5877 | 1.2272 | 0
5878 | 0.12485 | 0
5879 | 0.12485 | 0
5880 | 0.12485 | 0
5881 | 0.12485 | 0
5882 | 0.12485 | 0
5883 | 0.12485 | 0
5884 | 0.12485 | 0
5885 | 0.12485 | 0
5886 | 10.0749 | 12.7051
5887 | 1.2345 | 0
5888 | 1.5677 | 0
5889 | 0.12485 | 0
5890 | 0.12485 | 0
5891 | 0.12485 | 0
5892 | 0.82566 | 0
5893 | 0.12485 | 0
5894 | 0.12485 | 0
5895 | 0.12485 | 0
5896 | 0.12485 | 0
5897 | 0.12485 | 0
5898 | 5.1461 | 6.916
5899 | 10.0229 | 12.721
5900 | 0.12485 | 0
5901 | 1.2278 | 0
5902 | 0.12485 | 0
5903 | 0.12485 | 0
5904 | 0.12485 | 0
5905 | 0.12485 | 0
5906 | 0.12485 | 0
5907 | 0.12485 | 0
5908 | 0.12485 | 0
5909 | 0.12485 | 0
5910 | 10.0807 | 12.7123
5911 | 1.2352 | 0
5912 | 1.5686 | 0
5913 | 0.12485 | 0
5914 | 0.12485 | 0
5915 | 0.12485 | 0
5916 | 0.82609 | 0
5917 | 0.12485 | 0
5918 | 0.12485 | 0
5919 | 0.12485 | 0
5920 | 0.12485 | 0
5921 | 0.12485 | 0
5922 | 5.1492 | 6.9169
5923 | 10.0283 | 12.7284
5924 | 0.12485 | 0
5925 | 1.2284 | 0
5926 | 0.12485 | 0
5927 | 0.12485 | 0
5928 | 0.12485 | 0
5929 | 0.12485 | 0
5930 | 0.12485 | 0
5931 | 0.12485 | 0
5932 | 0.12485 | 0
5933 | 0.12485 | 0
5934 | 10.0869 | 12.7199
5935 | 1.2358 | 0
5936 | 1.5695 | 0
5937 | 0.12485 | 0
5938 | 0.12485 | 0
5939 | 0.12485 | 0
5940 | 0.82653 | 0
5941 | 0.12485 | 0
5942 | 0.12485 | 0
5943 | 0.12485 | 0
5944 | 0.12485 | 0
5945 | 0.12485 | 0
5946 | 5.1524 | 6.9179
5947 | 10.0341 | 12.7362
5948 | 0.12485 | 0
5949 | 1.2291 | 0
5950 | 0.12485 | 0
5951 | 0.12485 | 0
5952 | 0.12485 | 0
5953 | 0.12485 | 0
5954 | 0.12485 | 0
5955 | 0.12485 | 0
5956 | 0.12485 | 0
5957 | 0.12485 | 0
5958 | 10.0934 | 12.7278
5959 | 1.2366 | 0
5960 | 1.5704 | 0
5961 | 0.12485 | 0
5962 | 0.12485 | 0
5963 | 0.12485 | 0
5964 | 0.827 | 0
5965 | 0.12485 | 0
5966 | 0.12485 | 0
5967 | 0.12485 | 0
5968 | 0.12485 | 0
5969 | 0.12485 | 0
5970 | 5.1558 | 6.9189
5971 | 10.04 | 12.7444
5972 | 0.12485 | 0
5973 | 1.2298 | 0
5974 | 0.12485 | 0
5975 | 0.12485 | 0
5976 | 0.12485 | 0
5977 | 0.12485 | 0
5978 | 0.12485 | 0
5979 | 0.12485 | 0
5980 | 0.12485 | 0
5981 | 0.12485 | 0
5982 | 10.1001 | 12.7361
5983 | 1.2373 | 0
5984 | 1.5714 | 0
5985 | 0.12485 | 0
5986 | 0.12485 | 0
5987 | 0.12485 | 0
5988 | 0.82749 | 0
5989 | 0.12485 | 0
5990 | 0.12485 | 0
5991 | 0.12485 | 0
5992 | 0.12485 | 0
5993 | 0.12485 | 0
5994 | 5.1593 | 6.9199
5995 | 10.0463 | 12.753
5996 | 0.12485 | 0
5997 | 1.2305 | 0
5998 | 0.12485 | 0
5999 | 0.12485 | 0
6000 | 0.12485 | 0
6001 | 0.12485 | 0
6002 | 0.12485 | 0
6003 | 0.12485 | 0
6004 | 0.12485 | 0
6005 | 0.12485 | 0
6006 | 10.1071 | 12.7447
6007 | 1.2381 | 0
6008 | 1.5725 | 0
6009 | 0.12485 | 0
6010 | 0.12485 | 0
6011 | 0.12485 | 0
6012 | 0.828 | 0
6013 | 0.12485 | 0
6014 | 0.12485 | 0
6015 | 0.12485 | 0
6016 | 0.12485 | 0
6017 | 0.12485 | 0
6018 | 5.1629 | 6.921
6019 | 10.0528 | 12.7619
6020 | 0.12485 | 0
6021 | 1.2313 | 0
6022 | 0.12485 | 0
6023 | 0.12485 | 0
6024 | 0.12485 | 0
6025 | 0.12485 | 0
6026 | 0.12485 | 0
6027 | 0.12485 | 0
6028 | 0.12485 | 0
6029 | 0.12485 | 0
6030 | 10.1144 | 12.7537
6031 | 1.2389 | 0
6032 | 1.5735 | 0
6033 | 0.12485 | 0
6034 | 0.12485 | 0
6035 | 0.12485 | 0
6036 | 0.82852 | 0
6037 | 0.12485 | 0
6038 | 0.12485 | 0
6039 | 0.12485 | 0
6040 | 0.12485 | 0
6041 | 0.12485 | 0
6042 | 5.1667 | 6.9222
6043 | 10.0595 | 12.7712
6044 | 0.12485 | 0
6045 | 1.2321 | 0
6046 | 0.12485 | 0
6047 | 0.12485 | 0
6048 | 0.12485 | 0
6049 | 0.12485 | 0
6050 | 0.12485 | 0
6051 | 0.12485 | 0
6052 | 0.12485 | 0
6053 | 0.12485 | 0
6054 | 10.122 | 12.7631
6055 | 1.2398 | 0
6056 | 1.5747 | 0
6057 | 0.12485 | 0
6058 | 0.12485 | 0
6059 | 0.12485 | 0
6060 | 0.82907 | 0
6061 | 0.12485 | 0
6062 | 0.12485 | 0
6063 | 0.12485 | 0
6064 | 0.12485 | 0
6065 | 0.12485 | 0
6066 | 5.1706 | 6.9233
6067 | 10.0665 | 12.7808
6068 | 0.12485 | 0
6069 | 1.2329 | 0
6070 | 0.12485 | 0
6071 | 0.12485 | 0
6072 | 0.12485 | 0
6073 | 0.12485 | 0
6074 | 0.12485 | 0
6075 | 0.12485 | 0
6076 | 0.12485 | 0
6077 | 0.12485 | 0
6078 | 10.1298 | 12.7728
6079 | 1.2407 | 0
6080 | 1.5758 | 0
6081 | 0.12485 | 0
6082 | 0.12485 | 0
6083 | 0.12485 | 0
6084 | 0.82964 | 0
6085 | 0.12485 | 0
6086 | 0.12485 | 0
6087 | 0.12485 | 0
6088 | 0.12485 | 0
6089 | 0.12485 | 0
6090 | 5.1747 | 6.9246
6091 | 10.0738 | 12.7908
6092 | 0.12485 | 0
6093 | 1.2337 | 0
6094 | 0.12485 | 0
6095 | 0.12485 | 0
6096 | 0.12485 | 0
6097 | 0.12485 | 0
6098 | 0.12485 | 0
6099 | 0.12485 | 0
6100 | 0.12485 | 0
6101 | 0.12485 | 0
6102 | 10.1379 | 12.7829
6103 | 1.2416 | 0
6104 | 1.577 | 0
6105 | 0.12485 | 0
6106 | 0.12485 | 0
6107 | 0.12485 | 0
6108 | 0.83023 | 0
6109 | 0.12485 | 0
6110 | 0.12485 | 0
6111 | 0.12485 | 0
6112 | 0.12485 | 0
6113 | 0.12485 | 0
6114 | 5.179 | 6.9258
6115 | 10.0813 | 12.8012
6116 | 0.12485 | 0
6117 | 1.2346 | 0
6118 | 0.12485 | 0
6119 | 0.12485 | 0
6120 | 0.12485 | 0
6121 | 0.12485 | 0
6122 | 0.12485 | 0
6123 | 0.12485 | 0
6124 | 0.12485 | 0
6125 | 0.12485 | 0
6126 | 10.1463 | 12.7933
6127 | 1.2426 | 0
6128 | 1.5782 | 0
6129 | 0.12485 | 0
6130 | 0.12485 | 0
6131 | 0.12485 | 0
6132 | 0.83084 | 0
6133 | 0.12485 | 0
6134 | 0.12485 | 0
6135 | 0.12485 | 0
6136 | 0.12485 | 0
6137 | 0.12485 | 0
6138 | 5.1833 | 6.9272
6139 | 10.0891 | 12.8119
6140 | 0.12485 | 0
6141 | 1.2355 | 0
6142 | 0.12485 | 0
6143 | 0.12485 | 0
6144 | 0.12485 | 0
6145 | 0.12485 | 0
6146 | 0.12485 | 0
6147 | 0.12485 | 0
6148 | 0.12485 | 0
6149 | 0.12485 | 0
6150 | 10.1549 | 12.8041
6151 | 1.2435 | 0
6152 | 1.5795 | 0
6153 | 0.12485 | 0
6154 | 0.12485 | 0
6155 | 0.12485 | 0
6156 | 0.83146 | 0
6157 | 0.12485 | 0
6158 | 0.12485 | 0
6159 | 0.12485 | 0
6160 | 0.12485 | 0
6161 | 0.12485 | 0
6162 | 5.1878 | 6.9285
6163 | 10.0971 | 12.823
6164 | 0.12485 | 0
6165 | 1.2364 | 0
6166 | 0.12485 | 0
6167 | 0.12485 | 0
6168 | 0.12485 | 0
6169 | 0.12485 | 0
6170 | 0.12485 | 0
6171 | 0.12485 | 0
6172 | 0.12485 | 0
6173 | 0.12485 | 0
6174 | 10.1638 | 12.8152
6175 | 1.2445 | 0
6176 | 1.5808 | 0
6177 | 0.12485 | 0
6178 | 0.12485 | 0
6179 | 0.12485 | 0
6180 | 0.83211 | 0
6181 | 0.12485 | 0
6182 | 0.12485 | 0
6183 | 0.12485 | 0
6184 | 0.12485 | 0
6185 | 0.12485 | 0
6186 | 5.1925 | 6.9299
6187 | 10.1054 | 12.8344
6188 | 0.12485 | 0
6189 | 1.2374 | 0
6190 | 0.12485 | 0
6191 | 0.12485 | 0
6192 | 0.12485 | 0
6193 | 0.12485 | 0
6194 | 0.12485 | 0
6195 | 0.12485 | 0
6196 | 0.12485 | 0
6197 | 0.12485 | 0
6198 | 10.173 | 12.8266
6199 | 1.2456 | 0
6200 | 1.5822 | 0
6201 | 0.12485 | 0
6202 | 0.12485 | 0
6203 | 0.12485 | 0
6204 | 0.83277 | 0
6205 | 0.12485 | 0
6206 | 0.12485 | 0
6207 | 0.12485 | 0
6208 | 0.12485 | 0
6209 | 0.12485 | 0
6210 | 5.1972 | 6.9314
6211 | 10.1139 | 12.8462
6212 | 0.12485 | 0
6213 | 1.2384 | 0
6214 | 0.12485 | 0
6215 | 0.12485 | 0
6216 | 0.12485 | 0
6217 | 0.12485 | 0
6218 | 0.12485 | 0
6219 | 0.12485 | 0
6220 | 0.12485 | 0
6221 | 0.12485 | 0
6222 | 10.1824 | 12.8384
6223 | 1.2466 | 0
6224 | 1.5836 | 0
6225 | 0.12485 | 0
6226 | 0.12485 | 0
6227 | 0.12485 | 0
6228 | 0.83346 | 0
6229 | 0.12485 | 0
6230 | 0.12485 | 0
6231 | 0.12485 | 0
6232 | 0.12485 | 0
6233 | 0.12485 | 0
6234 | 5.2022 | 6.9329
6235 | 10.1227 | 12.8583
6236 | 0.12485 | 0
6237 | 1.2394 | 0
6238 | 0.12485 | 0
6239 | 0.12485 | 0
6240 | 0.12485 | 0
6241 | 0.12485 | 0
6242 | 0.12485 | 0
6243 | 0.12485 | 0
6244 | 0.12485 | 0
6245 | 0.12485 | 0
6246 | 10.1921 | 12.8505
6247 | 1.2477 | 0
6248 | 1.585 | 0
6249 | 0.12485 | 0
6250 | 0.12485 | 0
6251 | 0.12485 | 0
6252 | 0.83416 | 0
6253 | 0.12485 | 0
6254 | 0.12485 | 0
6255 | 0.12485 | 0
6256 | 0.12485 | 0
6257 | 0.12485 | 0
6258 | 5.2072 | 6.9344
6259 | 10.1317 | 12.8707
6260 | 0.12485 | 0
6261 | 1.2404 | 0
6262 | 0.12485 | 0
6263 | 0.12485 | 0
6264 | 0.12485 | 0
6265 | 0.12485 | 0
6266 | 0.12485 | 0
6267 | 0.12485 | 0
6268 | 0.12485 | 0
6269 | 0.12485 | 0
6270 | 10.202 | 12.863
6271 | 1.2488 | 0
6272 | 1.5865 | 0
6273 | 0.12485 | 0
6274 | 0.12485 | 0
6275 | 0.12485 | 0
6276 | 0.83488 | 0
6277 | 0.12485 | 0
6278 | 0.12485 | 0
6279 | 0.12485 | 0
6280 | 0.12485 | 0
6281 | 0.12485 | 0
6282 | 5.2124 | 6.936
6283 | 10.1409 | 12.8834
6284 | 0.12485 | 0
6285 | 1.2415 | 0
6286 | 0.12485 | 0
6287 | 0.12485 | 0
6288 | 0.12485 | 0
6289 | 0.12485 | 0
6290 | 0.12485 | 0
6291 | 0.12485 | 0
6292 | 0.12485 | 0
6293 | 0.12485 | 0
6294 | 10.2121 | 12.8757
6295 | 1.25 | 0
6296 | 1.588 | 0
6297 | 0.12485 | 0
6298 | 0.12485 | 0
6299 | 0.12485 | 0
6300 | 0.83562 | 0
6301 | 0.12485 | 0
6302 | 0.12485 | 0
6303 | 0.12485 | 0
6304 | 0.12485 | 0
6305 | 0.12485 | 0
6306 | 5.2177 | 6.9376
6307 | 10.1503 | 12.8965
6308 | 0.12485 | 0
6309 | 1.2426 | 0
6310 | 0.12485 | 0
6311 | 0.12485 | 0
6312 | 0.12485 | 0
6313 | 0.12485 | 0
6314 | 0.12485 | 0
6315 | 0.12485 | 0
6316 | 0.12485 | 0
6317 | 0.12485 | 0
6318 | 10.2225 | 12.8888
6319 | 1.2512 | 0
6320 | 1.5895 | 0
6321 | 0.12485 | 0
6322 | 0.12485 | 0
6323 | 0.12485 | 0
6324 | 0.83638 | 0
6325 | 0.12485 | 0
6326 | 0.12485 | 0
6327 | 0.12485 | 0
6328 | 0.12485 | 0
6329 | 0.12485 | 0
6330 | 5.2231 | 6.9392
6331 | 10.16 | 12.91
6332 | 0.12485 | 0
6333 | 1.2437 | 0
6334 | 0.12485 | 0
6335 | 0.12485 | 0
6336 | 0.12485 | 0
6337 | 0.12485 | 0
6338 | 0.12485 | 0
6339 | 0.12485 | 0
6340 | 0.12485 | 0
6341 | 0.12485 | 0
6342 | 10.2332 | 12.9023
6343 | 1.2524 | 0
6344 | 1.5911 | 0
6345 | 0.12485 | 0
6346 | 0.12485 | 0
6347 | 0.12485 | 0
6348 | 0.83715 | 0
6349 | 0.12485 | 0
6350 | 0.12485 | 0
6351 | 0.12485 | 0
6352 | 0.12485 | 0
6353 | 0.12485 | 0
6354 | 5.2287 | 6.9409
6355 | 10.1699 | 12.9237
6356 | 0.12485 | 0
6357 | 1.2449 | 0
6358 | 0.12485 | 0
6359 | 0.12485 | 0
6360 | 0.12485 | 0
6361 | 0.12485 | 0
6362 | 0.12485 | 0
6363 | 0.12485 | 0
6364 | 0.12485 | 0
6365 | 0.12485 | 0
6366 | 10.244 | 12.916
6367 | 1.2536 | 0
6368 | 1.5927 | 0
6369 | 0.12485 | 0
6370 | 0.12485 | 0
6371 | 0.12485 | 0
6372 | 0.83794 | 0
6373 | 0.12485 | 0
6374 | 0.12485 | 0
6375 | 0.12485 | 0
6376 | 0.12485 | 0
6377 | 0.12485 | 0
6378 | 5.2344 | 6.9426
6379 | 10.1801 | 12.9377
6380 | 0.12485 | 0
6381 | 1.246 | 0
6382 | 0.12485 | 0
6383 | 0.12485 | 0
6384 | 0.12485 | 0
6385 | 0.12485 | 0
6386 | 0.12485 | 0
6387 | 0.12485 | 0
6388 | 0.12485 | 0
6389 | 0.12485 | 0
6390 | 10.2552 | 12.93
6391 | 1.2549 | 0
6392 | 1.5943 | 0
6393 | 0.12485 | 0
6394 | 0.12485 | 0
6395 | 0.12485 | 0
6396 | 0.83875 | 0
6397 | 0.12485 | 0
6398 | 0.12485 | 0
6399 | 0.12485 | 0
6400 | 0.12485 | 0
6401 | 0.12485 | 0
6402 | 5.2402 | 6.9444
6403 | 10.1904 | 12.9521
6404 | 0.12485 | 0
6405 | 1.2473 | 0
6406 | 0.12485 | 0
6407 | 0.12485 | 0
6408 | 0.12485 | 0
6409 | 0.12485 | 0
6410 | 0.12485 | 0
6411 | 0.12485 | 0
6412 | 0.12485 | 0
6413 | 0.12485 | 0
6414 | 10.2665 | 12.9444
6415 | 1.2562 | 0
6416 | 1.596 | 0
6417 | 0.12485 | 0
6418 | 0.12485 | 0
6419 | 0.12485 | 0
6420 | 0.83958 | 0
6421 | 0.12485 | 0
6422 | 0.12485 | 0
6423 | 0.12485 | 0
6424 | 0.12485 | 0
6425 | 0.12485 | 0
6426 | 5.2461 | 6.9462
6427 | 10.201 | 12.9668
6428 | 0.12485 | 0
6429 | 1.2485 | 0
6430 | 0.12485 | 0
6431 | 0.12485 | 0
6432 | 0.12485 | 0
6433 | 0.12485 | 0
6434 | 0.12485 | 0
6435 | 0.12485 | 0
6436 | 0.12485 | 0
6437 | 0.12485 | 0
6438 | 10.2781 | 12.959
6439 | 1.2575 | 0
6440 | 1.5977 | 0
6441 | 0.12485 | 0
6442 | 0.12485 | 0
6443 | 0.12485 | 0
6444 | 0.84042 | 0
6445 | 0.12485 | 0
6446 | 0.12485 | 0
6447 | 0.12485 | 0
6448 | 0.12485 | 0
6449 | 0.12485 | 0
6450 | 5.2522 | 6.9481
6451 | 10.2118 | 12.9818
6452 | 0.12485 | 0
6453 | 1.2497 | 0
6454 | 0.12485 | 0
6455 | 0.12485 | 0
6456 | 0.12485 | 0
6457 | 0.12485 | 0
6458 | 0.12485 | 0
6459 | 0.12485 | 0
6460 | 0.12485 | 0
6461 | 0.12485 | 0
6462 | 10.2899 | 12.9739
6463 | 1.2588 | 0
6464 | 1.5995 | 0
6465 | 0.12485 | 0
6466 | 0.12485 | 0
6467 | 0.12485 | 0
6468 | 0.84128 | 0
6469 | 0.12485 | 0
6470 | 0.12485 | 0
6471 | 0.12485 | 0
6472 | 0.12485 | 0
6473 | 0.12485 | 0
6474 | 5.2584 | 6.9499
6475 | 10.2228 | 12.997
6476 | 0.12485 | 0
6477 | 1.251 | 0
6478 | 0.12485 | 0
6479 | 0.12485 | 0
6480 | 0.12485 | 0
6481 | 0.12485 | 0
6482 | 0.12485 | 0
6483 | 0.12485 | 0
6484 | 0.12485 | 0
6485 | 0.12485 | 0
6486 | 10.3019 | 12.9892
6487 | 1.2602 | 0
6488 | 1.6012 | 0
6489 | 0.12485 | 0
6490 | 0.12485 | 0
6491 | 0.12485 | 0
6492 | 0.84216 | 0
6493 | 0.12485 | 0
6494 | 0.12485 | 0
6495 | 0.12485 | 0
6496 | 0.12485 | 0
6497 | 0.12485 | 0
6498 | 5.2647 | 6.9519
6499 | 10.234 | 13.0126
6500 | 0.12485 | 0
6501 | 1.2523 | 0
6502 | 0.12485 | 0
6503 | 0.12485 | 0
6504 | 0.12485 | 0
6505 | 0.12485 | 0
6506 | 0.12485 | 0
6507 | 0.12485 | 0
6508 | 0.12485 | 0
6509 | 0.12485 | 0
6510 | 10.3141 | 13.0047
6511 | 1.2616 | 0
6512 | 1.603 | 0
6513 | 0.12485 | 0
6514 | 0.12485 | 0
6515 | 0.12485 | 0
6516 | 0.84305 | 0
6517 | 0.12485 | 0
6518 | 0.12485 | 0
6519 | 0.12485 | 0
6520 | 0.12485 | 0
6521 | 0.12485 | 0
6522 | 5.2711 | 6.9538
6523 | 10.2454 | 13.0285
6524 | 0.12485 | 0
6525 | 1.2536 | 0
6526 | 0.12485 | 0
6527 | 0.12485 | 0
6528 | 0.12485 | 0
6529 | 0.12485 | 0
6530 | 0.12485 | 0
6531 | 0.12485 | 0
6532 | 0.12485 | 0
6533 | 0.12485 | 0
6534 | 10.3266 | 13.0205
6535 | 1.263 | 0
6536 | 1.6049 | 0
6537 | 0.12485 | 0
6538 | 0.12485 | 0
6539 | 0.12485 | 0
6540 | 0.84396 | 0
6541 | 0.12485 | 0
6542 | 0.12485 | 0
6543 | 0.12485 | 0
6544 | 0.12485 | 0
6545 | 0.12485 | 0
6546 | 5.2776 | 6.9558
6547 | 10.257 | 13.0446
6548 | 0.12485 | 0
6549 | 1.255 | 0
6550 | 0.12485 | 0
6551 | 0.12485 | 0
6552 | 0.12485 | 0
6553 | 0.12485 | 0
6554 | 0.12485 | 0
6555 | 0.12485 | 0
6556 | 0.12485 | 0
6557 | 0.12485 | 0
6558 | 10.3392 | 13.0366
6559 | 1.2644 | 0
6560 | 1.6068 | 0
6561 | 0.12485 | 0
6562 | 0.12485 | 0
6563 | 0.12485 | 0
6564 | 0.84488 | 0
6565 | 0.12485 | 0
6566 | 0.12485 | 0
6567 | 0.12485 | 0
6568 | 0.12485 | 0
6569 | 0.12485 | 0
6570 | 5.2842 | 6.9578
6571 | 10.2688 | 13.061
6572 | 0.12485 | 0
6573 | 1.2564 | 0
6574 | 0.12485 | 0
6575 | 0.12485 | 0
6576 | 0.12485 | 0
6577 | 0.12485 | 0
6578 | 0.12485 | 0
6579 | 0.12485 | 0
6580 | 0.12485 | 0
6581 | 0.12485 | 0
6582 | 10.3521 | 13.053
6583 | 1.2659 | 0
6584 | 1.6087 | 0
6585 | 0.12485 | 0
6586 | 0.12485 | 0
6587 | 0.12485 | 0
6588 | 0.84582 | 0
6589 | 0.12485 | 0
6590 | 0.12485 | 0
6591 | 0.12485 | 0
6592 | 0.12485 | 0
6593 | 0.12485 | 0
6594 | 5.291 | 6.9599
6595 | 10.2808 | 13.0777
6596 | 0.12485 | 0
6597 | 1.2578 | 0
6598 | 0.12485 | 0
6599 | 0.12485 | 0
6600 | 0.12485 | 0
6601 | 0.12485 | 0
6602 | 0.12485 | 0
6603 | 0.12485 | 0
6604 | 0.12485 | 0
6605 | 0.12485 | 0
6606 | 10.3652 | 13.0696
6607 | 1.2674 | 0
6608 | 1.6106 | 0
6609 | 0.12485 | 0
6610 | 0.12485 | 0
6611 | 0.12485 | 0
6612 | 0.84677 | 0
6613 | 0.12485 | 0
6614 | 0.12485 | 0
6615 | 0.12485 | 0
6616 | 0.12485 | 0
6617 | 0.12485 | 0
6618 | 5.2978 | 6.962
6619 | 10.293 | 13.0947
6620 | 0.12485 | 0
6621 | 1.2592 | 0
6622 | 0.12485 | 0
6623 | 0.12485 | 0
6624 | 0.12485 | 0
6625 | 0.12485 | 0
6626 | 0.12485 | 0
6627 | 0.12485 | 0
6628 | 0.12485 | 0
6629 | 0.12485 | 0
6630 | 10.3785 | 13.0865
6631 | 1.2689 | 0
6632 | 1.6126 | 0
6633 | 0.12485 | 0
6634 | 0.12485 | 0
6635 | 0.12485 | 0
6636 | 0.84774 | 0
6637 | 0.12485 | 0
6638 | 0.12485 | 0
6639 | 0.12485 | 0
6640 | 0.12485 | 0
6641 | 0.12485 | 0
6642 | 5.3048 | 6.9641
6643 | 10.3054 | 13.1119
6644 | 0.12485 | 0
6645 | 1.2606 | 0
6646 | 0.12485 | 0
6647 | 0.12485 | 0
6648 | 0.12485 | 0
6649 | 0.12485 | 0
6650 | 0.12485 | 0
6651 | 0.12485 | 0
6652 | 0.12485 | 0
6653 | 0.12485 | 0
6654 | 10.3919 | 13.1036
6655 | 1.2704 | 0
6656 | 1.6146 | 0
6657 | 0.12485 | 0
6658 | 0.12485 | 0
6659 | 0.12485 | 0
6660 | 0.84872 | 0
6661 | 0.12485 | 0
6662 | 0.12485 | 0
6663 | 0.12485 | 0
6664 | 0.12485 | 0
6665 | 0.12485 | 0
6666 | 5.3118 | 6.9662
6667 | 10.318 | 13.1294
6668 | 0.12485 | 0
6669 | 1.2621 | 0
6670 | 0.12485 | 0
6671 | 0.12485 | 0
6672 | 0.12485 | 0
6673 | 0.12485 | 0
6674 | 0.12485 | 0
6675 | 0.12485 | 0
6676 | 0.12485 | 0
6677 | 0.12485 | 0
6678 | 10.4056 | 13.121
6679 | 1.2719 | 0
6680 | 1.6166 | 0
6681 | 0.12485 | 0
6682 | 0.12485 | 0
6683 | 0.12485 | 0
6684 | 0.84971 | 0
6685 | 0.12485 | 0
6686 | 0.12485 | 0
6687 | 0.12485 | 0
6688 | 0.12485 | 0
6689 | 0.12485 | 0
6690 | 5.319 | 6.9684
6691 | 10.3308 | 13.1472
6692 | 0.12485 | 0
6693 | 1.2636 | 0
6694 | 0.12485 | 0
6695 | 0.12485 | 0
6696 | 0.12485 | 0
6697 | 0.12485 | 0
6698 | 0.12485 | 0
6699 | 0.12485 | 0
6700 | 0.12485 | 0
6701 | 0.12485 | 0
6702 | 10.4194 | 13.1387
6703 | 1.2735 | 0
6704 | 1.6186 | 0
6705 | 0.12485 | 0
6706 | 0.12485 | 0
6707 | 0.12485 | 0
6708 | 0.85072 | 0
6709 | 0.12485 | 0
6710 | 0.12485 | 0
6711 | 0.12485 | 0
6712 | 0.12485 | 0
6713 | 0.12485 | 0
6714 | 5.3262 | 6.9706
6715 | 10.7421 | 13.2316
6716 | 0.12485 | 0
6717 | 1.2586 | 0
6718 | 0.12485 | 0
6719 | 0.12485 | 0
6720 | 0.12485 | 0
6721 | 0.12485 | 0
6722 | 0.12485 | 0
6723 | 0.12485 | 0
6724 | 0.12485 | 0
6725 | 0.12485 | 0
6726 | 10.3771 | 13.2476
6727 | 1.2718 | 0
6728 | 1.6164 | 0
6729 | 0.12485 | 0
6730 | 0.12485 | 0
6731 | 0.12485 | 0
6732 | 0.84964 | 0
6733 | 0.12485 | 0
6734 | 0.12485 | 0
6735 | 0.12485 | 0
6736 | 0.12485 | 0
6737 | 0.12485 | 0
6738 | 5.5261 | 6.7463
6739 | 10.6684 | 13.5257
6740 | 0.12485 | 0
6741 | 1.256 | 0
6742 | 0.12485 | 0
6743 | 0.12485 | 0
6744 | 0.12485 | 0
6745 | 0.12485 | 0
6746 | 0.12485 | 0
6747 | 0.12485 | 0
6748 | 0.12485 | 0
6749 | 0.12485 | 0
6750 | 10.7616 | 13.3957
6751 | 1.2647 | 0
6752 | 1.6072 | 0
6753 | 0.12485 | 0
6754 | 0.12485 | 0
6755 | 0.12485 | 0
6756 | 0.84521 | 0
6757 | 0.12485 | 0
6758 | 0.12485 | 0
6759 | 0.12485 | 0
6760 | 0.12485 | 0
6761 | 0.12485 | 0
6762 | 5.4996 | 6.8359
6763 | 10.8296 | 13.0492
6764 | 0.12485 | 0
6765 | 1.2397 | 0
6766 | 0.12485 | 0
6767 | 0.12485 | 0
6768 | 0.12485 | 0
6769 | 0.12485 | 0
6770 | 0.12485 | 0
6771 | 0.12485 | 0
6772 | 0.12485 | 0
6773 | 0.12485 | 0
6774 | 10.8305 | 13.1668
6775 | 1.2435 | 0
6776 | 1.5797 | 0
6777 | 0.12485 | 0
6778 | 0.12485 | 0
6779 | 0.12485 | 0
6780 | 0.83188 | 0
6781 | 0.12485 | 0
6782 | 0.12485 | 0
6783 | 0.12485 | 0
6784 | 0.12485 | 0
6785 | 0.12485 | 0
6786 | 5.4126 | 6.9617
6787 | 10.6984 | 13.3073
6788 | 0.12485 | 0
6789 | 1.232 | 0
6790 | 0.12485 | 0
6791 | 0.12485 | 0
6792 | 0.12485 | 0
6793 | 0.12485 | 0
6794 | 0.12485 | 0
6795 | 0.12485 | 0
6796 | 0.12485 | 0
6797 | 0.12485 | 0
6798 | 10.7698 | 13.3253
6799 | 1.2404 | 0
6800 | 1.5756 | 0
6801 | 0.12485 | 0
6802 | 0.12485 | 0
6803 | 0.12485 | 0
6804 | 0.82995 | 0
6805 | 0.12485 | 0
6806 | 0.12485 | 0
6807 | 0.12485 | 0
6808 | 0.12485 | 0
6809 | 0.12485 | 6.3674
6810 | 5.6514 | 0
6811 | 10.5488 | 13.6417
6812 | 0.12485 | 0
6813 | 1.2221 | 0
6814 | 0.12485 | 0
6815 | 0.12485 | 0
6816 | 0.12485 | 0
6817 | 0.12485 | 0
6818 | 0.12485 | 0
6819 | 0.12485 | 0
6820 | 0.12485 | 0
6821 | 0.12485 | 0
6822 | 10.6909 | 13.5062
6823 | 1.2361 | 0
6824 | 1.57 | 0
6825 | 0.12485 | 0
6826 | 0.12485 | 0
6827 | 0.12485 | 0
6828 | 0.82724 | 0
6829 | 0.12485 | 0
6830 | 0.12485 | 6.37
6831 | 0.12485 | 0
6832 | 0.12485 | 0
6833 | 0.12485 | 0
6834 | 5.6292 | 0
6835 | 10.5133 | 13.6696
6836 | 0.12485 | 0
6837 | 1.2192 | 0
6838 | 0.12485 | 0
6839 | 0.12485 | 0
6840 | 0.12485 | 0
6841 | 0.12485 | 0
6842 | 0.12485 | 0
6843 | 0.12485 | 0
6844 | 0.12485 | 0
6845 | 0.12485 | 0
6846 | 10.6661 | 13.5202
6847 | 1.2341 | 0
6848 | 1.5674 | 0
6849 | 0.12485 | 0
6850 | 0.12485 | 0
6851 | 0.12485 | 0
6852 | 0.82601 | 6.3633
6853 | 0.12485 | 0
6854 | 0.12485 | 0
6855 | 0.12485 | 0
6856 | 0.12485 | 0
6857 | 0.12485 | 0
6858 | 5.6176 | 0
6859 | 10.8691 | 13.7213
6860 | 0.12485 | 0
6861 | 1.2112 | 0
6862 | 0.12485 | 0
6863 | 0.12485 | 0
6864 | 0.12485 | 0
6865 | 0.12485 | 0
6866 | 0.12485 | 0
6867 | 0.12485 | 0
6868 | 0.12485 | 0
6869 | 0.12485 | 0
6870 | 10.5957 | 13.5124
6871 | 1.2276 | 0
6872 | 1.5591 | 0
6873 | 0.12485 | 0
6874 | 0.12485 | 0
6875 | 0.12485 | 0
6876 | 0.82198 | 6.492
6877 | 0.12485 | 0
6878 | 0.12485 | 0
6879 | 0.12485 | 0
6880 | 0.12485 | 0
6881 | 0.12485 | 0
6882 | 5.6007 | 6.4486
6883 | 10.9469 | 12.456
6884 | 0.12485 | 0
6885 | 1.3058 | 0
6886 | 0.12485 | 0
6887 | 0.12485 | 0
6888 | 0.12485 | 0
6889 | 0.12485 | 0
6890 | 0.12485 | 0
6891 | 0.12485 | 0
6892 | 0.12485 | 0
6893 | 0.12485 | 0
6894 | 10.7953 | 12.8565
6895 | 1.302 | 0
6896 | 1.6557 | 0
6897 | 0.12485 | 0
6898 | 0.12485 | 0
6899 | 0.12485 | 0
6900 | 0.86881 | 0
6901 | 0.12485 | 0
6902 | 0.12485 | 0
6903 | 0.12485 | 0
6904 | 0.12485 | 0
6905 | 0.12485 | 0
6906 | 5.4538 | 6.9659
6907 | 10.5644 | 13.1523
6908 | 0.12485 | 0
6909 | 1.2846 | 0
6910 | 0.12485 | 0
6911 | 0.12485 | 0
6912 | 0.12485 | 0
6913 | 0.12485 | 0
6914 | 0.12485 | 0
6915 | 0.12485 | 0
6916 | 0.12485 | 0
6917 | 0.12485 | 0
6918 | 10.6109 | 13.2092
6919 | 1.292 | 0
6920 | 1.6428 | 0
6921 | 0.12485 | 0
6922 | 0.12485 | 0
6923 | 0.12485 | 0
6924 | 0.86256 | 0
6925 | 0.12485 | 0
6926 | 0.12485 | 0
6927 | 0.12485 | 0
6928 | 0.12485 | 0
6929 | 0.12485 | 0
6930 | 5.618 | 6.7502
6931 | 10.8288 | 13.5736
6932 | 0.12485 | 0
6933 | 1.2712 | 0
6934 | 0.12485 | 0
6935 | 0.12485 | 0
6936 | 0.12485 | 0
6937 | 0.12485 | 0
6938 | 0.12485 | 0
6939 | 0.12485 | 0
6940 | 0.12485 | 0
6941 | 0.12485 | 0
6942 | 10.9021 | 13.5121
6943 | 1.2794 | 0
6944 | 1.6264 | 0
6945 | 0.12485 | 0
6946 | 0.12485 | 0
6947 | 0.12485 | 0
6948 | 0.85466 | 0
6949 | 0.12485 | 0
6950 | 0.12485 | 0
6951 | 0.12485 | 0
6952 | 0.12485 | 0
6953 | 0.12485 | 0
6954 | 5.5678 | 6.8513
6955 | 10.9541 | 13.188
6956 | 0.12485 | 0
6957 | 1.253 | 0
6958 | 0.12485 | 0
6959 | 0.12485 | 0
6960 | 0.12485 | 0
6961 | 0.12485 | 0
6962 | 0.12485 | 0
6963 | 0.12485 | 0
6964 | 0.12485 | 0
6965 | 0.12485 | 0
6966 | 10.9591 | 13.3112
6967 | 1.2572 | 0
6968 | 1.5975 | 0
6969 | 0.12485 | 0
6970 | 0.12485 | 0
6971 | 0.12485 | 0
6972 | 0.84067 | 0
6973 | 0.12485 | 0
6974 | 0.12485 | 0
6975 | 0.12485 | 0
6976 | 0.12485 | 6.365
6977 | 0.12485 | 0
6978 | 5.727 | 0
6979 | 10.6811 | 13.6631
6980 | 0.12485 | 0
6981 | 1.2343 | 0
6982 | 0.12485 | 0
6983 | 0.12485 | 0
6984 | 0.12485 | 0
6985 | 0.12485 | 0
6986 | 0.12485 | 0
6987 | 0.12485 | 0
6988 | 0.12485 | 0
6989 | 0.12485 | 0
6990 | 10.8038 | 13.5348
6991 | 1.2466 | 0
6992 | 1.5838 | 0
6993 | 0.12485 | 0
6994 | 0.12485 | 0
6995 | 0.12485 | 0
6996 | 0.83404 | 6.394
6997 | 0.12485 | 0
6998 | 0.12485 | 0
6999 | 0.12485 | 0
7000 | 0.12485 | 0
7001 | 0.12485 | 0
7002 | 5.6771 | 6.4021
7003 | 11.071 | 12.4769
7004 | 0.12485 | 0
7005 | 1.3174 | 0
7006 | 0.12485 | 0
7007 | 0.12485 | 0
7008 | 0.12485 | 0
7009 | 0.12485 | 0
7010 | 0.12485 | 0
7011 | 0.12485 | 0
7012 | 0.12485 | 0
7013 | 0.12485 | 0
7014 | 10.9004 | 12.9115
7015 | 1.3124 | 0
7016 | 1.6693 | 0
7017 | 0.12485 | 0
7018 | 0.12485 | 0
7019 | 0.12485 | 0
7020 | 0.87551 | 0
7021 | 0.12485 | 0
7022 | 0.12485 | 0
7023 | 0.12485 | 0
7024 | 0.12485 | 0
7025 | 0.12485 | 0
7026 | 5.5017 | 6.976
7027 | 10.649 | 13.2369
7028 | 0.12485 | 0
7029 | 1.2938 | 0
7030 | 0.12485 | 0
7031 | 0.12485 | 0
7032 | 0.12485 | 0
7033 | 0.12485 | 0
7034 | 0.12485 | 0
7035 | 0.12485 | 0
7036 | 0.12485 | 0
7037 | 0.12485 | 0
7038 | 10.6958 | 13.2999
7039 | 1.3013 | 0
7040 | 1.6549 | 0
7041 | 0.12485 | 0
7042 | 0.12485 | 0
7043 | 0.12485 | 0
7044 | 0.86854 | 0
7045 | 0.12485 | 0
7046 | 0.12485 | 0
7047 | 0.12485 | 0
7048 | 0.12485 | 0
7049 | 0.12485 | 0
7050 | 5.6642 | 6.8237
7051 | 11.1163 | 13.1048
7052 | 0.12485 | 0
7053 | 1.2662 | 0
7054 | 0.12485 | 0
7055 | 0.12485 | 0
7056 | 0.12485 | 0
7057 | 0.12485 | 0
7058 | 0.12485 | 0
7059 | 0.12485 | 0
7060 | 0.12485 | 0
7061 | 0.12485 | 0
7062 | 11.0772 | 13.2945
7063 | 1.2675 | 0
7064 | 1.611 | 0
7065 | 0.12485 | 0
7066 | 0.12485 | 0
7067 | 0.12485 | 0
7068 | 0.84729 | 0
7069 | 0.12485 | 0
7070 | 0.12485 | 0
7071 | 0.12485 | 0
7072 | 0.12485 | 6.3676
7073 | 0.12485 | 0
7074 | 5.7742 | 0
7075 | 10.7637 | 13.6742
7076 | 0.12485 | 0
7077 | 1.2418 | 0
7078 | 0.12485 | 0
7079 | 0.12485 | 0
7080 | 0.12485 | 0
7081 | 0.12485 | 0
7082 | 0.12485 | 0
7083 | 0.12485 | 0
7084 | 0.12485 | 0
7085 | 0.12485 | 0
7086 | 10.8733 | 13.5418
7087 | 1.2529 | 0
7088 | 1.5921 | 0
7089 | 0.12485 | 0
7090 | 0.12485 | 0
7091 | 0.12485 | 0
7092 | 0.83812 | 6.4642
7093 | 0.12485 | 0
7094 | 0.12485 | 0
7095 | 0.12485 | 0
7096 | 0.12485 | 0
7097 | 0.12485 | 0
7098 | 5.7127 | 6.4654
7099 | 11.1441 | 12.5443
7100 | 0.12485 | 0
7101 | 1.3252 | 0
7102 | 0.12485 | 0
7103 | 0.12485 | 0
7104 | 0.12485 | 0
7105 | 0.12485 | 0
7106 | 0.12485 | 0
7107 | 0.12485 | 0
7108 | 0.12485 | 0
7109 | 0.12485 | 0
7110 | 10.9724 | 12.9826
7111 | 1.3202 | 0
7112 | 1.6795 | 0
7113 | 0.12485 | 0
7114 | 0.12485 | 0
7115 | 0.12485 | 0
7116 | 0.88051 | 0
7117 | 0.12485 | 0
7118 | 0.12485 | 0
7119 | 0.12485 | 0
7120 | 0.12485 | 0
7121 | 0.12485 | 0
7122 | 5.5376 | 6.9858
7123 | 11.1121 | 13.3805
7124 | 0.12485 | 0
7125 | 1.2945 | 0
7126 | 0.12485 | 0
7127 | 0.12485 | 0
7128 | 0.12485 | 0
7129 | 0.12485 | 0
7130 | 0.12485 | 0
7131 | 0.12485 | 0
7132 | 0.12485 | 0
7133 | 0.12485 | 0
7134 | 11.1131 | 13.5398
7135 | 1.2988 | 0
7136 | 1.6517 | 0
7137 | 0.12485 | 0
7138 | 0.12485 | 0
7139 | 0.12485 | 0
7140 | 0.86707 | 0
7141 | 0.12485 | 0
7142 | 0.12485 | 0
7143 | 0.12485 | 0
7144 | 0.12485 | 0
7145 | 0.12485 | 0
7146 | 5.6565 | 6.8618
7147 | 11.1128 | 13.2972
7148 | 0.12485 | 0
7149 | 1.2689 | 0
7150 | 0.12485 | 0
7151 | 0.12485 | 0
7152 | 0.12485 | 0
7153 | 0.12485 | 0
7154 | 0.12485 | 0
7155 | 0.12485 | 0
7156 | 0.12485 | 0
7157 | 0.12485 | 0
7158 | 11.1098 | 13.4423
7159 | 1.2726 | 0
7160 | 1.6177 | 0
7161 | 0.12485 | 0
7162 | 0.12485 | 0
7163 | 0.12485 | 0
7164 | 0.8506 | 0
7165 | 0.12485 | 0
7166 | 0.12485 | 6.3662
7167 | 0.12485 | 0
7168 | 0.12485 | 0
7169 | 0.12485 | 0
7170 | 5.7948 | 0
7171 | 10.8025 | 13.7076
7172 | 0.12485 | 0
7173 | 1.2456 | 0
7174 | 0.12485 | 0
7175 | 0.12485 | 0
7176 | 0.12485 | 0
7177 | 0.12485 | 0
7178 | 0.12485 | 0
7179 | 0.12485 | 0
7180 | 0.12485 | 0
7181 | 0.12485 | 0
7182 | 10.9098 | 13.5447
7183 | 1.2562 | 0
7184 | 1.5964 | 0
7185 | 0.12485 | 0
7186 | 0.12485 | 0
7187 | 0.12485 | 0
7188 | 0.8403 | 6.5878
7189 | 0.12485 | 0
7190 | 0.12485 | 0
7191 | 0.12485 | 0
7192 | 0.12485 | 0
7193 | 0.12485 | 0
7194 | 5.7399 | 6.565
7195 | 11.2092 | 12.6306
7196 | 0.12485 | 0
7197 | 1.3326 | 0
7198 | 0.12485 | 0
7199 | 0.12485 | 0
7200 | 0.12485 | 0
7201 | 0.12485 | 0
7202 | 0.12485 | 0
7203 | 0.12485 | 0
7204 | 0.12485 | 0
7205 | 0.12485 | 0
7206 | 11.0411 | 13.0643
7207 | 1.3279 | 0
7208 | 1.6895 | 0
7209 | 0.12485 | 0
7210 | 0.12485 | 0
7211 | 0.12485 | 0
7212 | 0.88545 | 0
7213 | 0.12485 | 0
7214 | 0.12485 | 0
7215 | 0.12485 | 0
7216 | 0.12485 | 0
7217 | 0.12485 | 0
7218 | 5.5731 | 6.9963
7219 | 11.1754 | 13.4369
7220 | 0.12485 | 0
7221 | 1.3013 | 0
7222 | 0.12485 | 0
7223 | 0.12485 | 0
7224 | 0.12485 | 0
7225 | 0.12485 | 0
7226 | 0.12485 | 0
7227 | 0.12485 | 0
7228 | 0.12485 | 0
7229 | 0.12485 | 0
7230 | 11.1759 | 13.5778
7231 | 1.3051 | 0
7232 | 1.6599 | 0
7233 | 0.12485 | 0
7234 | 0.12485 | 0
7235 | 0.12485 | 0
7236 | 0.87112 | 0
7237 | 0.12485 | 0
7238 | 0.12485 | 0
7239 | 0.12485 | 0
7240 | 0.12485 | 0
7241 | 0.12485 | 0
7242 | 5.6859 | 6.8693
7243 | 11.1681 | 13.3987
7244 | 0.12485 | 0
7245 | 1.2754 | 0
7246 | 0.12485 | 0
7247 | 0.12485 | 0
7248 | 0.12485 | 0
7249 | 0.12485 | 0
7250 | 0.12485 | 0
7251 | 0.12485 | 0
7252 | 0.12485 | 0
7253 | 0.12485 | 0
7254 | 11.1738 | 13.537
7255 | 1.2798 | 0
7256 | 1.627 | 0
7257 | 0.12485 | 0
7258 | 0.12485 | 0
7259 | 0.12485 | 0
7260 | 0.8552 | 6.3704
7261 | 0.12485 | 0
7262 | 0.12485 | 0
7263 | 0.12485 | 0
7264 | 0.12485 | 0
7265 | 0.12485 | 0
7266 | 5.826 | 6.4026
7267 | 11.3291 | 12.5794
7268 | 0.12485 | 0
7269 | 1.3424 | 0
7270 | 0.12485 | 0
7271 | 0.12485 | 0
7272 | 0.12485 | 0
7273 | 0.12485 | 0
7274 | 0.12485 | 0
7275 | 0.12485 | 0
7276 | 0.12485 | 0
7277 | 0.12485 | 0
7278 | 11.1293 | 13.0673
7279 | 1.3359 | 0
7280 | 1.6999 | 0
7281 | 0.12485 | 0
7282 | 0.12485 | 0
7283 | 0.12485 | 0
7284 | 0.89054 | 0
7285 | 0.12485 | 0
7286 | 0.12485 | 0
7287 | 0.12485 | 0
7288 | 0.12485 | 0
7289 | 0.12485 | 0
7290 | 5.6093 | 7.001
7291 | 11.2391 | 13.4433
7292 | 0.12485 | 0
7293 | 1.3071 | 0
7294 | 0.12485 | 0
7295 | 0.12485 | 0
7296 | 0.12485 | 0
7297 | 0.12485 | 0
7298 | 0.12485 | 0
7299 | 0.12485 | 0
7300 | 0.12485 | 0
7301 | 0.12485 | 0
7302 | 11.4293 | 13.0835
7303 | 1.2966 | 0
7304 | 1.6489 | 0
7305 | 0.12485 | 0
7306 | 0.12485 | 0
7307 | 0.12485 | 0
7308 | 0.86584 | 0
7309 | 0.12485 | 0
7310 | 0.12485 | 0
7311 | 0.12485 | 0
7312 | 0.12485 | 0
7313 | 0.12485 | 6.3692
7314 | 5.907 | 0
7315 | 10.9948 | 13.6967
7316 | 0.12485 | 0
7317 | 1.2628 | 0
7318 | 0.12485 | 0
7319 | 0.12485 | 0
7320 | 0.12485 | 0
7321 | 0.12485 | 0
7322 | 0.12485 | 0
7323 | 0.12485 | 0
7324 | 0.12485 | 0
7325 | 0.12485 | 0
7326 | 11.0663 | 13.5614
7327 | 1.2705 | 0
7328 | 1.615 | 0
7329 | 0.12485 | 0
7330 | 0.12485 | 0
7331 | 0.12485 | 6.3383
7332 | 0.93096 | 0
7333 | 0.12485 | 0
7334 | 0.12485 | 0
7335 | 0.12485 | 0
7336 | 0.12485 | 0
7337 | 0.12485 | 0
7338 | 5.774 | 6.747
7339 | 11.3011 | 12.7775
7340 | 0.12485 | 0
7341 | 1.3437 | 0
7342 | 0.12485 | 0
7343 | 0.12485 | 0
7344 | 0.12485 | 0
7345 | 0.12485 | 0
7346 | 0.12485 | 0
7347 | 0.12485 | 0
7348 | 0.12485 | 0
7349 | 0.12485 | 0
7350 | 11.1425 | 13.1972
7351 | 1.3395 | 0
7352 | 1.7046 | 0
7353 | 0.12485 | 0
7354 | 0.12485 | 0
7355 | 0.12485 | 0
7356 | 0.89289 | 0
7357 | 0.12485 | 0
7358 | 0.12485 | 0
7359 | 0.12485 | 0
7360 | 0.12485 | 0
7361 | 0.12485 | 0
7362 | 5.8365 | 6.8163
7363 | 11.4193 | 13.2335
7364 | 0.12485 | 0
7365 | 1.2953 | 0
7366 | 0.12485 | 0
7367 | 0.12485 | 0
7368 | 0.12485 | 0
7369 | 0.12485 | 0
7370 | 0.12485 | 0
7371 | 0.12485 | 0
7372 | 0.12485 | 0
7373 | 0.12485 | 0
7374 | 11.3496 | 13.4834
7375 | 1.2948 | 0
7376 | 1.6465 | 0
7377 | 0.12485 | 0
7378 | 0.12485 | 0
7379 | 0.12485 | 0
7380 | 0.86477 | 0
7381 | 0.12485 | 6.3697
7382 | 0.12485 | 0
7383 | 0.12485 | 0
7384 | 0.12485 | 0
7385 | 0.12485 | 0
7386 | 5.8943 | 6.4112
7387 | 11.4491 | 12.6322
7388 | 0.12485 | 0
7389 | 1.3542 | 0
7390 | 0.12485 | 0
7391 | 0.12485 | 0
7392 | 0.12485 | 0
7393 | 0.12485 | 0
7394 | 0.12485 | 0
7395 | 0.12485 | 0
7396 | 0.12485 | 0
7397 | 0.12485 | 0
7398 | 11.2362 | 13.1431
7399 | 1.3469 | 0
7400 | 1.7142 | 0
7401 | 0.12485 | 0
7402 | 0.12485 | 0
7403 | 0.12485 | 0
7404 | 0.8976 | 0
7405 | 0.12485 | 0
7406 | 0.12485 | 0
7407 | 0.12485 | 0
7408 | 0.12485 | 0
7409 | 0.12485 | 0
7410 | 5.8687 | 6.7927
7411 | 11.4734 | 13.2435
7412 | 0.12485 | 0
7413 | 1.3003 | 0
7414 | 0.12485 | 0
7415 | 0.12485 | 0
7416 | 0.12485 | 0
7417 | 0.12485 | 0
7418 | 0.12485 | 0
7419 | 0.12485 | 0
7420 | 0.12485 | 0
7421 | 0.12485 | 0
7422 | 11.3958 | 13.5078
7423 | 1.2993 | 0
7424 | 1.6524 | 0
7425 | 0.12485 | 0
7426 | 0.12485 | 0
7427 | 0.12485 | 0
7428 | 0.86766 | 6.3693
7429 | 0.12485 | 0
7430 | 0.12485 | 0
7431 | 0.12485 | 0
7432 | 0.12485 | 0
7433 | 0.12485 | 0
7434 | 5.9142 | 6.443
7435 | 11.4893 | 12.6674
7436 | 0.12485 | 0
7437 | 1.3585 | 0
7438 | 0.12485 | 0
7439 | 0.12485 | 0
7440 | 0.12485 | 0
7441 | 0.12485 | 0
7442 | 0.12485 | 0
7443 | 0.12485 | 0
7444 | 0.12485 | 0
7445 | 0.12485 | 0
7446 | 11.2753 | 13.1808
7447 | 1.3511 | 0
7448 | 1.7197 | 0
7449 | 0.12485 | 0
7450 | 0.12485 | 0
7451 | 0.12485 | 0
7452 | 0.9003 | 0
7453 | 0.12485 | 0
7454 | 0.12485 | 0
7455 | 0.12485 | 0
7456 | 0.12485 | 0
7457 | 0.12485 | 0
7458 | 5.8894 | 6.8238
7459 | 11.5134 | 13.2793
7460 | 0.12485 | 0
7461 | 1.3044 | 0
7462 | 0.12485 | 0
7463 | 0.12485 | 0
7464 | 0.12485 | 0
7465 | 0.12485 | 0
7466 | 0.12485 | 0
7467 | 0.12485 | 0
7468 | 0.12485 | 0
7469 | 0.12485 | 0
7470 | 11.4349 | 13.5461
7471 | 1.3034 | 0
7472 | 1.6577 | 0
7473 | 0.12485 | 0
7474 | 0.12485 | 0
7475 | 0.12485 | 0
7476 | 0.87028 | 6.3773
7477 | 0.12485 | 0
7478 | 0.12485 | 0
7479 | 0.12485 | 0
7480 | 0.12485 | 0
7481 | 0.12485 | 0
7482 | 5.9329 | 6.4795
7483 | 11.5284 | 12.7051
7484 | 0.12485 | 0
7485 | 1.3627 | 0
7486 | 0.12485 | 0
7487 | 0.12485 | 0
7488 | 0.12485 | 0
7489 | 0.12485 | 0
7490 | 0.12485 | 0
7491 | 0.12485 | 0
7492 | 0.12485 | 0
7493 | 0.12485 | 0
7494 | 11.3137 | 13.2199
7495 | 1.3553 | 0
7496 | 1.7252 | 0
7497 | 0.12485 | 0
7498 | 0.12485 | 0
7499 | 0.12485 | 0
7500 | 0.90298 | 0
7501 | 0.12485 | 0
7502 | 0.12485 | 0
7503 | 0.12485 | 0
7504 | 0.12485 | 0
7505 | 0.12485 | 0
7506 | 5.9102 | 6.8557
7507 | 11.5535 | 13.3155
7508 | 0.12485 | 0
7509 | 1.3086 | 0
7510 | 0.12485 | 0
7511 | 0.12485 | 0
7512 | 0.12485 | 0
7513 | 0.12485 | 0
7514 | 0.12485 | 0
7515 | 0.12485 | 0
7516 | 0.12485 | 0
7517 | 0.12485 | 0
7518 | 11.4741 | 13.5846
7519 | 1.3074 | 0
7520 | 1.6631 | 0
7521 | 0.12485 | 0
7522 | 0.12485 | 0
7523 | 0.12485 | 0
7524 | 0.8729 | 6.4077
7525 | 0.12485 | 0
7526 | 0.12485 | 0
7527 | 0.12485 | 0
7528 | 0.12485 | 0
7529 | 0.12485 | 0
7530 | 5.9544 | 6.5064
7531 | 11.5706 | 12.7381
7532 | 0.12485 | 0
7533 | 1.3671 | 0
7534 | 0.12485 | 0
7535 | 0.12485 | 0
7536 | 0.12485 | 0
7537 | 0.12485 | 0
7538 | 0.12485 | 0
7539 | 0.12485 | 0
7540 | 0.12485 | 0
7541 | 0.12485 | 0
7542 | 11.3538 | 13.2566
7543 | 1.3595 | 0
7544 | 1.7308 | 0
7545 | 0.12485 | 0
7546 | 0.12485 | 0
7547 | 0.12485 | 0
7548 | 0.90573 | 0
7549 | 0.12485 | 0
7550 | 0.12485 | 0
7551 | 0.12485 | 0
7552 | 0.12485 | 0
7553 | 0.12485 | 0
7554 | 5.93 | 6.8614
7555 | 11.5899 | 13.3566
7556 | 0.12485 | 0
7557 | 1.3125 | 0
7558 | 0.12485 | 0
7559 | 0.12485 | 0
7560 | 0.12485 | 0
7561 | 0.12485 | 0
7562 | 0.12485 | 0
7563 | 0.12485 | 0
7564 | 0.12485 | 0
7565 | 0.12485 | 0
7566 | 11.5103 | 13.5957
7567 | 1.3108 | 0
7568 | 1.6675 | 0
7569 | 0.12485 | 0
7570 | 0.12485 | 0
7571 | 0.12485 | 0
7572 | 0.87509 | 6.4494
7573 | 0.12485 | 0
7574 | 0.12485 | 0
7575 | 0.12485 | 0
7576 | 0.12485 | 0
7577 | 0.12485 | 0
7578 | 5.9739 | 6.541
7579 | 11.6105 | 12.7749
7580 | 0.12485 | 0
7581 | 1.3714 | 0
7582 | 0.12485 | 0
7583 | 0.12485 | 0
7584 | 0.12485 | 0
7585 | 0.12485 | 0
7586 | 0.12485 | 0
7587 | 0.12485 | 0
7588 | 0.12485 | 0
7589 | 0.12485 | 0
7590 | 11.3928 | 13.2954
7591 | 1.3638 | 0
7592 | 1.7363 | 0
7593 | 0.12485 | 0
7594 | 0.12485 | 0
7595 | 0.12485 | 0
7596 | 0.90844 | 0
7597 | 0.12485 | 0
7598 | 0.12485 | 0
7599 | 0.12485 | 0
7600 | 0.12485 | 0
7601 | 0.12485 | 0
7602 | 5.9496 | 6.8662
7603 | 11.6258 | 13.3988
7604 | 0.12485 | 0
7605 | 1.3163 | 0
7606 | 0.12485 | 0
7607 | 0.12485 | 0
7608 | 0.12485 | 0
7609 | 0.12485 | 0
7610 | 0.12485 | 0
7611 | 0.12485 | 0
7612 | 0.12485 | 0
7613 | 0.12485 | 0
7614 | 11.546 | 13.6024
7615 | 1.3141 | 0
7616 | 1.6718 | 0
7617 | 0.12485 | 0
7618 | 0.12485 | 0
7619 | 0.12485 | 0
7620 | 0.8772 | 6.4908
7621 | 0.12485 | 0
7622 | 0.12485 | 0
7623 | 0.12485 | 0
7624 | 0.12485 | 0
7625 | 0.12485 | 0
7626 | 5.9928 | 6.5777
7627 | 11.65 | 12.8128
7628 | 0.12485 | 0
7629 | 1.3756 | 0
7630 | 0.12485 | 0
7631 | 0.12485 | 0
7632 | 0.12485 | 0
7633 | 0.12485 | 0
7634 | 0.12485 | 0
7635 | 0.12485 | 0
7636 | 0.12485 | 0
7637 | 0.12485 | 0
7638 | 11.4316 | 13.3347
7639 | 1.368 | 0
7640 | 1.7418 | 0
7641 | 0.12485 | 0
7642 | 0.12485 | 0
7643 | 0.12485 | 0
7644 | 0.91114 | 0
7645 | 0.12485 | 0
7646 | 0.12485 | 0
7647 | 0.12485 | 0
7648 | 0.12485 | 0
7649 | 0.12485 | 0
7650 | 5.9691 | 6.8709
7651 | 11.6616 | 13.4412
7652 | 0.12485 | 0
7653 | 1.3202 | 0
7654 | 0.12485 | 0
7655 | 0.12485 | 0
7656 | 0.12485 | 0
7657 | 0.12485 | 0
7658 | 0.12485 | 0
7659 | 0.12485 | 0
7660 | 0.12485 | 0
7661 | 0.12485 | 0
7662 | 11.5816 | 13.609
7663 | 1.3174 | 0
7664 | 1.676 | 0
7665 | 0.12485 | 0
7666 | 0.12485 | 0
7667 | 0.12485 | 0
7668 | 0.87931 | 6.5324
7669 | 0.12485 | 0
7670 | 0.12485 | 0
7671 | 0.12485 | 0
7672 | 0.12485 | 0
7673 | 0.12485 | 0
7674 | 6.0117 | 6.6145
7675 | 11.6894 | 12.8508
7676 | 0.12485 | 0
7677 | 1.3799 | 0
7678 | 0.12485 | 0
7679 | 0.12485 | 0
7680 | 0.12485 | 0
7681 | 0.12485 | 0
7682 | 0.12485 | 0
7683 | 0.12485 | 0
7684 | 0.12485 | 0
7685 | 0.12485 | 0
7686 | 11.4703 | 13.374
7687 | 1.3722 | 0
7688 | 1.7473 | 0
7689 | 0.12485 | 0
7690 | 0.12485 | 0
7691 | 0.12485 | 0
7692 | 0.91384 | 0
7693 | 0.12485 | 0
7694 | 0.12485 | 0
7695 | 0.12485 | 0
7696 | 0.12485 | 0
7697 | 0.12485 | 0
7698 | 5.9886 | 6.8757
7699 | 11.6973 | 13.4836
7700 | 0.12485 | 0
7701 | 1.324 | 0
7702 | 0.12485 | 0
7703 | 0.12485 | 0
7704 | 0.12485 | 0
7705 | 0.12485 | 0
7706 | 0.12485 | 0
7707 | 0.12485 | 0
7708 | 0.12485 | 0
7709 | 0.12485 | 0
7710 | 11.6172 | 13.6157
7711 | 1.3206 | 0
7712 | 1.6803 | 0
7713 | 0.12485 | 0
7714 | 0.12485 | 0
7715 | 0.12485 | 0
7716 | 0.88142 | 6.574
7717 | 0.12485 | 0
7718 | 0.12485 | 0
7719 | 0.12485 | 0
7720 | 0.12485 | 0
7721 | 0.12485 | 0
7722 | 6.0306 | 6.6512
7723 | 11.7288 | 12.8887
7724 | 0.12485 | 0
7725 | 1.3841 | 0
7726 | 0.12485 | 0
7727 | 0.12485 | 0
7728 | 0.12485 | 0
7729 | 0.12485 | 0
7730 | 0.12485 | 0
7731 | 0.12485 | 0
7732 | 0.12485 | 0
7733 | 0.12485 | 0
7734 | 11.5089 | 13.4132
7735 | 1.3764 | 0
7736 | 1.7527 | 0
7737 | 0.12485 | 0
7738 | 0.12485 | 0
7739 | 0.12485 | 0
7740 | 0.91654 | 0
7741 | 0.12485 | 0
7742 | 0.12485 | 0
7743 | 0.12485 | 0
7744 | 0.12485 | 0
7745 | 0.12485 | 0
7746 | 6.0081 | 6.8804
7747 | 11.7325 | 13.5111
7748 | 0.12485 | 0
7749 | 1.3276 | 0
7750 | 0.12485 | 0
7751 | 0.12485 | 0
7752 | 0.12485 | 0
7753 | 0.12485 | 0
7754 | 0.12485 | 0
7755 | 0.12485 | 0
7756 | 0.12485 | 0
7757 | 0.12485 | 0
7758 | 11.6504 | 13.6231
7759 | 1.3237 | 0
7760 | 1.6843 | 0
7761 | 0.12485 | 0
7762 | 0.12485 | 0
7763 | 0.12485 | 0
7764 | 0.88339 | 6.6187
7765 | 0.12485 | 0
7766 | 0.12485 | 0
7767 | 0.12485 | 0
7768 | 0.12485 | 0
7769 | 0.12485 | 0
7770 | 6.0489 | 6.6901
7771 | 11.7674 | 12.9276
7772 | 0.12485 | 0
7773 | 1.3883 | 0
7774 | 0.12485 | 0
7775 | 0.12485 | 0
7776 | 0.12485 | 0
7777 | 0.12485 | 0
7778 | 0.12485 | 0
7779 | 0.12485 | 0
7780 | 0.12485 | 0
7781 | 0.12485 | 0
7782 | 11.5471 | 13.4529
7783 | 1.3806 | 0
7784 | 1.7582 | 0
7785 | 0.12485 | 0
7786 | 0.12485 | 0
7787 | 0.12485 | 0
7788 | 0.91921 | 0
7789 | 0.12485 | 0
7790 | 0.12485 | 0
7791 | 0.12485 | 0
7792 | 0.12485 | 0
7793 | 0.12485 | 0
7794 | 6.0274 | 6.8852
7795 | 11.7666 | 13.5144
7796 | 0.12485 | 0
7797 | 1.3307 | 0
7798 | 0.12485 | 0
7799 | 0.12485 | 0
7800 | 0.12485 | 0
7801 | 0.12485 | 0
7802 | 0.12485 | 0
7803 | 0.12485 | 0
7804 | 0.12485 | 0
7805 | 0.12485 | 0
7806 | 11.6791 | 13.6269
7807 | 1.3263 | 0
7808 | 1.6877 | 0
7809 | 0.12485 | 0
7810 | 0.12485 | 0
7811 | 0.12485 | 6.3418
7812 | 0.96659 | 0
7813 | 0.12485 | 0
7814 | 0.12485 | 0
7815 | 0.12485 | 0
7816 | 0.12485 | 0
7817 | 0.12485 | 0
7818 | 6.0271 | 6.8421
7819 | 11.757 | 13.0443
7820 | 0.12485 | 0
7821 | 1.3896 | 0
7822 | 0.12485 | 0
7823 | 0.12485 | 0
7824 | 0.12485 | 0
7825 | 0.12485 | 0
7826 | 0.12485 | 0
7827 | 0.12485 | 0
7828 | 0.12485 | 0
7829 | 0.12485 | 0
7830 | 11.5598 | 13.5347
7831 | 1.3832 | 0
7832 | 1.7617 | 0
7833 | 0.12485 | 0
7834 | 0.12485 | 0
7835 | 0.12485 | 0
7836 | 0.92094 | 0
7837 | 0.12485 | 0
7838 | 0.12485 | 0
7839 | 0.12485 | 0
7840 | 0.12485 | 0
7841 | 0.12485 | 0
7842 | 6.0403 | 6.8925
7843 | 11.7897 | 13.5164
7844 | 0.12485 | 0
7845 | 1.3328 | 0
7846 | 0.12485 | 0
7847 | 0.12485 | 0
7848 | 0.12485 | 0
7849 | 0.12485 | 0
7850 | 0.12485 | 0
7851 | 0.12485 | 0
7852 | 0.12485 | 0
7853 | 0.12485 | 0
7854 | 11.6988 | 13.6299
7855 | 1.3281 | 0
7856 | 1.6901 | 0
7857 | 0.12485 | 6.3392
7858 | 0.12485 | 0
7859 | 0.12485 | 0
7860 | 0.96745 | 0
7861 | 0.12485 | 0
7862 | 0.12485 | 0
7863 | 0.12485 | 0
7864 | 0.12485 | 0
7865 | 0.12485 | 0
7866 | 6.0335 | 6.8617
7867 | 11.7718 | 13.1165
7868 | 0.12485 | 0
7869 | 1.3923 | 0
7870 | 0.12485 | 0
7871 | 0.12485 | 0
7872 | 0.12485 | 0
7873 | 0.12485 | 0
7874 | 0.12485 | 0
7875 | 0.12485 | 0
7876 | 0.12485 | 0
7877 | 0.12485 | 0
7878 | 11.9931 | 13.6308
7879 | 1.3794 | 0
7880 | 1.7567 | 0
7881 | 0.12485 | 0
7882 | 0.12485 | 0
7883 | 0.12485 | 0
7884 | 0.91857 | 0
7885 | 0.12485 | 0
7886 | 0.12485 | 0
7887 | 0.12485 | 0
7888 | 0.12485 | 0
7889 | 0.12485 | 0
7890 | 6.0246 | 6.9051
7891 | 11.7636 | 13.512
7892 | 0.12485 | 0
7893 | 1.3304 | 0
7894 | 0.12485 | 0
7895 | 0.12485 | 0
7896 | 0.12485 | 0
7897 | 0.12485 | 0
7898 | 0.12485 | 0
7899 | 0.12485 | 0
7900 | 0.12485 | 0
7901 | 0.12485 | 0
7902 | 11.6787 | 13.6268
7903 | 1.3263 | 0
7904 | 1.6877 | 6.3963
7905 | 0.12485 | 0
7906 | 0.12485 | 0
7907 | 0.12485 | 0
7908 | 0.96677 | 0
7909 | 0.12485 | 0
7910 | 0.12485 | 0
7911 | 0.12485 | 0
7912 | 0.12485 | 0
7913 | 0.12485 | 0
7914 | 6.0292 | 6.8852
7915 | 11.7685 | 13.2149
7916 | 0.12485 | 0
7917 | 1.3939 | 0
7918 | 0.12485 | 0
7919 | 0.12485 | 0
7920 | 0.12485 | 0
7921 | 0.12485 | 0
7922 | 0.12485 | 0
7923 | 0.12485 | 0
7924 | 0.12485 | 0
7925 | 0.12485 | 0
7926 | 12.009 | 13.64
7927 | 1.3809 | 0
7928 | 1.7587 | 0
7929 | 0.12485 | 0
7930 | 0.12485 | 0
7931 | 0.12485 | 0
7932 | 0.91958 | 0
7933 | 0.12485 | 0
7934 | 0.12485 | 0
7935 | 0.12485 | 0
7936 | 0.12485 | 0
7937 | 0.12485 | 0
7938 | 6.0321 | 6.9058
7939 | 11.7767 | 13.5133
7940 | 0.12485 | 0
7941 | 1.3316 | 0
7942 | 0.12485 | 0
7943 | 0.12485 | 0
7944 | 0.12485 | 0
7945 | 0.12485 | 0
7946 | 0.12485 | 0
7947 | 0.12485 | 0
7948 | 0.12485 | 0
7949 | 0.12485 | 0
7950 | 11.6903 | 18.9887
7951 | 1.4306 | 0
7952 | 1.8233 | 0
7953 | 0.12485 | 0
7954 | 0.12485 | 0
7955 | 0.12485 | 0
7956 | 0.95094 | 0
7957 | 0.12485 | 0
7958 | 0.12485 | 0
7959 | 0.12485 | 0
7960 | 0.12485 | 0
7961 | 0.12485 | 0
7962 | 6.0371 | 7.0195
7963 | 12.1884 | 13.0651
7964 | 0.12485 | 0
7965 | 1.3627 | 0
7966 | 0.12485 | 0
7967 | 0.12485 | 0
7968 | 0.12485 | 0
7969 | 0.12485 | 0
7970 | 0.12485 | 0
7971 | 0.12485 | 0
7972 | 0.12485 | 0
7973 | 0.12485 | 0
7974 | 11.9628 | 13.6319
7975 | 1.3519 | 0
7976 | 1.7211 | 0
7977 | 0.12485 | 0
7978 | 0.12485 | 0
7979 | 0.12485 | 0
7980 | 0.90141 | 6.5817
7981 | 0.12485 | 0
7982 | 0.12485 | 0
7983 | 0.12485 | 0
7984 | 0.12485 | 0
7985 | 0.12485 | 0
7986 | 6.1733 | 6.7042
7987 | 11.9858 | 13.0226
7988 | 0.12485 | 0
7989 | 1.4097 | 0
7990 | 0.12485 | 0
7991 | 0.12485 | 0
7992 | 0.12485 | 0
7993 | 0.12485 | 0
7994 | 0.12485 | 0
7995 | 0.12485 | 0
7996 | 0.12485 | 0
7997 | 0.12485 | 0
7998 | 11.74 | 13.5896
7999 | 1.4004 | 0
8000 | 1.7841 | 0
8001 | 0.12485 | 0
8002 | 0.12485 | 0
8003 | 0.12485 | 0
8004 | 0.93195 | 0
8005 | 0.12485 | 0
8006 | 0.12485 | 0
8007 | 0.12485 | 0
8008 | 0.12485 | 0
8009 | 0.12485 | 0
8010 | 6.1191 | 6.9041
8011 | 11.9282 | 13.5305
8012 | 0.12485 | 0
8013 | 1.3454 | 0
8014 | 0.12485 | 0
8015 | 0.12485 | 0
8016 | 0.12485 | 0
8017 | 0.12485 | 0
8018 | 0.12485 | 0
8019 | 0.12485 | 0
8020 | 0.12485 | 0
8021 | 0.12485 | 0
8022 | 11.8137 | 13.6412
8023 | 1.3385 | 0
8024 | 1.7038 | 6.4244
8025 | 0.12485 | 0
8026 | 0.12485 | 0
8027 | 0.12485 | 0
8028 | 0.975 | 0
8029 | 0.12485 | 0
8030 | 0.12485 | 0
8031 | 0.12485 | 0
8032 | 0.12485 | 0
8033 | 0.12485 | 0
8034 | 6.2018 | 6.7989
8035 | 11.838 | 13.4081
8036 | 0.12485 | 0
8037 | 1.4035 | 0
8038 | 0.12485 | 0
8039 | 0.12485 | 0
8040 | 0.12485 | 0
8041 | 0.12485 | 0
8042 | 0.12485 | 0
8043 | 0.12485 | 0
8044 | 0.12485 | 0
8045 | 0.12485 | 0
8046 | 12.2985 | 13.1831
8047 | 1.3761 | 0
8048 | 1.7525 | 0
8049 | 0.12485 | 0
8050 | 0.12485 | 0
8051 | 0.12485 | 0
8052 | 0.91668 | 0
8053 | 0.12485 | 6.3647
8054 | 0.12485 | 0
8055 | 0.12485 | 0
8056 | 0.12485 | 0
8057 | 0.12485 | 0
8058 | 6.263 | 6.5295
8059 | 12.1097 | 12.9655
8060 | 0.12485 | 0
8061 | 1.4197 | 0
8062 | 0.12485 | 0
8063 | 0.12485 | 0
8064 | 0.12485 | 0
8065 | 0.12485 | 0
8066 | 0.12485 | 0
8067 | 0.12485 | 0
8068 | 0.12485 | 0
8069 | 0.12485 | 0
8070 | 11.8295 | 13.5894
8071 | 1.4085 | 0
8072 | 1.7945 | 0
8073 | 0.12485 | 0
8074 | 0.12485 | 0
8075 | 0.12485 | 0
8076 | 0.93708 | 0
8077 | 0.12485 | 0
8078 | 0.12485 | 0
8079 | 0.12485 | 0
8080 | 0.12485 | 0
8081 | 0.12485 | 0
8082 | 6.1557 | 6.9076
8083 | 11.9923 | 13.5373
8084 | 0.12485 | 0
8085 | 1.3513 | 0
8086 | 0.12485 | 0
8087 | 0.12485 | 0
8088 | 0.12485 | 0
8089 | 0.12485 | 0
8090 | 0.12485 | 0
8091 | 0.12485 | 0
8092 | 0.12485 | 0
8093 | 0.12485 | 0
8094 | 11.8667 | 19.0027
8095 | 1.4466 | 0
8096 | 1.8441 | 0
8097 | 0.12485 | 0
8098 | 0.12485 | 0
8099 | 0.12485 | 0
8100 | 0.96115 | 0
8101 | 0.12485 | 0
8102 | 0.12485 | 0
8103 | 0.12485 | 0
8104 | 0.12485 | 0
8105 | 0.12485 | 0
8106 | 6.1098 | 7.0288
8107 | 12.3185 | 13.1412
8108 | 0.12485 | 0
8109 | 1.3755 | 0
8110 | 0.12485 | 0
8111 | 0.12485 | 0
8112 | 0.12485 | 0
8113 | 0.12485 | 0
8114 | 0.12485 | 0
8115 | 0.12485 | 0
8116 | 0.12485 | 0
8117 | 0.12485 | 0
8118 | 12.0794 | 13.6491
8119 | 1.3626 | 0
8120 | 1.735 | 0
8121 | 0.12485 | 0
8122 | 0.12485 | 0
8123 | 0.12485 | 6.3501
8124 | 0.98993 | 0
8125 | 0.12485 | 0
8126 | 0.12485 | 0
8127 | 0.12485 | 0
8128 | 0.12485 | 0
8129 | 0.12485 | 0
8130 | 6.1927 | 6.8573
8131 | 12.047 | 13.2092
8132 | 0.12485 | 0
8133 | 1.4187 | 0
8134 | 0.12485 | 0
8135 | 0.12485 | 0
8136 | 0.12485 | 0
8137 | 0.12485 | 0
8138 | 0.12485 | 0
8139 | 0.12485 | 0
8140 | 0.12485 | 0
8141 | 0.12485 | 0
8142 | 12.2319 | 13.6604
8143 | 1.4012 | 0
8144 | 1.7851 | 0
8145 | 0.12485 | 0
8146 | 0.12485 | 0
8147 | 0.12485 | 0
8148 | 0.93258 | 0
8149 | 0.12485 | 0
8150 | 0.12485 | 0
8151 | 0.12485 | 0
8152 | 0.12485 | 0
8153 | 0.12485 | 0
8154 | 6.1251 | 6.9152
8155 | 11.9399 | 18.8796
8156 | 0.12485 | 0
8157 | 1.4494 | 0
8158 | 0.12485 | 0
8159 | 0.12485 | 0
8160 | 0.12485 | 0
8161 | 0.12485 | 0
8162 | 0.12485 | 0
8163 | 0.12485 | 0
8164 | 0.12485 | 0
8165 | 0.12485 | 0
8166 | 12.0906 | 13.3495
8167 | 1.4274 | 0
8168 | 1.8192 | 0
8169 | 0.12485 | 0
8170 | 0.12485 | 0
8171 | 0.12485 | 0
8172 | 0.94909 | 0
8173 | 0.12485 | 0
8174 | 0.12485 | 0
8175 | 0.12485 | 0
8176 | 0.12485 | 0
8177 | 0.12485 | 0
8178 | 6.24 | 6.8979
8179 | 12.1383 | 13.5539
8180 | 0.12485 | 0
8181 | 1.3646 | 0
8182 | 0.12485 | 0
8183 | 0.12485 | 0
8184 | 0.12485 | 0
8185 | 0.12485 | 0
8186 | 0.12485 | 0
8187 | 0.12485 | 0
8188 | 0.12485 | 0
8189 | 0.12485 | 0
8190 | 11.986 | 19.0044
8191 | 1.4573 | 0
8192 | 1.858 | 0
8193 | 0.12485 | 0
8194 | 0.12485 | 0
8195 | 0.12485 | 0
8196 | 0.96796 | 0
8197 | 0.12485 | 0
8198 | 0.12485 | 0
8199 | 0.12485 | 0
8200 | 0.12485 | 0
8201 | 0.12485 | 0
8202 | 6.1582 | 7.0344
8203 | 12.4049 | 13.187
8204 | 0.12485 | 0
8205 | 1.384 | 0
8206 | 0.12485 | 0
8207 | 0.12485 | 0
8208 | 0.12485 | 0
8209 | 0.12485 | 0
8210 | 0.12485 | 0
8211 | 0.12485 | 0
8212 | 0.12485 | 0
8213 | 0.12485 | 0
8214 | 12.156 | 13.66
8215 | 1.3696 | 0
8216 | 1.7441 | 0
8217 | 0.12485 | 6.3438
8218 | 0.12485 | 0
8219 | 0.12485 | 0
8220 | 0.99406 | 0
8221 | 0.12485 | 0
8222 | 0.12485 | 0
8223 | 0.12485 | 0
8224 | 0.12485 | 0
8225 | 0.12485 | 0
8226 | 6.2223 | 6.8789
8227 | 12.1023 | 13.3025
8228 | 0.12485 | 0
8229 | 1.4255 | 0
8230 | 0.12485 | 0
8231 | 0.12485 | 0
8232 | 0.12485 | 0
8233 | 0.12485 | 0
8234 | 0.12485 | 0
8235 | 0.12485 | 0
8236 | 0.12485 | 0
8237 | 0.12485 | 0
8238 | 12.4964 | 13.2306
8239 | 1.3945 | 0
8240 | 1.7765 | 0
8241 | 0.12485 | 0
8242 | 0.12485 | 0
8243 | 0.12485 | 0
8244 | 0.92851 | 6.3689
8245 | 0.12485 | 0
8246 | 0.12485 | 0
8247 | 0.12485 | 0
8248 | 0.12485 | 0
8249 | 0.12485 | 0
8250 | 6.346 | 6.6205
8251 | 12.27 | 13.0843
8252 | 0.12485 | 0
8253 | 1.4363 | 0
8254 | 0.12485 | 0
8255 | 0.12485 | 0
8256 | 0.12485 | 0
8257 | 0.12485 | 0
8258 | 0.12485 | 0
8259 | 0.12485 | 0
8260 | 0.12485 | 0
8261 | 0.12485 | 0
8262 | 12.3882 | 13.6664
8263 | 1.4153 | 0
8264 | 1.8036 | 0
8265 | 0.12485 | 0
8266 | 0.12485 | 0
8267 | 0.12485 | 0
8268 | 0.94162 | 0
8269 | 0.12485 | 0
8270 | 0.12485 | 0
8271 | 0.12485 | 0
8272 | 0.12485 | 0
8273 | 0.12485 | 0
8274 | 6.1896 | 6.9223
8275 | 12.0528 | 18.9308
8276 | 0.12485 | 0
8277 | 1.4604 | 0
8278 | 0.12485 | 0
8279 | 0.12485 | 0
8280 | 0.12485 | 0
8281 | 0.12485 | 0
8282 | 0.12485 | 0
8283 | 0.12485 | 0
8284 | 0.12485 | 0
8285 | 0.12485 | 0
8286 | 12.1897 | 13.4199
8287 | 1.4376 | 0
8288 | 1.8325 | 0
8289 | 0.12485 | 0
8290 | 0.12485 | 0
8291 | 0.12485 | 0
8292 | 0.95564 | 0
8293 | 0.12485 | 0
8294 | 0.12485 | 0
8295 | 0.12485 | 0
8296 | 0.12485 | 0
8297 | 0.12485 | 0
8298 | 6.2871 | 6.9076
8299 | 12.2213 | 13.5622
8300 | 0.12485 | 0
8301 | 1.3721 | 0
8302 | 0.12485 | 0
8303 | 0.12485 | 0
8304 | 0.12485 | 0
8305 | 0.12485 | 0
8306 | 0.12485 | 0
8307 | 0.12485 | 0
8308 | 0.12485 | 0
8309 | 0.12485 | 0
8310 | 12.0546 | 19.1173
8311 | 1.4655 | 0
8312 | 1.8688 | 0
8313 | 0.12485 | 0
8314 | 0.12485 | 0
8315 | 0.12485 | 0
8316 | 0.97328 | 0
8317 | 0.12485 | 0
8318 | 0.12485 | 0
8319 | 0.12485 | 0
8320 | 0.12485 | 0
8321 | 0.12485 | 0
8322 | 6.1966 | 7.0483
8323 | 12.4772 | 13.2947
8324 | 0.12485 | 0
8325 | 1.3921 | 0
8326 | 0.12485 | 0
8327 | 0.12485 | 0
8328 | 0.12485 | 0
8329 | 0.12485 | 0
8330 | 0.12485 | 0
8331 | 0.12485 | 0
8332 | 0.12485 | 0
8333 | 0.12485 | 0
8334 | 12.2307 | 13.6755
8335 | 1.3764 | 0
8336 | 1.7531 | 6.3688
8337 | 0.12485 | 0
8338 | 0.12485 | 0
8339 | 0.12485 | 0
8340 | 0.99849 | 0
8341 | 0.12485 | 0
8342 | 0.12485 | 0
8343 | 0.12485 | 0
8344 | 0.12485 | 0
8345 | 0.12485 | 0
8346 | 6.3686 | 6.8143
8347 | 12.1296 | 13.5365
8348 | 0.12485 | 0
8349 | 1.4321 | 0
8350 | 0.12485 | 0
8351 | 0.12485 | 0
8352 | 0.12485 | 0
8353 | 0.12485 | 0
8354 | 0.12485 | 0
8355 | 0.12485 | 0
8356 | 0.12485 | 0
8357 | 0.12485 | 0
8358 | 12.5613 | 13.3569
8359 | 1.4022 | 0
8360 | 1.7866 | 0
8361 | 0.12485 | 0
8362 | 0.12485 | 0
8363 | 0.12485 | 0
8364 | 0.93347 | 6.4541
8365 | 0.12485 | 0
8366 | 0.12485 | 0
8367 | 0.12485 | 0
8368 | 0.12485 | 0
8369 | 0.12485 | 0
8370 | 6.389 | 6.6974
8371 | 12.3585 | 13.166
8372 | 0.12485 | 0
8373 | 1.4458 | 0
8374 | 0.12485 | 0
8375 | 0.12485 | 0
8376 | 0.12485 | 0
8377 | 0.12485 | 0
8378 | 0.12485 | 0
8379 | 0.12485 | 0
8380 | 0.12485 | 0
8381 | 0.12485 | 0
8382 | 12.6754 | 13.1926
8383 | 1.4101 | 0
8384 | 1.7968 | 0
8385 | 0.12485 | 0
8386 | 0.12485 | 0
8387 | 0.12485 | 0
8388 | 0.93841 | 6.3655
8389 | 0.12485 | 0
8390 | 0.12485 | 0
8391 | 0.12485 | 0
8392 | 0.12485 | 0
8393 | 0.12485 | 0
8394 | 6.416 | 6.6445
8395 | 12.3957 | 13.1486
8396 | 0.12485 | 0
8397 | 1.4488 | 0
8398 | 0.12485 | 0
8399 | 0.12485 | 0
8400 | 0.12485 | 0
8401 | 0.12485 | 0
8402 | 0.12485 | 0
8403 | 0.12485 | 0
8404 | 0.12485 | 0
8405 | 0.12485 | 0
8406 | 12.702 | 13.1907
8407 | 1.4124 | 0
8408 | 1.7998 | 0
8409 | 0.12485 | 0
8410 | 0.12485 | 0
8411 | 0.12485 | 0
8412 | 0.93992 | 6.3674
8413 | 0.12485 | 0
8414 | 0.12485 | 0
8415 | 0.12485 | 0
8416 | 0.12485 | 0
8417 | 0.12485 | 0
8418 | 6.4269 | 6.6498
8419 | 12.4155 | 13.1597
8420 | 0.12485 | 0
8421 | 1.4508 | 0
8422 | 0.12485 | 0
8423 | 0.12485 | 0
8424 | 0.12485 | 0
8425 | 0.12485 | 0
8426 | 0.12485 | 0
8427 | 0.12485 | 0
8428 | 0.12485 | 0
8429 | 0.12485 | 0
8430 | 12.7202 | 13.2037
8431 | 1.4142 | 0
8432 | 1.8022 | 0
8433 | 0.12485 | 0
8434 | 0.12485 | 0
8435 | 0.12485 | 0
8436 | 0.9411 | 6.371
8437 | 0.12485 | 0
8438 | 0.12485 | 0
8439 | 0.12485 | 0
8440 | 0.12485 | 0
8441 | 0.12485 | 0
8442 | 6.4354 | 6.6634
8443 | 12.4327 | 13.1747
8444 | 0.12485 | 0
8445 | 1.4526 | 0
8446 | 0.12485 | 0
8447 | 0.12485 | 0
8448 | 0.12485 | 0
8449 | 0.12485 | 0
8450 | 0.12485 | 0
8451 | 0.12485 | 0
8452 | 0.12485 | 0
8453 | 0.12485 | 0
8454 | 12.7371 | 13.2188
8455 | 1.416 | 0
8456 | 1.8045 | 0
8457 | 0.12485 | 0
8458 | 0.12485 | 0
8459 | 0.12485 | 0
8460 | 0.94221 | 6.3832
8461 | 0.12485 | 0
8462 | 0.12485 | 0
8463 | 0.12485 | 0
8464 | 0.12485 | 0
8465 | 0.12485 | 0
8466 | 6.4444 | 6.6743
8467 | 12.4504 | 13.1883
8468 | 0.12485 | 0
8469 | 1.4545 | 0
8470 | 0.12485 | 0
8471 | 0.12485 | 0
8472 | 0.12485 | 0
8473 | 0.12485 | 0
8474 | 0.12485 | 0
8475 | 0.12485 | 0
8476 | 0.12485 | 0
8477 | 0.12485 | 0
8478 | 12.7541 | 13.233
8479 | 1.4177 | 0
8480 | 1.8068 | 0
8481 | 0.12485 | 0
8482 | 0.12485 | 0
8483 | 0.12485 | 0
8484 | 0.94333 | 6.3948
8485 | 0.12485 | 0
8486 | 0.12485 | 0
8487 | 0.12485 | 0
8488 | 0.12485 | 0
8489 | 0.12485 | 0
8490 | 6.4535 | 6.6849
8491 | 12.4679 | 13.2017
8492 | 0.12485 | 0
8493 | 1.4563 | 0
8494 | 0.12485 | 0
8495 | 0.12485 | 0
8496 | 0.12485 | 0
8497 | 0.12485 | 0
8498 | 0.12485 | 0
8499 | 0.12485 | 0
8500 | 0.12485 | 0
8501 | 0.12485 | 0
8502 | 12.771 | 13.247
8503 | 1.4194 | 0
8504 | 1.809 | 0
8505 | 0.12485 | 0
8506 | 0.12485 | 0
8507 | 0.12485 | 0
8508 | 0.94443 | 6.4063
8509 | 0.12485 | 0
8510 | 0.12485 | 0
8511 | 0.12485 | 0
8512 | 0.12485 | 0
8513 | 0.12485 | 0
8514 | 6.4624 | 6.6953
8515 | 12.4853 | 13.2149
8516 | 0.12485 | 0
8517 | 1.4581 | 0
8518 | 0.12485 | 0
8519 | 0.12485 | 0
8520 | 0.12485 | 0
8521 | 0.12485 | 0
8522 | 0.12485 | 0
8523 | 0.12485 | 0
8524 | 0.12485 | 0
8525 | 0.12485 | 0
8526 | 12.7876 | 13.2609
8527 | 1.4211 | 0
8528 | 1.8112 | 0
8529 | 0.12485 | 0
8530 | 0.12485 | 0
8531 | 0.12485 | 0
8532 | 0.94552 | 6.4176
8533 | 0.12485 | 0
8534 | 0.12485 | 0
8535 | 0.12485 | 0
8536 | 0.12485 | 0
8537 | 0.12485 | 0
8538 | 6.4712 | 6.7056
8539 | 12.5025 | 13.2279
8540 | 0.12485 | 0
8541 | 1.4599 | 0
8542 | 0.12485 | 0
8543 | 0.12485 | 0
8544 | 0.12485 | 0
8545 | 0.12485 | 0
8546 | 0.12485 | 0
8547 | 0.12485 | 0
8548 | 0.12485 | 0
8549 | 0.12485 | 0
8550 | 12.804 | 13.2745
8551 | 1.4228 | 0
8552 | 1.8134 | 0
8553 | 0.12485 | 0
8554 | 0.12485 | 0
8555 | 0.12485 | 0
8556 | 0.9466 | 6.4288
8557 | 0.12485 | 0
8558 | 0.12485 | 0
8559 | 0.12485 | 0
8560 | 0.12485 | 0
8561 | 0.12485 | 0
8562 | 6.4799 | 6.7157
8563 | 12.5194 | 13.2408
8564 | 0.12485 | 0
8565 | 1.4617 | 0
8566 | 0.12485 | 0
8567 | 0.12485 | 0
8568 | 0.12485 | 0
8569 | 0.12485 | 0
8570 | 0.12485 | 0
8571 | 0.12485 | 0
8572 | 0.12485 | 0
8573 | 0.12485 | 0
8574 | 12.8202 | 13.288
8575 | 1.4245 | 0
8576 | 1.8156 | 0
8577 | 0.12485 | 0
8578 | 0.12485 | 0
8579 | 0.12485 | 0
8580 | 0.94766 | 6.4398
8581 | 0.12485 | 0
8582 | 0.12485 | 0
8583 | 0.12485 | 0
8584 | 0.12485 | 0
8585 | 0.12485 | 0
8586 | 6.4885 | 6.7257
8587 | 12.5361 | 13.2535
8588 | 0.12485 | 0
8589 | 1.4634 | 0
8590 | 0.12485 | 0
8591 | 0.12485 | 0
8592 | 0.12485 | 0
8593 | 0.12485 | 0
8594 | 0.12485 | 0
8595 | 0.12485 | 0
8596 | 0.12485 | 0
8597 | 0.12485 | 0
8598 | 12.8362 | 13.3013
8599 | 1.4261 | 0
8600 | 1.8177 | 0
8601 | 0.12485 | 0
8602 | 0.12485 | 0
8603 | 0.12485 | 0
8604 | 0.94871 | 6.4507
8605 | 0.12485 | 0
8606 | 0.12485 | 0
8607 | 0.12485 | 0
8608 | 0.12485 | 0
8609 | 0.12485 | 0
8610 | 6.497 | 6.7356
8611 | 12.5525 | 13.266
8612 | 0.12485 | 0
8613 | 1.4651 | 0
8614 | 0.12485 | 0
8615 | 0.12485 | 0
8616 | 0.12485 | 0
8617 | 0.12485 | 0
8618 | 0.12485 | 0
8619 | 0.12485 | 0
8620 | 0.12485 | 0
8621 | 0.12485 | 0
8622 | 12.852 | 13.3144
8623 | 1.4277 | 0
8624 | 1.8198 | 0
8625 | 0.12485 | 0
8626 | 0.12485 | 0
8627 | 0.12485 | 0
8628 | 0.94974 | 6.4614
8629 | 0.12485 | 0
8630 | 0.12485 | 0
8631 | 0.12485 | 0
8632 | 0.12485 | 0
8633 | 0.12485 | 0
8634 | 6.5053 | 6.7454
8635 | 12.5688 | 13.2784
8636 | 0.12485 | 0
8637 | 1.4668 | 0
8638 | 0.12485 | 0
8639 | 0.12485 | 0
8640 | 0.12485 | 0
8641 | 0.12485 | 0
8642 | 0.12485 | 0
8643 | 0.12485 | 0
8644 | 0.12485 | 0
8645 | 0.12485 | 0
8646 | 12.8675 | 13.3274
8647 | 1.4293 | 0
8648 | 1.8218 | 0
8649 | 0.12485 | 0
8650 | 0.12485 | 0
8651 | 0.12485 | 0
8652 | 0.95076 | 6.472
8653 | 0.12485 | 0
8654 | 0.12485 | 0
8655 | 0.12485 | 0
8656 | 0.12485 | 0
8657 | 0.12485 | 0
8658 | 6.5135 | 6.755
8659 | 12.5847 | 13.2905
8660 | 0.12485 | 0
8661 | 1.4685 | 0
8662 | 0.12485 | 0
8663 | 0.12485 | 0
8664 | 0.12485 | 0
8665 | 0.12485 | 0
8666 | 0.12485 | 0
8667 | 0.12485 | 0
8668 | 0.12485 | 0
8669 | 0.12485 | 0
8670 | 12.8828 | 13.3401
8671 | 1.4309 | 0
8672 | 1.8239 | 0
8673 | 0.12485 | 0
8674 | 0.12485 | 0
8675 | 0.12485 | 0
8676 | 0.95176 | 6.4824
8677 | 0.12485 | 0
8678 | 0.12485 | 0
8679 | 0.12485 | 0
8680 | 0.12485 | 0
8681 | 0.12485 | 0
8682 | 6.5216 | 6.7644
8683 | 12.6005 | 13.3025
8684 | 0.12485 | 0
8685 | 1.4701 | 0
8686 | 0.12485 | 0
8687 | 0.12485 | 0
8688 | 0.12485 | 0
8689 | 0.12485 | 0
8690 | 0.12485 | 0
8691 | 0.12485 | 0
8692 | 0.12485 | 0
8693 | 0.12485 | 0
8694 | 12.8978 | 13.3526
8695 | 1.4324 | 0
8696 | 1.8259 | 0
8697 | 0.12485 | 0
8698 | 0.12485 | 0
8699 | 0.12485 | 0
8700 | 0.95275 | 6.4926
8701 | 0.12485 | 0
8702 | 0.12485 | 0
8703 | 0.12485 | 0
8704 | 0.12485 | 0
8705 | 0.12485 | 0
8706 | 6.5296 | 6.7737
8707 | 12.616 | 13.3143
8708 | 0.12485 | 0
8709 | 1.4717 | 0
8710 | 0.12485 | 0
8711 | 0.12485 | 0
8712 | 0.12485 | 0
8713 | 0.12485 | 0
8714 | 0.12485 | 0
8715 | 0.12485 | 0
8716 | 0.12485 | 0
8717 | 0.12485 | 0
8718 | 12.9126 | 13.3649
8719 | 1.4339 | 0
8720 | 1.8279 | 0
8721 | 0.12485 | 0
8722 | 0.12485 | 0
8723 | 0.12485 | 0
8724 | 0.95372 | 6.5027
8725 | 0.12485 | 0
8726 | 0.12485 | 0
8727 | 0.12485 | 0
8728 | 0.12485 | 0
8729 | 0.12485 | 0
8730 | 6.5374 | 6.7829
8731 | 12.6312 | 13.3259
8732 | 0.12485 | 0
8733 | 1.4733 | 0
8734 | 0.12485 | 0
8735 | 0.12485 | 0
8736 | 0.12485 | 0
8737 | 0.12485 | 0
8738 | 0.12485 | 0
8739 | 0.12485 | 0
8740 | 0.12485 | 0
8741 | 0.12485 | 0
8742 | 12.9271 | 13.3771
8743 | 1.4354 | 0
8744 | 1.8298 | 0
8745 | 0.12485 | 0
8746 | 0.12485 | 0
8747 | 0.12485 | 0
8748 | 0.95467 | 6.5126
8749 | 0.12485 | 0
8750 | 0.12485 | 0
8751 | 0.12485 | 0
8752 | 0.12485 | 0
8753 | 0.12485 | 0
8754 | 6.5451 | 6.7919
8755 | 12.6462 | 13.3372
8756 | 0.12485 | 0
8757 | 1.4748 | 0
8758 | 0.12485 | 0
8759 | 0.12485 | 0
Total (kWh)
Deviation %
Tolerance % (editable) | 5
Verdict
Monthly energy — the GOVERNING DHW resolution
month | CogenS kWh | EnergyPlus kWh | deviation %
1
2
3
4
5
6
7
8
9
10
11
12
Monthly NMBE %
Monthly CV(RMSE) %

## Gates
Gate | Resolution | Standard | Tolerance | Deviation % | Result | Note
Annual source-side energy | annual | ASHRAE Guideline 14-2023 | +-5.0% | -0.2175 | PASS
Monthly NMBE | monthly | ASHRAE Guideline 14-2023 | +-5.0% | -0.2175 | PASS
Monthly CV(RMSE) | monthly | ASHRAE Guideline 14-2023 | +-15.0% | 0.286 | PASS
Peak hourly source demand (reported, not gated) | hourly_peak | ASHRAE Guideline 14-2023 | +-10.0% | -31.3502 | outside — not gated | Reported, not gated: follows the shipped dhw-heat-pump contract — hourly dispersion and a single-hour extremum are dominated by intra-hour cycling phase.
Hourly CV(RMSE) (reported, not gated) | hourly | ASHRAE Guideline 14-2023 | +-30.0% | 84.2222 | outside — not gated | Reported, not gated: follows the shipped dhw-heat-pump contract — hourly dispersion and a single-hour extremum are dominated by intra-hour cycling phase.

## Timestep Control
Timestep-sensitivity control test — all 7 direct-fired scenarios
Does the model's OWN timestep choice move the score against the same EnergyPlus reference? The engine has run natively at 15 / 20 / 30 / 60 minutes since 2026-07-29, so every case was re-run at all four. The result has structure rather than being uniformly small, and the structure is predictive: sensitivity requires BOTH a part-load curve AND tank state. The part-load curve is evaluated at each step's part-load ratio, and a coarser step averages the burner's on-time into a different ratio — but only if there is a tank whose on-time can be averaged. - Cycle cases carry no curve, so efficiency is constant: shift -0.15% to -0.73%. - Tankless + Modulate carries a curve but NO tank state — its algebraic branch reads the instantaneous served load, so the part-load ratio is identical at every step: shift exactly 0.00%. - Storage + Modulate carries both: shift -5.19%, the only material mover in the matrix. There is no counter-example. Note that the storage-modulate case stays inside the +-5% annual gate at every timestep (+1.98% at 60 min, -3.21% at 15 min) — the timestep changes where in the band it sits, not whether it passes.
Scenario | 60 min % | 30 min % | 20 min % | 15 min % | shift %
GAS_STORAGE_CYCLE_UAR2JACKET | 0.34 | -0.35 | -0.26 | -0.39 | -0.73
GAS_STORAGE_CYCLE_UAMIDGRADE | -0.47 | -0.68 | -0.76 | -0.78 | -0.31
GAS_STORAGE_CYCLE_UAEPEXAMPLE | -0.9 | -0.93 | -0.98 | -1.06 | -0.15
ELECTRIC_STORAGE_CYCLE | 0.34 | -0.35 | -0.26 | -0.39 | -0.73
OIL_STORAGE_CYCLE | 0.34 | -0.35 | -0.26 | -0.39 | -0.73
GAS_STORAGE_MODULATE | 1.98 | -1.75 | -2.59 | -3.21 | -5.19
GAS_TANKLESS_MODULATE | 6.01 | 6.01 | 6.01 | 6.01 | 0
Max ¦shift¦ across the matrix
Every gated metric in this pack is reported at 60 minutes, the engine's default. Sub-hourly agreement against EnergyPlus is NOT itself validated — this test establishes only that the model's own timestep choice does not move the direct-fired score outside the band. See the module README, Known gaps.